{"text_format":"2","workbook":"xls","n_sheets":2,"sheets":["Уинск больница","Лист2"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Уинск больница","index":0,"n_rows":31,"n_cols":18,"rows_kept":31,"cut":false,"hidden":false,"merged":[[27,8,27,10],[20,11,23,11],[24,9,24,10],[26,8,26,10],[11,11,16,11],[2,13,4,13],[2,22,2,27],[8,22,8,28],[14,25,14,31],[27,13,29,14],[29,9,29,10],[30,9,30,10],[28,9,28,10],[4,2,6,2],[1,2,3,2],[7,2,10,2],[1,11,10,11],[1,10,10,10],[25,9,25,10]],"flags":["formulas_cached_only"]}
[null,null,"Вид огр.","Ори-ен-та-ция","F,     м2","Тв,  °С","Тн,  °С","Rо, м2•°С/Вт","Добав. на ориент.","Qогр,    Вт","Qинф,    Вт","Qрасч,    Вт"]
[null,null,"нс до 4 м","сз",531.6,18,-35,3.94,0.1,7866.060913705585,null,50655.38730964468]
[null,null,null,"св",174.5,18,-35,3.94,0.1,2582.068527918782]
[null,null,null,"юз",132,18,-35,3.94,null,1775.6345177664975]
[null,null,"нс после 4 м","сз",939,20.6,-35,3.94,0.1,14575.949238578682]
[null,null,null,"св",537.6,20.6,-35,3.94,0.1,8345.080203045685]
[null,null,null,"юз",597,20.6,-35,3.94,null,8424.670050761422]
[null,null,"фонарь","сз",177.6,23.2,-35,3.94,0.1,2885.7746192893405]
[null,null,null,"св",46.6,23.2,-35,3.94,0.1,757.1908629441626]
[null,null,null,"юз",46.6,23.2,-35,3.94,null,688.3553299492387]
[null,null,null,"юв",177.6,23.2,-35,3.94,0.05,2754.6030456852795]
[null,null,"окно до 4 м","св",12.6,18,-35,0.54,0.1,1360.3333333333333,121.53960000000001,94421.30762370369]
[null,null,"окно после 4 м","сз",523,20.6,-35,0.54,0.1,59234.59259259259,5292.341600000001]
[null,null,null,"св",63,20.6,-35,0.54,0.1,7135.333333333334,637.5096000000001]
[null,null,null,"юз",3.6,20.6,-35,0.54,null,370.66666666666663,36.429120000000005]
[null,null,"окно фонарь","сз",80,23.2,-35,0.54,0.1,9484.444444444445,847.3920000000002]
[null,null,null,"юв",80,23.2,-35,0.54,0.05,9053.333333333334,847.3920000000002]
[null,null,"ворота","св",31.3,18,-35,2.6,0.1,701.8423076923077,177.52032,879.3626276923077]
[null,null,"ворота","юз",86.4,18,-35,2.6,null,1761.2307692307695,88.76016,1849.9909292307696]
[null,null,"кровля",null,7232.5,23.2,-35,3.18,null,132368.3962264151,null,132368.3962264151]
[null,null,"пол 1",null,481,18,-35,2.15,null,11857.209302325582,null,42282.386177530294]
[null,null,"пол 2",null,464,18,-35,4.3,null,5719.069767441861]
[null,null,"пол 3",null,449,18,-35,8.6,null,2767.093023255814]
[null,null,"пол 4",null,5878,18,-35,14.2,null,21939.014084507042]
[{"$nulls":9},"Сумма=",null,322456.8308942168]
[{"$nulls":9},"Q неучтенные 10%",null,354702.5139836385]
[{"$nulls":8},"Нагрев. ввоз. матер.",null,null,61000]
[{"$nulls":8},"Нагрев транспорта",null,null,10000,null,"Тепловыделения в цехе",null,"Плащадь пола, м2",6469,"Вт"]
[{"$nulls":15},"Тепловыделения, Вт/м2",23]
[{"$nulls":9},"Тепловыделения в цехе",null,148787,{"$nulls":4},148787]
[{"$nulls":9},"Тепловой баланс, теплонедостатки",null,276915.5139836385,"Вт"]

{"sheet":"Лист2","index":1,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}