{"text_format":"2","workbook":"xls","n_sheets":3,"sheets":["Двухтрубная","Однотрубная","Лист1"],"not_rendered":{"charts":1,"images":33,"macros":1,"external_links":1,"defined_names":20,"comments":181,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Двухтрубная","index":0,"n_rows":89,"n_cols":61,"rows_kept":89,"cut":false,"hidden":false,"merged":[[15,6,15,12],[0,17,0,20],[0,0,0,2],[5,0,5,2],[11,0,11,1],[8,18,8,19],[9,18,9,19]],"flags":["formulas_cached_only"]}
["радиатор",{"$nulls":9},"       эти кнопки раскрывают столбцы",{"$nulls":6},"Трубы",{"$nulls":5},1]
["q ном",125.71,"кк/ч",{"$nulls":14},"dу","dн","s","dв","ξ отв","start",2]
["▼t ном",50,"°С",{"$nulls":5},"kvs клапана при пред.настройке, м3/ч",{"$nulls":7},15.700000000000001,15,21.3,2.8,15.700000000000001,1.5,"step",3]
["n",0.33,null,null,"dу",1,2,3,4,5,6,7,"N",null,null,null,21.200000000000003,20,26.8,2.8,21.200000000000003,1,null,4]
[{"$nulls":4},10,0.04,0.08,0.12,0.19,0.25,0.33,0.38,0.56,null,null,null,27.1,25,33.5,3.2,27.1,0.5,null,5]
["температурный график",null,null,null,15,0.04,0.09,0.16,0.25,0.36,0.43,0.52,0.73,null,null,null,35.9,32,42.3,3.2,35.9,0.3,null,6]
["t пр",95,"°С",null,20,0.1,0.15,0.17,0.26,0.35,0.46,0.73,1.04,{"$nulls":10},7]
["t обр",70,"°С",null,25,0.1,0.15,0.17,0.26,0.35,0.46,0.7,1.04,{"$nulls":10},8]
[{"$nulls":18},"dу стояка",null,32,null,null,9]
["kэ",0.5,"мм",{"$nulls":4},70,{"$nulls":10},"dу подвод",null,15,null,null,10]
["ν",5e-06,{"$nulls":18},4]
["Δдоп. -60 ккал/ч"]
[1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,16,17,18,19,20,21,22,23,24,25,26,27,28,29,30]
["       изменять можно только зеленые ячейки"]
["       эти кнопки раскрывают строки",{"$nulls":22},29.427377090965567]
[{"$nulls":6},"тепловой расчет",{"$nulls":13},"гидравлиический расчет"]
[null,"Q тр","t вв",null,"L","изол","t вх","t вых","Δt тр","n","Δ","Δ","Qфакт","Q труб","Q тр","▼t","Q1","G","α","kv","kvs","настр.","ΔP","ΔPуд","d вн","ξ 1","ξ 2","ξ рад","d вн","ρ","v","Pд","Re","Re пр","λ","r","r*L","z","R","Z","ΔP","ΔPкл","ΔPкл","G ","G ","G","a","авт","ρ вх","ρ вых","P ест"]
["этаж","ккал/ч","°С",null,"м","%","°С","°С","°С","сек","%","ккал/ч","ккал/ч","ккал/ч","ккал/ч","°С","ккал/ч","кг/ч",0.3517962764478356,"м3/ч","м3/ч",null,"Па","Па/м","мм",null,null,null,"м","кг/м3","м/с","Па",{"$nulls":8},"Па","Па","бар","м3/ч","м3/ч","кг/ч",null,null,"кг/м3","кг/м3","Па"]
[12,700,20,{"$nulls":6},4,-3,-23,676.5815256539861,0,null,null,null,28,0.0077777777777777776,null,null,null,3110.111928542235,{"$nulls":37},4]
[null,null,null,"рад",0.6,100,95,70,25,4.138451751684337,-3,-23,676.5815256539861,0,700,62.5,169.14538141349652,28,0.0077777777777777776,0.16,0.16,3,3071.0314091558866,null,15,1.5,1.5,1.4,0.015,922.2075,0.04775014622411101,1.05135180803264,143.25043867233302,17040,0.09286761031617528,6.191174021078353,3.7147044126470115,4.4,3.905461200543262,4.625947955343617,8.531409155886879,3062.4999999999995,0.030624999999999996,null,0.028,28,1]
[null,null,null,"под1",0.9,100,95,95,0,null,null,null,0,0,null,null,null,28,0.0077777777777777776,{"$nulls":5},15,null,null,null,0.015,906.0699999999999,0.048600597055384075,1.0700768400965275,145.8017911661522,17040,0.09248564954270265,6.16570996951351,5.549138972562159,0,5.9380050970158065,0,5.9380050970158065]
[null,null,null,"обр2",0.4,100,70,70,0,null,null,null,0,0,null,null,null,28,0.0077777777777777776,{"$nulls":5},15,null,null,null,0.015,937.22,0.04698527877549759,1.0345111313312358,140.95583632649274,17040,0.09321876043104256,6.214584028736171,2.485833611494469,0,2.5716225417283547,0,2.5716225417283547]
[11,700,20,{"$nulls":6},4,-3,-23,676.5815256539861,0,null,null,null,56,0.015555555555555555,null,null,null,3201.4352425490038,{"$nulls":37},4]
[null,null,null,"обр1",2.6,100,70,70,0,null,null,null,0,0,null,null,null,28,0.0077777777777777776,{"$nulls":5},15,null,null,null,0.015,937.22,0.04698527877549759,1.0345111313312358,140.95583632649274,17040,0.09321876043104256,6.214584028736171,16.157918474714045,0,16.7155465212343,0,16.7155465212343]
[null,null,null,"под2",2.1,100,95,95,0,null,null,null,0,0,null,null,null,28,0.0077777777777777776,{"$nulls":5},15,null,null,null,0.015,906.0699999999999,0.048600597055384075,1.0700768400965275,145.8017911661522,17040,0.09248564954270265,6.16570996951351,12.947990935978371,0,13.855345226370215,0,13.855345226370215]
[null,null,null,"рад",0.6,100,95,70,25,4.138451751684337,-3,-23,676.5815256539861,0,700,62.5,169.14538141349652,28,0.0077777777777777776,0.16,0.16,3,3067.8773537317884,1.3579760401177254,15,null,null,1.4,0.015,922.2075,0.04775014622411101,1.05135180803264,143.25043867233302,17040,0.09286761031617528,6.191174021078353,3.7147044126470115,1.4,3.905461200543262,1.471892531245696,5.377353731788958,3062.4999999999995,0.030624999999999996,null,0.028,28,1]
[null,null,null,"под1",0.9,100,95,95,0,null,null,null,0,0,null,null,null,56,0.015555555555555555,{"$nulls":5},15,null,null,null,0.015,906.0699999999999,0.09720119411076815,4.28030736038611,291.6035823323044,17040,0.07903652479028649,5.269101652685766,4.742191487417189,0,20.29803712795215,0,20.29803712795215]
[null,null,null,"обр2",0.4,100,70,70,0,null,null,null,0,0,null,null,null,56,0.015555555555555555,{"$nulls":5},15,null,null,null,0.015,937.22,0.09397055755099518,4.138044525324943,281.9116726529855,17040,0.07962428225950509,5.308285483967006,2.1233141935868023,0,8.786368674316615,0,8.786368674316615]
[10,700,20,{"$nulls":6},4,-3,-23,676.5815256539861,0,null,null,null,84,0.023333333333333334,null,null,null,3343.5049549440605,{"$nulls":37},4]
[null,null,null,"обр1",2.6,100,70,70,0,null,null,null,0,0,null,null,null,56,0.015555555555555555,{"$nulls":5},15,null,null,null,0.015,937.22,0.09397055755099518,4.138044525324943,281.9116726529855,17040,0.07962428225950509,5.308285483967006,13.801542258314216,0,57.11139638305799,0,57.11139638305799]
[null,null,null,"под2",2.1,100,95,95,0,null,null,null,0,0,null,null,null,56,0.015555555555555555,{"$nulls":5},15,null,null,null,0.015,906.0699999999999,0.09720119411076815,4.28030736038611,291.6035823323044,17040,0.07903652479028649,5.269101652685766,11.065113470640108,0,47.36208663188835,0,47.36208663188835]
[null,null,null,"рад",0.6,100,95,70,25,4.138451751684337,-3,-23,676.5815256539861,0,700,62.5,169.14538141349652,28,0.0077777777777777776,0.16,0.16,3,3067.8773537317884,4.171812911976181,15,null,null,1.4,0.015,922.2075,0.04775014622411101,1.05135180803264,143.25043867233302,17040,0.09286761031617528,6.191174021078353,3.7147044126470115,1.4,3.905461200543262,1.471892531245696,5.377353731788958,3062.4999999999995,0.030624999999999996,null,0.028,28,1]
[null,null,null,"под1",0.9,100,95,95,0,null,null,null,0,0,null,null,null,84,0.023333333333333334,{"$nulls":5},15,null,null,null,0.015,906.0699999999999,0.14580179116615222,9.630691560868746,437.4053734984566,17040,0.07250878231065824,4.83391882071055,4.350526938639495,0,41.898583073287526,0,41.898583073287526]
[null,null,null,"обр2",0.4,100,70,70,0,null,null,null,0,0,null,null,null,84,0.023333333333333334,{"$nulls":5},15,null,null,null,0.015,937.22,0.14095583632649278,9.310600181981123,422.86750897947826,17040,0.07301659129224684,4.867772752816457,1.9471091011265829,0,18.12875435128626,0,18.12875435128626]
[9,700,20,{"$nulls":6},4,-3,-23,676.5815256539861,0,null,null,null,112,0.03111111111111111,null,null,null,3530.3567239821764,{"$nulls":37},4]
[null,null,null,"обр1",2.6,100,70,70,0,null,null,null,0,0,null,null,null,84,0.023333333333333334,{"$nulls":5},15,null,null,null,0.015,937.22,0.14095583632649278,9.310600181981123,422.86750897947826,17040,0.07301659129224684,4.867772752816457,12.656209157322788,0,117.8369032833607,0,117.8369032833607]
[null,null,null,"под2",2.1,100,95,95,0,null,null,null,0,0,null,null,null,84,0.023333333333333334,{"$nulls":5},15,null,null,null,0.015,906.0699999999999,0.14580179116615222,9.630691560868746,437.4053734984566,17040,0.07250878231065824,4.83391882071055,10.151229523492155,0,97.76336050433756,0,97.76336050433756]
[null,null,null,"рад",0.6,100,95,70,25,4.138451751684337,-3,-23,676.5815256539861,0,700,62.5,169.14538141349652,28,0.0077777777777777776,0.16,0.16,3,3067.8773537317884,8.24367258091543,15,null,null,1.4,0.015,922.2075,0.04775014622411101,1.05135180803264,143.25043867233302,17040,0.09286761031617528,6.191174021078353,3.7147044126470115,1.4,3.905461200543262,1.471892531245696,5.377353731788958,3062.4999999999995,0.030624999999999996,null,0.028,28,1]
[null,null,null,"под1",0.9,100,95,95,0,null,null,null,0,0,null,null,null,112,0.03111111111111111,{"$nulls":5},15,null,null,null,0.015,906.0699999999999,0.1944023882215363,17.12122944154444,583.2071646646089,17040,0.06844863727085512,4.563242484723675,4.106918236251308,0,70.31548942052166,0,70.31548942052166]
[null,null,null,"обр2",0.4,100,70,70,0,null,null,null,0,0,null,null,null,112,0.03111111111111111,{"$nulls":5},15,null,null,null,0.015,937.22,0.18794111510199035,16.552178101299774,563.823345305971,17040,0.06890162857098682,4.593441904732455,1.837376761892982,0,30.412587402042103,0,30.412587402042103]
[8,700,20,{"$nulls":6},4,-3,-23,676.5815256539861,0,null,null,null,140,0.03888888888888889,null,null,null,3760.480349037919,{"$nulls":37},4]
[null,null,null,"обр1",2.6,100,70,70,0,null,null,null,0,0,null,null,null,112,0.03111111111111111,{"$nulls":5},15,null,null,null,0.015,937.22,0.18794111510199035,16.552178101299774,563.823345305971,17040,0.06890162857098682,4.593441904732455,11.942948952304382,0,197.68181811327366,0,197.68181811327366]
[null,null,null,"под2",2.1,100,95,95,0,null,null,null,0,0,null,null,null,112,0.03111111111111111,{"$nulls":5},15,null,null,null,0.015,906.0699999999999,0.1944023882215363,17.12122944154444,583.2071646646089,17040,0.06844863727085512,4.563242484723675,9.582809217919719,0,164.06947531455054,0,164.06947531455054]
[null,null,null,"рад",0.6,100,95,70,25,4.138451751684337,-3,-23,676.5815256539861,0,700,62.5,169.14538141349652,28,0.0077777777777777776,0.16,0.16,3,3067.8773537317884,13.100074763230152,15,null,null,1.4,0.015,922.2075,0.04775014622411101,1.05135180803264,143.25043867233302,17040,0.09286761031617528,6.191174021078353,3.7147044126470115,1.4,3.905461200543262,1.471892531245696,5.377353731788958,3062.4999999999995,0.030624999999999996,null,0.028,28,1]
[null,null,null,"под1",0.9,100,95,95,0,null,null,null,0,0,null,null,null,140,0.03888888888888889,{"$nulls":5},15,null,null,null,0.015,906.0699999999999,0.24300298527692035,26.751921002413184,729.008955830761,17040,0.06561607459510885,4.374404973007256,3.9369644757065307,0,105.32136264340815,0,105.32136264340815]
[null,null,null,"обр2",0.4,100,70,70,0,null,null,null,0,0,null,null,null,140,0.03888888888888889,{"$nulls":5},15,null,null,null,0.015,937.22,0.23492639387748795,25.8627782832809,704.7791816324637,17040,0.06602766778454632,4.401844518969755,1.760737807587902,0,45.537571532636015,0,45.537571532636015]
[7,700,20,{"$nulls":6},4,-3,-23,676.5815256539861,0,null,null,null,168,0.04666666666666667,null,null,null,4032.9429988835386,{"$nulls":37},4]
[null,null,null,"обр1",2.6,100,70,70,0,null,null,null,0,0,null,null,null,140,0.03888888888888889,{"$nulls":5},15,null,null,null,0.015,937.22,0.23492639387748795,25.8627782832809,704.7791816324637,17040,0.06602766778454632,4.401844518969755,11.444795749321363,0,295.9942149621341,0,295.9942149621341]
[null,null,null,"под2",2.1,100,95,95,0,null,null,null,0,0,null,null,null,140,0.03888888888888889,{"$nulls":5},15,null,null,null,0.015,906.0699999999999,0.24300298527692035,26.751921002413184,729.008955830761,17040,0.06561607459510885,4.374404973007256,9.186250443315238,0,245.74984616795234,0,245.74984616795234]
[null,null,null,"рад",0.6,100,95,70,25,4.138451751684337,-3,-23,676.5815256539861,0,700,62.5,169.14538141349652,28,0.0077777777777777776,0.16,0.16,3,3067.8773537317884,18.417939492313163,15,null,null,1.4,0.015,922.2075,0.04775014622411101,1.05135180803264,143.25043867233302,17040,0.09286761031617528,6.191174021078353,3.7147044126470115,1.4,3.905461200543262,1.471892531245696,5.377353731788958,3062.4999999999995,0.030624999999999996,null,0.028,28,1]
[null,null,null,"под1",0.9,100,95,95,0,null,null,null,0,0,null,null,null,168,0.04666666666666667,{"$nulls":5},15,null,null,null,0.015,906.0699999999999,0.29160358233230443,38.52276624347498,874.8107469969132,17040,0.06350185830594285,4.23345722039619,3.8101114983565707,0,146.77603461276638,0,146.77603461276638]
[null,null,null,"обр2",0.4,100,70,70,0,null,null,null,0,0,null,null,null,168,0.04666666666666667,{"$nulls":5},15,null,null,null,0.015,937.22,0.28191167265298556,37.24240072792449,845.7350179589565,17040,0.06388044099500854,4.258696066333903,1.7034784265335614,0,63.441626192337175,0,63.441626192337175]
[6,700,20,{"$nulls":6},4,-3,-23,676.5815256539861,0,null,null,null,196,0.05444444444444444,null,null,null,4347.121060933461,{"$nulls":37},4]
[null,null,null,"обр1",2.6,100,70,70,0,null,null,null,0,0,null,null,null,168,0.04666666666666667,{"$nulls":5},15,null,null,null,0.015,937.22,0.28191167265298556,37.24240072792449,845.7350179589565,17040,0.06388044099500854,4.258696066333903,11.07260977246815,0,412.37057025019163,0,412.37057025019163]
[null,null,null,"под2",2.1,100,95,95,0,null,null,null,0,0,null,null,null,168,0.04666666666666667,{"$nulls":5},15,null,null,null,0.015,906.0699999999999,0.29160358233230443,38.52276624347498,874.8107469969132,17040,0.06350185830594285,4.23345722039619,8.890260162831998,0,342.4774140964549,0,342.4774140964549]
[null,null,null,"рад",0.6,100,95,70,25,4.138451751684337,-3,-23,676.5815256539861,0,700,62.5,169.14538141349652,28,0.0077777777777777776,0.16,0.16,3,3067.8773537317884,23.929563235059724,15,null,null,1.4,0.015,922.2075,0.04775014622411101,1.05135180803264,143.25043867233302,17040,0.09286761031617528,6.191174021078353,3.7147044126470115,1.4,3.905461200543262,1.471892531245696,5.377353731788958,3062.4999999999995,0.030624999999999996,null,0.028,28,1]
[null,null,null,"под1",0.9,100,95,95,0,null,null,null,0,0,null,null,null,196,0.05444444444444444,{"$nulls":5},15,null,null,null,0.015,906.0699999999999,0.3402041793876885,52.433765164729834,1020.6125381630653,17040,0.06185135736406371,4.1234238242709145,3.711081441843823,0,194.58597282882602,0,194.58597282882602]
[null,null,null,"обр2",0.4,100,70,70,0,null,null,null,0,0,null,null,null,196,0.05444444444444444,{"$nulls":5},15,null,null,null,0.015,937.22,0.32889695142848313,50.69104543523056,986.6908542854492,17040,0.06220268218555679,4.146845479037119,1.6587381916148478,0,84.08317303630044,0,84.08317303630044]
[5,700,20,{"$nulls":6},4,-3,-23,676.5815256539861,0,null,null,null,224,0.06222222222222222,null,null,null,3736.3790235429406,{"$nulls":37},4]
[null,null,null,"обр1",2.6,100,70,70,0,null,null,null,0,0,null,null,null,196,0.05444444444444444,{"$nulls":5},15,null,null,null,0.015,937.22,0.32889695142848313,50.69104543523056,986.6908542854492,17040,0.06220268218555679,4.146845479037119,10.78179824549651,0,546.5406247359527,0,546.5406247359527]
[null,null,null,"под2",2.1,100,95,95,0,null,null,null,0,0,null,null,null,196,0.05444444444444444,{"$nulls":5},15,null,null,null,0.015,906.0699999999999,0.3402041793876885,52.433765164729834,1020.6125381630653,17040,0.06185135736406371,4.1234238242709145,8.65919003096892,0,454.033936600594,0,454.033936600594]
[null,null,null,"рад",0.6,100,95,70,25,4.138451751684337,-3,-23,676.5815256539861,0,700,62.5,169.14538141349652,28,0.0077777777777777776,0.16,0.16,3,3067.8773537317884,29.427377090965567,15,null,null,1.4,0.015,922.2075,0.04775014622411101,1.05135180803264,143.25043867233302,17040,0.09286761031617528,6.191174021078353,3.7147044126470115,1.4,3.905461200543262,1.471892531245696,5.377353731788958,3062.4999999999995,0.030624999999999996,null,0.028,28,1]
[null,null,null,"под1",0.9,100,95,95,0,null,null,null,0,0,null,null,null,224,0.06222222222222222,{"$nulls":5},15,null,null,null,0.015,906.0699999999999,0.3888047764430726,68.48491776617776,1166.4143293292177,17040,0.06052071777108842,4.034714518072561,3.631243066265305,0,248.6853827821826,0,248.6853827821826]
[null,null,null,"обр2",0.4,100,70,70,0,null,null,null,0,0,null,null,null,224,0.06222222222222222,{"$nulls":5},15,null,null,null,0.015,937.22,0.3758822302039807,66.2087124051991,1127.646690611942,17040,0.060848978650567494,4.056598576704499,1.6226394306818,0,107.43286740334729,0,107.43286740334729]
[4,700,20,{"$nulls":6},4,-3,-23,676.5815256539861,0,null,null,null,252,0.07,null,null,null,3562.3071482438554,{"$nulls":37},4]
[null,null,null,"обр1",2.6,100,70,70,0,null,null,null,0,0,null,null,null,224,0.06222222222222222,{"$nulls":5},20,null,null,null,0.02,937.22,0.2114337544897391,20.94885040945752,845.7350179589564,22720,0.06267673655433002,3.133836827716501,8.147975752062903,0,170.6907251698529,0,170.6907251698529]
[null,null,null,"под2",2.1,100,95,95,0,null,null,null,0,0,null,null,null,224,0.06222222222222222,{"$nulls":5},20,null,null,null,0.02,906.0699999999999,0.21870268674922833,21.66905601195468,874.8107469969132,22720,0.0622756354576592,3.1137817728829598,6.538941723054216,0,141.69269445576924,0,141.69269445576924]
[null,null,null,"рад",0.6,100,95,70,25,4.138451751684337,-3,-23,676.5815256539861,0,700,62.5,169.14538141349652,28,0.0077777777777777776,0.16,0.16,3,3067.8773537317884,17.891698502719354,15,null,null,1.4,0.015,922.2075,0.04775014622411101,1.05135180803264,143.25043867233302,17040,0.09286761031617528,6.191174021078353,3.7147044126470115,1.4,3.905461200543262,1.471892531245696,5.377353731788958,3062.4999999999995,0.030624999999999996,null,0.028,28,1]
[null,null,null,"под1",0.9,100,95,95,0,null,null,null,0,0,null,null,null,252,0.07,{"$nulls":5},20,null,null,null,0.02,906.0699999999999,0.24604052259288187,27.42489901513014,984.1620903715274,22720,0.06092331479584401,3.0461657397922,2.7415491658129802,0,75.18670901743526,0,75.18670901743526]
[null,null,null,"обр2",0.4,100,70,70,0,null,null,null,0,0,null,null,null,252,0.07,{"$nulls":5},20,null,null,null,0.02,937.22,0.2378629738009565,26.513388799469674,951.451895203826,22720,0.0613042295887107,3.065211479435535,1.226084591774214,0,32.50765748274879,0,32.50765748274879]
[3,700,20,{"$nulls":6},4,-3,-23,676.5815256539861,0,null,null,null,280,0.07777777777777778,null,null,null,3666.704187452495,{"$nulls":37},4]
[null,null,null,"обр1",2.6,100,70,70,0,null,null,null,0,0,null,null,null,252,0.07,{"$nulls":5},20,null,null,null,0.02,937.22,0.2378629738009565,26.513388799469674,951.451895203826,22720,0.0613042295887107,3.065211479435535,7.9695498465323915,0,211.29977363786716,0,211.29977363786716]
[null,null,null,"под2",2.1,100,95,95,0,null,null,null,0,0,null,null,null,252,0.07,{"$nulls":5},20,null,null,null,0.02,906.0699999999999,0.24604052259288187,27.42489901513014,984.1620903715274,22720,0.06092331479584401,3.0461657397922,6.39694805356362,0,175.4356543740156,0,175.4356543740156]
[null,null,null,"рад",0.6,100,95,70,25,4.138451751684337,-3,-23,676.5815256539861,0,700,62.5,169.14538141349652,28,0.0077777777777777776,0.16,0.16,3,3067.8773537317884,13.87948242351339,15,null,null,1.4,0.015,922.2075,0.04775014622411101,1.05135180803264,143.25043867233302,17040,0.09286761031617528,6.191174021078353,3.7147044126470115,1.4,3.905461200543262,1.471892531245696,5.377353731788958,3062.4999999999995,0.030624999999999996,null,0.028,28,1]
[null,null,null,"под1",0.9,100,95,95,0,null,null,null,0,0,null,null,null,280,0.07777777777777778,{"$nulls":5},20,null,null,null,0.02,906.0699999999999,0.2733783584365354,33.85790001867919,1093.5134337461416,22720,0.05977271417039171,2.9886357085195856,2.689772137667627,0,91.07003611017952,0,91.07003611017952]
[null,null,null,"обр2",0.4,100,70,70,0,null,null,null,0,0,null,null,null,280,0.07777777777777778,{"$nulls":5},20,null,null,null,0.02,937.22,0.2642921931121739,32.73257876477737,1057.1687724486956,22720,0.06013581531080914,3.006790765540457,1.2027163062161828,0,39.368006224903304,0,39.368006224903304]
[2,700,20,{"$nulls":6},4,-3,-23,676.5815256539861,0,null,null,null,308,0.08555555555555555,null,null,null,3780.3566349434686,{"$nulls":37},4]
[null,null,null,"обр1",2.6,100,70,70,0,null,null,null,0,0,null,null,null,280,0.07777777777777778,{"$nulls":5},20,null,null,null,0.02,937.22,0.2642921931121739,32.73257876477737,1057.1687724486956,22720,0.06013581531080914,3.006790765540457,7.817655990405188,0,255.8920404618715,0,255.8920404618715]
[null,null,null,"под2",2.1,100,95,95,0,null,null,null,0,0,null,null,null,280,0.07777777777777778,{"$nulls":5},20,null,null,null,0.02,906.0699999999999,0.2733783584365354,33.85790001867919,1093.5134337461416,22720,0.05977271417039171,2.9886357085195856,6.27613498789113,0,212.4967509237522,0,212.4967509237522]
[null,null,null,"рад",0.6,100,95,70,25,4.138451751684337,-3,-23,676.5815256539861,0,700,62.5,169.14538141349652,28,0.0077777777777777776,0.16,0.16,3,3067.8773537317884,16.33147380063815,15,null,null,1.4,0.015,922.2075,0.04775014622411101,1.05135180803264,143.25043867233302,17040,0.09286761031617528,6.191174021078353,3.7147044126470115,1.4,3.905461200543262,1.471892531245696,5.377353731788958,3062.4999999999995,0.030624999999999996,null,0.028,28,1]
[null,null,null,"под1",0.9,100,95,95,0,null,null,null,0,0,null,null,null,308,0.08555555555555555,{"$nulls":5},20,null,null,null,0.02,906.0699999999999,0.300716194280189,40.96805902260183,1202.864777120756,22720,0.058779287833465296,2.938964391673265,2.6450679525059386,0,108.36329999705586,0,108.36329999705586]
[null,null,null,"обр2",0.4,100,70,70,0,null,null,null,0,0,null,null,null,308,0.08555555555555555,{"$nulls":5},20,null,null,null,0.02,937.22,0.2907214124233913,39.60642030538062,1162.885649693565,22720,0.05912648816582115,2.956324408291058,1.1825297633164231,0,46.835770829532514,0,46.835770829532514]
[1,700,20,{"$nulls":6},4,-3,-23,676.5815256539861,0,null,null,null,336,0.09333333333333334,null,null,null,3249.8405348268398,{"$nulls":37},4]
[null,null,null,"обр1",2.6,100,70,70,0,null,null,null,0,0,null,null,null,308,0.08555555555555555,{"$nulls":5},20,null,null,null,0.02,937.22,0.2907214124233913,39.60642030538062,1162.885649693565,22720,0.05912648816582115,2.956324408291058,7.686443461556751,0,304.4325103919614,0,304.4325103919614]
[null,null,null,"под2",2.1,100,95,95,0,null,null,null,0,0,null,null,null,308,0.08555555555555555,{"$nulls":5},20,null,null,null,0.02,906.0699999999999,0.300716194280189,40.96805902260183,1202.864777120756,22720,0.058779287833465296,2.938964391673265,6.171825222513856,0,252.84769999313033,0,252.84769999313033]
[null,null,null,"рад",0.6,100,95,70,25,4.138451751684337,-3,-23,676.5815256539861,0,700,62.5,169.14538141349652,28,0.0077777777777777776,0.16,0.16,3,3067.8773537317884,18.846880070148053,15,null,null,1.4,0.015,922.2075,0.04775014622411101,1.05135180803264,143.25043867233302,17040,0.09286761031617528,6.191174021078353,3.7147044126470115,1.4,3.905461200543262,1.471892531245696,5.377353731788958,3062.4999999999995,0.030624999999999996,null,0.028,28,1]
[null,null,null,"под1",0.9,100,95,95,0,null,null,null,0,0,null,null,null,336,0.09333333333333334,{"$nulls":5},20,null,null,null,0.02,906.0699999999999,0.3280540301238425,48.75537602689803,1312.21612049537,22720,0.05791116417364402,2.8955582086822007,2.6060023878139806,0,127.05662634486477,0,127.05662634486477]
[null,null,null,"обр2",0.4,100,70,70,0,null,null,null,0,0,null,null,null,336,0.09333333333333334,{"$nulls":5},20,null,null,null,0.02,937.22,0.31715063173460867,47.13491342127941,1268.6025269384345,22720,0.05824403904113071,2.9122019520565354,1.1648807808226143,0,54.906554750186274,0,54.906554750186274]
["стояк:",8400,{"$nulls":11},0,null,null,null,336,0.09333333333333334]

{"sheet":"Однотрубная","index":1,"n_rows":93,"n_cols":61,"rows_kept":93,"cut":false,"hidden":false,"merged":[[15,6,15,12],[11,0,11,1],[0,0,0,2],[5,0,5,2],[2,11,3,11],[4,11,5,11],[7,4,7,11],[10,18,10,19],[0,17,0,20],[8,17,8,18],[9,17,9,18]],"flags":["formulas_cached_only"]}
["радиатор",{"$nulls":9},"       эти кнопки раскрывают столбцы",null,null,"верхняя",null,null,null,"Трубы",null,null,null,"клапан"]
["q ном",125.71,"кк/ч",{"$nulls":10},"нижняя",null,null,null,"dу","dн","s","dв","kvs"]
["▼t ном",50,"°С",{"$nulls":8},100,{"$nulls":4},15.700000000000001,15,21.3,2.8,15.700000000000001,1.63,1.5]
["n",0.33,{"$nulls":14},21.200000000000003,20,26.8,2.8,21.200000000000003,2.06,1]
[{"$nulls":11},100,{"$nulls":4},27.1,25,33.5,3.2,27.1,2.27,0.5]
["температурный график",{"$nulls":15},35.9,32,42.3,3.2,35.9,2.27,0.3]
["t пр",95,"°С"]
["t обр",70,"°С"]
[{"$nulls":17},"dу стояка",null,20]
["kэ",0.5,"мм",{"$nulls":14},"dу замык.уч-ка",null,15]
["ν",5e-06,{"$nulls":14},1,"разводка","верхняя"]
["Δдоп. -60 ккал/ч",{"$nulls":31},"dP радиат",13.886665992395343]
[1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,16,17,18,19,20,21,22,{"$nulls":11},1.7546621015128525]
["       изменять можно только зеленые ячейки"]
["       эти кнопки раскрывают строки",{"$nulls":16},0.047402469650152185]
[{"$nulls":6},"тепловой расчет",{"$nulls":12},"гидравлиический расчет"]
[12,"Q тр","t вв",null,"L","изол","t вх","t вых","Δt тр","n","Δ","Δ","Qфакт","Q труб","Q тр","▼t","Q1","G","α","kv","kvs","ΔP","ΔPуд","d вн","ξ 1","ξ 2","ξ рад","d вн","ρ","v","Pд","Re","Re пр","λ","r","r*L","z","R","Z","ΔP","ΔPкл","ΔPкл","G ","G ","G","a","авт","α","ρ вх","ρ вых","P ест"]
["этаж","ккал/ч","°С",null,"м","%","°С","°С","°С","сек","%","ккал/ч","ккал/ч","ккал/ч","ккал/ч","°С","ккал/ч","кг/ч",0.3517962764478356,"м3/ч","м3/ч","Па","Па/м","мм",null,null,null,"м","кг/м3","м/с","Па",{"$nulls":8},"Па","Па","бар","м3/ч","м3/ч","кг/ч",null,null,null,"кг/м3","кг/м3","Па"]
[12,1000,20,null,null,null,95,92.91666666666667,2.0833333333333335,5,"+ 2","+ 22",1022.1703940982553,0,1000,null,null,480,0.36,2.0283145961100413,2.06,1427.6453721572725,245.57045989983666,{"$nulls":37},5]
[null,null,null,"общ",1.9,100,95,95,0,null,null,null,0,0,null,null,null,480,{"$nulls":5},21.200000000000003,1,null,null,0.021200000000000004,906.0699999999999,0.41709559848934846,78.81392734631183,1768.4853375948376,24083.200000000004,0.05489760998379865,2.589509904896162,4.920068819302708,1,387.76994646337783,78.81392734631183,466.58387380968963,{"$nulls":8},906.0699999999999,906.0699999999999,0]
[null,null,null,"рад",0.6,100,95,89.1400146484375,5.8599853515625,4.8915523565040555,2,22,1022.1703940982553,0,1000,72.07000732421875,204.43407881965106,170.64889074054787,0.36,2.0283145961100413,2.06,null,null,21.200000000000003,4.3159544962465874,6.377251543358004,1.4,0.021200000000000004,909.9535647293553,0.14765234866460683,9.919047137425245,626.045958337933,24083.200000000004,0.06632894949365,3.128724032719339,1.8772344196316033,12.093206039604592,18.620376696322996,119.95308074943361,93.21995282695585,707.8419662699138,0.007078419662699138,0.17064889074054787,0.1733146897427626,173.3146897427626,0.9846187359757481,0.883629528998141,0.36107227029742206,906.0699999999999,913.7753184877337,45.35350461880076]
[null,null,null,"зам",0.5,100,95,95,0,null,null,null,0,0,null,null,null,309.35110925945213,0.36,0.031685403889958774,null,null,null,15.700000000000001,2.7075710888016125,2.8132164249562224,null,0.015700000000000002,906.0699999999999,0.49013810140005853,108.83502561270203,1539.033638396184,17835.2,0.05776169610601409,3.6790889239499416,1.8395444619749708,5.520787513757835,200.20686863475012,600.8550504621195,801.0619190968696,801.0619190968696,{"$nulls":7},906.0699999999999,906.0699999999999,0]
[null,null,null,"общ",0.4,100,92.91666666666667,92.91666666666667,0,null,null,null,0,0,null,null,null,480,{"$nulls":5},21.200000000000003,1,null,null,0.021200000000000004,908.8377083333332,0.4158254058541282,78.57391313750541,1763.0997208215038,24083.200000000004,0.05492357618040144,2.5907347254906337,1.0362938901962535,1,81.425666113208,78.57391313750541,159.9995792507134,{"$nulls":8},908.8377083333332,908.8377083333332,0]
[11,1000,20,null,null,null,92.91666666666667,90.83333333333334,2.0833333333333335,5,-2,-17,982.9980374822048,0,1000,null,null,480,0.36,2.028409729908459,2.06,1267.3955541011603,203.56416528301997,{"$nulls":37},5]
[null,null,null,"общ",1.9,100,92.91666666666667,92.91666666666667,0,null,null,null,0,0,null,null,null,480,{"$nulls":5},21.200000000000003,null,null,null,0.021200000000000004,908.8377083333332,0.4158254058541282,78.57391313750541,1763.0997208215038,24083.200000000004,0.05492357618040144,2.5907347254906337,4.922395978432204,0,386.77191403773793,0,386.77191403773793,{"$nulls":8},908.8377083333332,908.8377083333332,0]
[null,null,null,"рад",0.6,100,92.91666666666667,87.05001831054688,5.866648356119796,5.08648014476887,-2,-17,982.9980374822048,0,1000,69.98334248860678,196.59960749644097,170.45507746460544,0.36,2.028409729908459,2.06,null,null,21.200000000000003,4.327249832552438,6.392376134462955,1.4,0.021200000000000004,912.6816537659096,0.14704380841488682,9.866947324985208,623.4657476791202,24083.200000000004,0.0663852605457508,3.1313802144222067,1.878828128653324,12.119625967015393,18.53829817812288,119.5837110150638,93.23573075667636,706.1687820123437,0.0070616878201234376,0.17045507746460545,0.1731097294593109,173.10972945931093,0.9846649174312907,0.8833685208584556,0.36064526970689775,908.8377083333332,916.4636475852038,44.8862784365103]
[null,null,null,"зам",0.5,100,92.91666666666667,92.91666666666667,0,null,null,null,0,0,null,null,null,309.54492253539456,0.36,0.03159027009154114,null,null,null,15.700000000000001,2.7045571601260305,2.8135670539502193,null,0.015700000000000002,908.8377083333332,0.48895161441141977,108.63958828845814,1535.3080692518581,17835.2,0.057782048678116496,3.6803852661220695,1.8401926330610348,5.51812421407625,199.91777002720454,599.4867427418155,799.4045127690201,799.4045127690201,{"$nulls":7},908.8377083333332,908.8377083333332,0]
[null,null,null,"общ",0.4,100,90.83333333333334,90.83333333333334,0,null,null,null,0,0,null,null,null,480,{"$nulls":5},21.200000000000003,null,null,null,0.021200000000000004,911.5741666666667,0.4145771378155304,78.3380417764575,1757.807064337849,24083.200000000004,0.054949213038625655,2.5919440112559267,1.0367776045023707,0,81.21912729440224,0,81.21912729440224,{"$nulls":8},911.5741666666667,911.5741666666667,0]
[10,1000,20,null,null,null,90.83333333333334,88.75000000000001,2.0833333333333335,5,-6,-56,944.3016319075293,0,1000,null,null,480,0.36,2.033637912392721,2.06,1263.5541177259354,203.0478182360056,{"$nulls":37},5]
[null,null,null,"общ",1.9,100,90.83333333333334,90.83333333333334,0,null,null,null,0,0,null,null,null,480,{"$nulls":5},21.200000000000003,null,null,null,0.021200000000000004,911.5741666666667,0.4145771378155304,78.3380417764575,1757.807064337849,24083.200000000004,0.054949213038625655,2.5919440112559267,4.92469362138626,0,385.79085464841063,0,385.79085464841063,{"$nulls":8},911.5741666666667,911.5741666666667,0]
[null,null,null,"рад",0.6,100,90.83333333333334,84.97000885009766,5.863324483235687,5.294918308993905,-6,-56,944.3016319075293,0,1000,67.9016710917155,188.86032638150587,170.5517071175546,0.36,2.033637912392721,2.06,null,null,21.200000000000003,4.32161301216967,6.384829380405703,1.4,0.021200000000000004,915.3719768376235,0.14669475245430422,9.84910515686985,621.98575040625,24083.200000000004,0.0664177060235971,3.132910661490429,1.8797463968942574,12.106442392575373,18.51381993125875,119.23762420006187,93.40785691458728,703.3392956946841,0.007033392956946841,0.1705517071175546,0.17276257219693048,172.76257219693048,0.9872028700935539,0.8827634882551065,0.35992202541027185,911.5741666666667,919.1079055753879,44.34358721673334]
[null,null,null,"зам",0.5,100,90.83333333333334,90.83333333333334,0,null,null,null,0,0,null,null,null,309.4482928824454,0.36,0.026362087607278983,null,null,null,15.700000000000001,2.7060591092837205,2.8133923503506097,null,0.015700000000000002,911.5741666666667,0.48733165222440844,108.2458494678052,1530.2213879846427,17835.2,0.057809961959576356,3.6821631821386207,1.8410815910693104,5.519451459634331,199.28944076483586,597.4577118444355,796.7471526092713,796.7471526092713,{"$nulls":7},911.5741666666667,911.5741666666667,0]
[null,null,null,"общ",0.4,100,88.75000000000001,88.75000000000001,0,null,null,null,0,0,null,null,null,480,{"$nulls":5},21.200000000000003,null,null,null,0.021200000000000004,914.279375,0.4133504695140301,78.1062518780682,1752.6059907394877,24083.200000000004,0.05497452190537286,2.5931378257251345,1.037255130290054,0,81.0161104682534,0,81.0161104682534,{"$nulls":8},914.279375,914.279375,0]
[9,1000,20,null,null,null,88.75000000000001,86.66666666666669,2.0833333333333335,6,"+ 8","+ 87",1087.1939149274933,0,1000,null,null,480,0.36,2.038853133616613,2.06,1259.7728765990853,202.54027617063346,{"$nulls":37},6]
[null,null,null,"общ",1.9,100,88.75000000000001,88.75000000000001,0,null,null,null,0,0,null,null,null,480,{"$nulls":5},21.200000000000003,null,null,null,0.021200000000000004,914.279375,0.4133504695140301,78.1062518780682,1752.6059907394877,24083.200000000004,0.05497452190537286,2.5931378257251345,4.926961868877755,0,384.8265247242036,0,384.8265247242036,{"$nulls":8},914.279375,914.279375,0]
[null,null,null,"рад",0.6,100,88.75000000000001,82.8900146484375,5.859985351562514,5.518794685674956,8,87,1087.1939149274933,0,1000,65.82000732421875,181.1989858212489,170.64889074054744,0.36,2.038853133616613,2.06,null,null,21.200000000000003,4.31595449624661,6.377251543358036,1.4,0.021200000000000004,918.0310900589451,0.14635319267824962,9.831771929248092,620.5375369557784,24083.200000000004,0.06644955824523759,3.1344131247753575,1.8806478748652145,12.093206039604647,18.490100984899893,118.89764367479846,93.586374360967,700.543411861599,0.00700543411861599,0.17064889074054745,0.17241885113223213,172.41885113223213,0.9897345308818509,0.8821522930072564,0.35920593985881694,914.279375,921.7209941469132,43.801370298731335]
[null,null,null,"зам",0.5,100,88.75000000000001,88.75000000000001,0,null,null,null,0,0,null,null,null,309.3511092594525,0.36,0.021146866383387142,null,null,null,15.700000000000001,2.7075710888016067,2.8132164249562233,null,0.015700000000000002,914.279375,0.48573711895836186,107.85778871682547,1525.2145535292561,17835.2,0.057837579082880744,3.683922234578391,1.8419611172891954,5.5207875137578295,198.66985301318581,595.4599332093801,794.1297862225659,794.129786222566,{"$nulls":7},914.279375,914.279375,0]
[null,null,null,"общ",0.4,100,86.66666666666669,86.66666666666669,0,null,null,null,0,0,null,null,null,480,{"$nulls":5},21.200000000000003,null,null,null,0.021200000000000004,916.9533333333334,0.41214508436261094,77.87848362040174,1747.4951576974704,24083.200000000004,0.054999504105016375,2.5943162313686967,1.0377264925474787,0,80.81656565231577,0,80.81656565231577,{"$nulls":8},916.9533333333334,916.9533333333334,0]
[8,1000,20,null,null,null,86.66666666666669,84.58333333333336,2.0833333333333335,6,"+ 4","+ 42",1041.5944956038816,0,1000,null,null,480,0.36,2.0388411681067997,2.06,1257.0852243926602,202.0414141307894,{"$nulls":37},6]
[null,null,null,"общ",1.9,100,86.66666666666669,86.66666666666669,0,null,null,null,0,0,null,null,null,480,{"$nulls":5},21.200000000000003,null,null,null,0.021200000000000004,916.9533333333334,0.41214508436261094,77.87848362040174,1747.4951576974704,24083.200000000004,0.054999504105016375,2.5943162313686967,4.929200839600523,0,383.87868684849985,0,383.87868684849985,{"$nulls":8},916.9533333333334,916.9533333333334,0]
[null,null,null,"рад",0.6,100,86.66666666666669,80.80001831054688,5.866648356119811,5.760399104760438,4,42,1041.5944956038816,0,1000,63.73334248860678,173.59908260064694,170.455077464605,0.36,2.0388411681067997,2.06,null,null,21.200000000000003,4.3272498325524635,6.392376134462988,1.4,0.021200000000000004,920.6652791778968,0.14576870582104834,9.781385271995797,618.059312681245,24083.200000000004,0.0665043038298507,3.1369954636722026,1.8821972782033214,12.119625967015452,18.410496736008543,118.54673093586275,93.62484838544671,698.9612450344799,0.0069896124503448,0.170455077464605,0.17222403837526046,172.22403837526045,0.9897287223819415,0.8818742226709212,0.35880007994845925,916.9533333333334,924.3152734091785,43.33237928642458]
[null,null,null,"зам",0.5,100,86.66666666666669,86.66666666666669,0,null,null,null,0,0,null,null,null,309.544922535395,0.36,0.021158831893200336,null,null,null,15.700000000000001,2.704557160126023,2.81356705395022,null,0.015700000000000002,916.9533333333334,0.48462407908169697,107.6780582665342,1521.7196083165286,17835.2,0.05785694089786809,3.6851554712017887,1.8425777356008943,5.518124214076243,198.40519277465174,594.180900645275,792.5860934199267,792.5860934199267,{"$nulls":7},916.9533333333334,916.9533333333334,0]
[null,null,null,"общ",0.4,100,84.58333333333336,84.58333333333336,0,null,null,null,0,0,null,null,null,480,{"$nulls":5},21.200000000000003,null,null,null,0.021200000000000004,919.5960416666667,0.41096067381750523,77.65467870136577,1742.4732569862224,24083.200000000004,0.055024160939696774,2.595479289608338,1.0381917158433351,0,80.62044412423381,0,80.62044412423381,{"$nulls":8},919.5960416666667,919.5960416666667,0]
[7,1000,20,null,null,null,84.58333333333336,82.50000000000003,2.0833333333333335,6,0,-3,996.592442625996,0,1000,null,null,480,0.36,2.043985343433576,2.06,1253.4252015329114,201.55111031058456,{"$nulls":37},6]
[null,null,null,"общ",1.9,100,84.58333333333336,84.58333333333336,0,null,null,null,0,0,null,null,null,480,{"$nulls":5},21.200000000000003,null,null,null,0.021200000000000004,919.5960416666667,0.41096067381750523,77.65467870136577,1742.4732569862224,24083.200000000004,0.055024160939696774,2.595479289608338,4.931410650255842,0,382.94710959011064,0,382.94710959011064,{"$nulls":8},919.5960416666667,919.5960416666667,0]
[null,null,null,"рад",0.6,100,84.58333333333336,78.72000122070312,5.863332112630232,6.020515251139323,0,-3,996.592442625996,0,1000,61.65166727701825,166.098740437666,170.55148519489373,0.36,2.043985343433576,2.06,null,null,21.200000000000003,4.321625945793431,6.384846698667915,1.4,0.021200000000000004,923.2619317665633,0.14544094822882633,9.764911868535545,616.6696204902237,24083.200000000004,0.06653513601542965,3.138449812048568,1.8830698872291407,12.106472644461347,18.388011491085727,118.21863841200151,93.81602671076173,696.2343668446532,0.006962343668446532,0.17055148519489374,0.17188775870148434,171.88775870148436,0.9922258948706679,0.8812531105913798,0.3580994972947591,919.5960416666667,926.8659402722266,42.7906231923255]
[null,null,null,"зам",0.5,100,84.58333333333336,84.58333333333336,0,null,null,null,0,0,null,null,null,309.44851480510624,0.36,0.01601465656642409,null,null,null,15.700000000000001,2.7060556582485877,2.81339275183035,null,0.015700000000000002,919.5960416666667,0.4830808781540519,107.30174672609938,1516.8739574037231,17835.2,0.05788390076258607,3.686872660037329,1.8434363300186645,5.519448410078938,197.8039381893529,592.246455366062,790.050393555415,790.050393555415,{"$nulls":7},919.5960416666667,919.5960416666667,0]
[null,null,null,"общ",0.4,100,82.50000000000003,82.50000000000003,0,null,null,null,0,0,null,null,null,480,{"$nulls":5},21.200000000000003,null,null,null,0.021200000000000004,922.2075,0.4097969371570324,77.43478029692099,1737.5390135458176,24083.200000000004,0.0550484936896107,2.5966270608306927,1.0386508243322772,0,80.42769838738576,0,80.42769838738576,{"$nulls":8},922.2075,922.2075,0]
[6,1000,20,null,null,null,82.50000000000003,80.4166666666667,2.0833333333333335,7,"+ 10","+ 111",1110.7709235997932,0,1000,null,null,480,0.36,2.049120773851487,2.06,1249.821964992765,201.06924596846437,{"$nulls":37},7]
[null,null,null,"общ",1.9,100,82.50000000000003,82.50000000000003,0,null,null,null,0,0,null,null,null,480,{"$nulls":5},21.200000000000003,null,null,null,0.021200000000000004,922.2075,0.4097969371570324,77.43478029692099,1737.5390135458176,24083.200000000004,0.0550484936896107,2.5966270608306927,4.933591415578316,0,382.0315673400823,0,382.0315673400823,{"$nulls":8},922.2075,922.2075,0]
[null,null,null,"рад",0.6,100,82.50000000000003,76.64000701904297,5.85999298095706,6.30192945392769,10,111,1110.7709235997932,0,1000,59.5700035095215,158.68156051425615,170.64866856490315,0.36,2.049120773851487,2.06,null,null,21.200000000000003,4.315967420295877,6.377268853463432,1.4,0.021200000000000004,925.827370061173,0.14512058125249247,9.748954384919978,615.3112645105682,24083.200000000004,0.06656536591651079,3.13987575077881,1.883925450467286,12.09323627375931,18.366303281195393,117.89640879893916,94.01342204252367,693.5386934724278,0.006935386934724278,0.17064866856490316,0.17155467931885726,171.55467931885727,0.9947188222580035,0.8806257767702754,0.35740558191428595,922.2075,929.3854289904198,42.24929003761087]
[null,null,null,"зам",0.5,100,82.50000000000003,82.50000000000003,0,null,null,null,0,0,null,null,null,309.3513314350969,0.36,0.010879226148512888,null,null,null,15.700000000000001,2.7075676305752374,2.8132168273989517,null,0.015700000000000002,922.2075,0.48156163172312,106.93069976468549,1512.1035236105968,17835.2,0.05791057383037448,3.688571581552514,1.844285790776257,5.520784457974189,197.2107701737715,590.3413453411799,787.5521155149514,787.5521155149514,{"$nulls":7},922.2075,922.2075,0]
[null,null,null,"общ",0.4,100,80.4166666666667,80.4166666666667,0,null,null,null,0,0,null,null,null,480,{"$nulls":5},21.200000000000003,null,null,null,0.021200000000000004,924.7877083333333,0.408653581268217,77.2187330207607,1732.6911845772402,24083.200000000004,0.05507250361329315,2.5977596044006197,1.0391038417602478,0,80.23828213773135,0,80.23828213773135,{"$nulls":8},924.7877083333333,924.7877083333333,0]
[5,1000,20,null,null,null,80.4166666666667,78.33333333333337,2.0833333333333335,7,"+ 6","+ 59",1059.3234830095814,0,1000,null,null,480,0.36,2.049003221503593,2.06,1247.3013283207765,200.59570534432837,{"$nulls":37},7]
[null,null,null,"общ",1.9,100,80.4166666666667,80.4166666666667,0,null,null,null,0,0,null,null,null,480,{"$nulls":5},21.200000000000003,null,null,null,0.021200000000000004,924.7877083333333,0.408653581268217,77.2187330207607,1732.6911845772402,24083.200000000004,0.05507250361329315,2.5977596044006197,4.935743248361177,0,381.1318401542239,0,381.1318401542239,{"$nulls":8},924.7877083333333,924.7877083333333,0]
[null,null,null,"рад",0.6,100,80.4166666666667,74.55001068115234,5.866655985514356,6.607990960525782,6,59,1059.3234830095814,0,1000,57.483338673909515,151.33192614422592,170.45485579334263,0.36,2.049003221503593,2.06,null,null,21.200000000000003,4.327262775708589,6.392393460843939,1.4,0.021200000000000004,928.3676592052103,0.1445591198500691,9.700206906715673,612.9306681642931,24083.200000000004,0.06661856860788729,3.142385311692796,1.8854311870156775,12.119656236552528,18.289072622426605,117.5631731328265,94.07371223571991,692.0436256990157,0.006920436256990157,0.17045485579334263,0.17136966855357874,171.36966855357875,0.994661758011453,0.8803312079557136,0.3570201428199557,924.7877083333333,931.8856583026729,41.77853351953319]
[null,null,null,"зам",0.5,100,80.4166666666667,80.4166666666667,0,null,null,null,0,0,null,null,null,309.54514420665737,0.36,0.0109967784964069,null,null,null,15.700000000000001,2.7045537162275144,2.8135674544746445,null,0.015700000000000002,924.7877083333333,0.4805189114765472,106.76601232689391,1508.8293820363583,17835.2,0.057928956774503944,3.6897424697136265,1.8448712348568133,5.518121170702159,196.96954500225453,589.147792932481,786.1173379347356,786.1173379347356,{"$nulls":7},924.7877083333333,924.7877083333333,0]
[null,null,null,"общ",0.4,100,78.33333333333337,78.33333333333337,0,null,null,null,0,0,null,null,null,480,{"$nulls":5},21.200000000000003,null,null,null,0.021200000000000004,927.3366666666666,0.4075303204408798,77.00648288540239,1727.9285586693306,24083.200000000004,0.055096191947893426,2.598876978674218,1.039550791469687,0,80.05215023181697,0,80.05215023181697,{"$nulls":8},927.3366666666666,927.3366666666666,0]
[4,1000,20,null,null,null,78.33333333333337,76.25000000000004,2.0833333333333335,7,"+ 1","+ 9",1008.6098621905307,0,1000,null,null,480,0.36,2.0540801010146676,2.06,1243.8120196762288,200.13037557954243,{"$nulls":37},7]
[null,null,null,"общ",1.9,100,78.33333333333337,78.33333333333337,0,null,null,null,0,0,null,null,null,480,{"$nulls":5},21.200000000000003,null,null,null,0.021200000000000004,927.3366666666666,0.4075303204408798,77.00648288540239,1727.9285586693306,24083.200000000004,0.055096191947893426,2.598876978674218,4.937866259481014,0,380.2477136011306,0,380.2477136011306,{"$nulls":8},927.3366666666666,927.3366666666666,0]
[null,null,null,"рад",0.6,100,78.33333333333337,72.47001647949219,5.863316853841184,6.9402454431658835,1,9,1008.6098621905307,0,1000,55.40167490641278,144.0871231700758,170.55192904079178,0.36,2.0540801010146676,2.06,null,null,21.200000000000003,4.321600078567859,6.384812062162225,1.4,0.021200000000000004,930.8706226777264,0.14425252768863034,9.685146464214412,611.6307173997927,24083.200000000004,0.06664774118357836,3.143761376583884,1.8862568259503303,12.106412140730084,18.26867362845314,117.25237473911442,94.2835513732547,689.4114960459507,0.006894114960459507,0.17055192904079178,0.17104346303266302,171.04346303266303,0.9971262626284794,0.8796935725398025,0.35634054798471465,927.3366666666666,934.3426974166348,41.23749699431285]
[null,null,null,"зам",0.5,100,78.33333333333337,78.33333333333337,0,null,null,null,0,0,null,null,null,309.4480709592082,0.36,0.005919898985332406,null,null,null,15.700000000000001,2.7060625603352406,2.813391948868675,null,0.015700000000000002,927.3366666666666,0.47904783898407166,106.40577693175835,1504.2102144099852,17835.2,0.05795499760102242,3.69140112108423,1.845700560542115,5.519454509203916,196.39320212786566,587.3018452913396,783.6950474192054,783.6950474192054,{"$nulls":7},927.3366666666666,927.3366666666666,0]
[null,null,null,"общ",0.4,100,76.25000000000004,76.25000000000004,0,null,null,null,0,0,null,null,null,480,{"$nulls":5},21.200000000000003,null,null,null,0.021200000000000004,929.8543749999999,0.4064268761689098,76.7979772646365,1723.2499549561778,24083.200000000004,0.055119559909444796,2.5999792410115465,1.0399916964046187,0,79.86925865589265,0,79.86925865589265,{"$nulls":8},929.8543749999999,929.8543749999999,0]
[3,1000,20,null,null,null,76.25000000000004,74.16666666666671,2.0833333333333335,8,"+ 9","+ 95",1095.4529152833807,0,1000,null,null,480,0.36,2.0591365301678417,2.06,1240.3794129412386,199.6731466397316,{"$nulls":37},8]
[null,null,null,"общ",1.9,100,76.25000000000004,76.25000000000004,0,null,null,null,0,0,null,null,null,480,{"$nulls":5},21.200000000000003,null,null,null,0.021200000000000004,929.8543749999999,0.4064268761689098,76.7979772646365,1723.2499549561778,24083.200000000004,0.055119559909444796,2.5999792410115465,4.939960557921938,0,379.37897861549004,0,379.37897861549004,{"$nulls":8},929.8543749999999,929.8543749999999,0]
[null,null,null,"рад",0.6,100,76.25000000000004,70.39002227783203,5.859977722168011,7.302915431952176,9,95,1095.4529152833807,0,1000,53.320011138916044,136.93161441042258,170.64911291676904,0.36,2.0591365301678417,2.06,null,null,21.200000000000003,4.31594157221929,6.377234233271374,1.4,0.021200000000000004,933.342386217148,0.1439524850878167,9.670508847748884,610.3585367723429,24083.200000000004,0.06667637359782826,3.14511196216171,1.8870671772970258,12.093175805490665,18.2488998343474,116.94716362438021,94.4990138382843,686.8118559913664,0.006868118559913664,0.17064911291676904,0.17072067221297377,170.72067221297377,0.9995808398873017,0.8790506858571058,0.35566806711036203,929.8543749999999,936.7685866242682,40.69704962044332]
[null,null,null,"зам",0.5,100,76.25000000000004,76.25000000000004,0,null,null,null,0,0,null,null,null,309.350887083231,0.36,0.0008634698321583478,null,null,null,15.700000000000001,2.7075745470444113,2.8132160225112925,null,0.015700000000000002,929.8543749999999,0.47760071095323453,106.0510254740641,1499.6662323931566,17835.2,0.05798073656936566,3.693040545819468,1.846520272909734,5.520790569555704,195.825368500726,585.4855013289248,781.3108698296508,781.3108698296508,{"$nulls":7},929.8543749999999,929.8543749999999,0]
[null,null,null,"общ",0.4,100,74.16666666666671,74.16666666666671,0,null,null,null,0,0,null,null,null,480,{"$nulls":5},21.200000000000003,null,null,null,0.021200000000000004,932.3408333333333,0.40534297695843774,76.59316485727888,1718.6542223037764,24083.200000000004,0.05514260869312811,2.6010664477890617,1.0404265791156246,0,79.68956449609774,0,79.68956449609774,{"$nulls":8},932.3408333333333,932.3408333333333,0]
[2,1000,20,null,null,null,74.16666666666671,72.08333333333339,2.0833333333333335,8,"+ 4","+ 39",1038.8069076172903,0,1000,null,null,480,0.36,2.058914757110389,2.06,1238.0190442306673,199.22391124024438,{"$nulls":37},8]
[null,null,null,"общ",1.9,100,74.16666666666671,74.16666666666671,0,null,null,null,0,0,null,null,null,480,{"$nulls":5},21.200000000000003,null,null,null,0.021200000000000004,932.3408333333333,0.40534297695843774,76.59316485727888,1718.6542223037764,24083.200000000004,0.05514260869312811,2.6010664477890617,4.942026250799217,0,378.5254313564643,0,378.5254313564643,{"$nulls":8},932.3408333333333,932.3408333333333,0]
[null,null,null,"рад",0.6,100,74.16666666666671,68.3000259399414,5.866640726725308,7.701142475409204,4,39,1038.8069076172903,0,1000,51.23334630330406,129.8508634521613,170.4552991364427,0.36,2.058914757110389,2.06,null,null,21.200000000000003,4.32723688941829,6.392358808100765,1.4,0.021200000000000004,935.7887755582066,0.14341309093892157,9.623331097664373,608.0715055810275,24083.200000000004,0.06672805463944174,3.147549747143478,1.8885298482860866,12.119595697519054,18.173948017878878,116.63088216705445,94.58030056107872,685.4002864034494,0.006854002864034494,0.1704552991364427,0.17054514520741063,170.54514520741063,0.9994731830632957,0.8787401864331528,0.35530238584877216,932.3408333333333,939.1747663309301,40.22452962385462]
[null,null,null,"зам",0.5,100,74.16666666666671,74.16666666666671,0,null,null,null,0,0,null,null,null,309.5447008635573,0.36,0.0010852428896108712,null,null,null,15.700000000000001,2.7045606040408696,2.813566653423609,null,0.015700000000000002,932.3408333333333,0.4766254256078397,105.90077095280036,1496.6038364086166,17835.2,0.05799815193881417,3.69414980502001,1.847074902510005,5.518127257464478,195.6066561833781,584.3739307811501,779.9805869645281,779.9805869645281,{"$nulls":7},932.3408333333333,932.3408333333333,0]
[null,null,null,"общ",0.4,100,72.08333333333339,72.08333333333339,0,null,null,null,0,0,null,null,null,480,{"$nulls":5},21.200000000000003,null,null,null,0.021200000000000004,934.7960416666666,0.4042783581426455,76.39199565217756,1714.1402385248173,24083.200000000004,0.05516533947352944,2.6021386544117657,1.0408554617647063,0,79.51302590967471,0,79.51302590967471,{"$nulls":8},934.7960416666666,934.7960416666666,0]
[1,1000,20,null,null,null,72.08333333333339,70.00000000000006,2.0833333333333335,8,-2,-17,982.9170234856464,0,1000,null,null,480,0.35,2.0586529128111404,2.06,1235.7101367567116,198.78256477418677,{"$nulls":37},8]
[null,null,null,"общ",1.9,100,72.08333333333339,72.08333333333339,0,null,null,null,0,0,null,null,null,480,{"$nulls":5},21.200000000000003,null,null,null,0.021200000000000004,934.7960416666666,0.4042783581426455,76.39199565217756,1714.1402385248173,24083.200000000004,0.05516533947352944,2.6021386544117657,4.944063443382355,0,377.68687307095485,0,377.68687307095485,{"$nulls":8},934.7960416666666,934.7960416666666,0]
[null,null,null,"рад",0.6,100,72.08333333333339,66.21000671386719,5.873326619466198,8.139039012296468,-2,-17,982.9170234856464,0,1000,49.14667002360028,122.8646279357058,170.26126159673473,0.35,2.0586529128111404,2.06,null,null,21.200000000000003,4.338587782916425,6.407549623483353,1.4,0.021200000000000004,938.203828033343,0.14288109409290164,9.576718881436344,605.815838953903,24083.200000000004,0.06677929046562338,3.149966531397329,1.8899799188383972,12.14613740639978,18.099806374275207,116.32014343638903,94.66896655826463,684.0146950303213,0.006840146950303213,0.17026126159673471,0.1703726726863986,170.3726726863986,0.9993460741801652,0.8784243573762274,0.35494306809666376,934.7960416666666,941.5495216619775,39.75098325239961]
[null,null,null,"зам",0.5,100,72.08333333333339,72.08333333333339,0,null,null,null,0,0,null,null,null,309.7387384032653,0.35,0.0013470871888596747,null,null,null,15.700000000000001,2.7015488472174,2.813916810566405,null,0.015700000000000002,934.7960416666666,0.47567157307139407,105.75508658007841,1493.6087394441774,17835.2,0.05801523841360427,3.695238115516195,1.8476190577580975,5.515465657783805,195.3951134202105,583.2885481683754,778.6836615885859,778.6836615885859,{"$nulls":7},934.7960416666666,934.7960416666666,0]
[null,null,null,"общ",0.4,100,70.00000000000006,70.00000000000006,0,null,null,null,0,0,null,null,null,480,{"$nulls":5},21.200000000000003,null,null,null,0.021200000000000004,937.22,0.4032327617029555,76.19442089442475,1709.7069096205316,24083.200000000004,0.05518775340489186,2.603195915325087,1.0412783661300349,0,79.3396020971708,0,79.3396020971708,{"$nulls":8},937.22,937.22,0]
["стояк:",12000,{"$nulls":4},95,70,25,null,null,null,12370.732031831581,{"$nulls":4},480,null,null,null,15183.922253427412]
[]
[{"$nulls":6},"поток","Д.СО"]
[12,1000,null,null,12,5,6,6,-1,-1]
[11,1000,null,null,11,5,6,6,-1,-1]
[10,1000,null,null,10,5,6,6,-1,-1,{"$nulls":7},"G","Δt тр","Qфакт"]
[9,1000,null,null,9,6,6,6,0,0,{"$nulls":6},"со",0.034,7.63,1086.1396560000003]
[8,1000,null,null,8,6,7,7,-1,-1,{"$nulls":7},0.047402469650152185,5.8599853515625,1163]
[7,1000,null,null,7,6,7,7,-1,-1]
[6,1000,null,null,6,7,7,7,0,0]
[5,1000,null,null,5,7,7,8,0,-1]
[4,1000,null,null,4,7,8,8,-1,-1]
[3,1000,null,null,3,8,8,8,0,0]
[2,1000,null,null,2,8,8,9,0,-1]
[1,1000,null,null,1,8,9,9,-1,-1]

{"sheet":"Лист1","index":2,"n_rows":31,"n_cols":7,"rows_kept":31,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
[3,482,160.66666666666666,null,50,125.71,1.3]
[4,749,187.25,55,133.7,142.29194541850845]
[5,936,187.2,57.5,145,150.7568376334421]
[6,1123,187.16666666666666,60,156,159.33289467899897]
[7,1310,187.14285714285714,62.5,166.7,168.01685195611532]
[8,1497,187.125,65,177,176.80566839273467]
[9,1685,187.22222222222223,67.5,187.3,185.69650307045438]
[10,1872,187.2,70,197,194.6866950764249]
[11,2059,187.1818181818182,72.5,207,203.77374603536194]
[12,2246,187.16666666666666]
[13,2433,187.15384615384616]
[14,2621,187.21428571428572]
[15,2808,187.2]
[16,2995,187.1875]
[17,3181,187.11764705882354]
[18,3369,187.16666666666666]
[19,3557,187.21052631578948]
[20,3744,187.2]
[21,3931,187.1904761904762]
[22,4118,187.1818181818182]
[23,4305,187.17391304347825]
[24,4492,187.16666666666666]
[25,4680,187.2]
[]
[]
[]
[70]
[60]
[5]
[]
[60]