{"text_format":"2","workbook":"xls","n_sheets":2,"sheets":["Hárok1","В кубах"],"not_rendered":{"charts":3,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Hárok1","index":0,"n_rows":60,"n_cols":10,"rows_kept":60,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
[]
[{"$nulls":9},"Hydraulic power electroboiler K13"]
[]
[]
[]
[]
[null,null,"Pump maximum speed"]
[]
[null,null,"Water flow","Water flow","Pressure"]
[null,null,"l/min","l/h","bar"]
[null,null,21,1260,0.2968]
[null,null,20,1200,0.3039]
[null,null,19,1140,0.3141]
[null,null,18,1080,0.3235]
[null,null,17,1020,0.3447]
[null,null,16,960,0.3561]
[null,null,15,900,0.3766]
[null,null,14,840,0.3893]
[null,null,13,780,0.4017]
[null,null,12,720,0.4114]
[null,null,11,660,0.4273]
[null,null,10,600,0.4349]
[null,null,9,540,0.4519]
[null,null,8,480,0.4573]
[null,null,7,420,0.4617]
[null,null,6,360,0.4691]
[null,null,5,300,0.4746]
[null,null,4,240,0.4818]
[null,null,3,180,0.4895]
[null,null,2,120,0.4943]
[null,null,1,60,0.4959]
[null,null,0,0,0.5122]
[]
[]
[null,null,"Pump minimum speed"]
[]
[null,null,"Water flow","Water flow","Pressure"]
[null,null,"l/min","l/h","bar"]
[null,null,21,1260,0.087]
[null,null,20,1200,0.121]
[null,null,19,1140,0.14]
[null,null,18,1080,0.169]
[null,null,17,1020,0.2083]
[null,null,16,960,0.2215]
[null,null,15,900,0.2416]
[null,null,14,840,0.2673]
[null,null,13,780,0.2859]
[null,null,12,720,0.3065]
[null,null,11,660,0.3294]
[null,null,10,600,0.3455]
[null,null,9,540,0.3592]
[null,null,8,480,0.3719]
[null,null,7,420,0.389]
[null,null,6,360,0.3997]
[null,null,5,300,0.4047]
[null,null,4,240,0.4242]
[null,null,3,180,0.4367]
[null,null,2,120,0.4487]
[null,null,1,60,0.4623]
[null,null,0,0,0.4687]

{"sheet":"В кубах","index":1,"n_rows":60,"n_cols":10,"rows_kept":60,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
[]
[{"$nulls":9},"Hydraulic power electroboiler K13"]
[]
[]
[]
[]
[null,null,"Максимальная скорость"]
[]
[null,null,"Water flow","Расход","Pressure","Напор"]
[null,null,"l/min","м3/ч","bar","м"]
[null,null,21,1.26,0.2968,3.026517720118491]
[null,null,20,1.2,0.3039,3.098917571239924]
[null,null,19,1.14,0.3141,3.2029286249636724]
[null,null,18,1.08,0.3235,3.298781948983598]
[null,null,17,1.02,0.3447,3.5149617861349185]
[null,null,16,0.96,0.3561,3.631209434414403]
[null,null,15,0.9,0.3766,3.8402512580748778]
[null,null,14,0.84,0.3893,3.9697552171230743]
[null,null,13,0.78,0.4017,4.096200027532338]
[null,null,12,0.72,0.4114,4.195112500191197]
[null,null,11,0.66,0.4273,4.357247378054687]
[null,null,10,0.6,0.4349,4.43474581024101]
[null,null,9,0.54,0.4519,4.608097566447258]
[null,null,8,0.48,0.4573,4.663162241948066]
[null,null,7,0.42,0.4617,4.708029755319095]
[null,null,6,0.36,0.4691,4.783488755079461]
[null,null,5,0.3,0.4746,4.8395731467932475]
[null,null,4,0.24,0.4818,4.912992714127658]
[null,null,3,0.18,0.4895,4.991510862526958]
[null,null,2,0.12,0.4943,5.040457240749899]
[null,null,1,0.06,0.4959,5.056772700157546]
[null,null,0,0,0.5122,5.222986442872949]
[]
[]
[null,null,"Минимальная скорость"]
[]
[null,null,"Water flow","Расход","Pressure"]
[null,null,"l/min","м3/ч","bar"]
[null,null,21,1.26,0.087,0.8871531052907975]
[null,null,20,1.2,0.121,1.233856617703293]
[null,null,19,1.14,0.14,1.4276026981690997]
[null,null,18,1.08,0.169,1.723320399932699]
[null,null,17,1.02,0.2083,2.1240688716330247]
[null,null,16,0.96,0.2215,2.258671411746111]
[null,null,15,0.9,0.2416,2.463634370554675]
[null,null,14,0.84,0.2673,2.725701437290002]
[null,null,13,0.78,0.2859,2.9153686529038967]
[null,null,12,0.72,0.3065,3.12543019277735]
[null,null,11,0.66,0.3294,3.3589452055492957]
[null,null,10,0.6,0.3455,3.523119515838742]
[null,null,9,0.54,0.3592,3.6628206370167185]
[null,null,8,0.48,0.3719,3.792324596064915]
[null,null,7,0.42,0.389,3.966696068484141]
[null,null,6,0.36,0.3997,4.0758057032727795]
[null,null,5,0.3,0.4047,4.126791513921676]
[null,null,4,0.24,0.4242,4.325636175452372]
[null,null,3,0.18,0.4367,4.453100702074613]
[null,null,2,0.12,0.4487,4.575466647631964]
[null,null,1,0.06,0.4623,4.714148052596962]
[null,null,0,0,0.4687,4.77940989022755]