{"text_format":"2","workbook":"xlsx","n_sheets":1,"sheets":["Russian"],"not_rendered":{"charts":0,"images":2,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Russian","index":0,"n_rows":54,"n_cols":4,"rows_kept":54,"cut":false,"hidden":false,"merged":[[33,0,33,7],[22,2,22,3],[23,2,23,3],[24,2,24,3],[6,2,6,3],[8,2,8,3],[9,2,9,3],[7,2,7,3],[10,2,10,3],[25,2,25,3]]}
[]
[]
[]
[]
[]
[]
["Тип теплообменника",null,"XG 30-1 70"]
[null,null,"ОТОПЛЕНИЕ"]
["Danfoss Code",null,"004B5435"]
["Категория PED",":","II"]
["Мощность","[kW]","55"]
[null,null,"Первичная сторона","Вторичная сторона"]
["Расход","[l/s]","0,66","0,64"]
["Входная температура","[°C]","80","55"]
["Выходная температура","[°C]","60","76"]
["Деств. расход/обр. темп.","[l/s/°C]","0,664 /","59,8"]
["LMTD","[°C]","4,5","4,4"]
["Потери напора","[kPa]","0","0"]
["Скорость","[m/s]","0,2","0,2"]
["РАСЧЁТ"]
["Число  / Контур",":","34","35"]
["Объём вода","[l]","19,38","19,95"]
["Запас поверхности","[%]","5,15"]
["Поверхность теплообмена","[m2]","9,14"]
["Вес","[kg]","290"]
["ФИЗИЧЕСКИЕ СВОЙСТВА"]
["Теплоноситель первого контура",null,{"$f":"CONCATENATE([1]Translations!A20,[1]Translations!A21)","v":"Вода"}]
["Теплоноситель второго контура",null,{"$f":"CONCATENATE([1]Translations!B20,[1]Translations!B21)","v":"Вода"}]
["Теплоёмкость","[kJ/kgK]","4,200","4,196"]
["Плотность","[kg/m3]","977,3","979,9"]
["Динамическая вязскость","[mNs/m2]","0,409","0,431"]
["Теплопроводность","[W/mK]","0,667","0,663"]
["ГАБАРИТНЫЙ РАЗМЕРЫ","[mm]"]
["A - 0    "]
[null,null,null,"Материал пластин: EN 1.4404 (AISI 316 L)"]
[]
[null,null,null,"T11 на входе греющего контура"]
[null,null,null,"DN 65"]
[null,null,null,{"$f":"[1]Translations!J10","v":"Фланец DN65, PN16 l=160 EN 1.4301 (AISI 304) (Стандартное присоединение)"}]
[null,null,null,"T12 на выходе греющего контура"]
[null,null,null,"DN 65"]
[null,null,null,{"$f":"[1]Translations!J10","v":"Фланец DN65, PN16 l=160 EN 1.4301 (AISI 304) (Стандартное присоединение)"}]
[null,null,null,"T21 на входе нагреваемого контура"]
[null,null,null,"DN 65"]
[null,null,null,{"$f":"[1]Translations!J10","v":"Фланец DN65, PN16 l=160 EN 1.4301 (AISI 304) (Стандартное присоединение)"}]
[null,null,null,"T22 на выходе нагреваемого контура"]
[null,null,null,"DN 65"]
[null,null,null,{"$f":"[1]Translations!J10","v":"Фланец DN65, PN16 l=160 EN 1.4301 (AISI 304) (Стандартное присоединение)"}]
[null,null,null,"T112 на входе греющего контура"]
[]
[]
[null,null,null,"T212 на входе нагреваемого контура"]
[]
["Дополнительные принадлежности"]