{"text_format":"2","workbook":"xlsx","n_sheets":1,"sheets":["Лист1"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":0,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Лист1","index":0,"n_rows":52,"n_cols":13,"rows_kept":52,"cut":false,"hidden":false,"merged":[[37,0,37,10],[44,0,44,9],[0,0,0,10],[2,0,2,10],[13,0,13,10],[25,0,25,10],[26,0,26,10]]}
["Гидравлический расчет системы отопления храма"]
["№ участка","Длина, L, м","Tп, 0С","Tо, 0С","Тепловая мощность, Q, Вт","Расход, кг/ч","Диаметр условного прохода, d, мм","Скорость теплоносителя, ѵ, м/с","Линейные потери давления на трение, RL, Па","Потери давления на местные сопротивления, Z, Па","Суммарные потери давления, ∆P, Па"]
["С.О.1"]
["1-1",7.88,95,70,1820,62.6,10,0.22800000000000001,719,302,1021,null,12]
["1-2",6.6,95,70,2990,102.8,10,0.375,1467,136,1603,null,2]
["1-3",6.6,95,70,4290,147.5,10,0.53800000000000003,2817,281,3098,null,2]
["1-4",8.8000000000000007,95,70,5590,192.3,15,0.312,847,236,1083,null,5]
["1-5",6.6,95,70,10790,371.1,15,0.60099999999999998,2074,350,2424,null,2]
["1-6",6.9,95,70,15990,549.9,20,0.501,1088,244,1332,null,2]
["1-7",6.8,95,70,21450,737.7,25,0.43,615,179,794,null,2]
["1-8",31,95,70,26780,921,25,0.53700000000000003,4181,1399,5580,null,10]
["Итого",{"$f":"SUM(B4:B11)","v":81.179999999999993},{"$nulls":8},{"$f":"SUM(K4:K11)","v":16935}]
[]
["С.О.2"]
["2-1",7.7,95,70,1300,44.7,10,0.16300000000000001,388,206,594,null,16]
["2-2",6.6,95,70,2470,84.9,10,0.309,1036,93,1129,null,2]
["2-3",6.6,95,70,3770,129.69999999999999,10,0.47299999999999998,2227,217,2444,null,2]
["2-4",8.8000000000000007,95,70,5070,174.4,15,0.28299999999999997,712,233,945,null,6]
["2-5",10,95,70,10010,344.3,15,0.55800000000000005,2740,302,3042,null,2]
["2-6",3.4,95,70,13780,473.9,20,0.432,409,181,590,null,2]
["2-7",3.4,95,70,16900,581.20000000000005,20,0.53,593,273,866,null,2]
["2-8",3.4,95,70,17420,599.1,20,0.54600000000000004,627,289,916,null,2]
["2-9",1.4,95,70,21060,724.3,25,0.42199999999999999,122,173,295,null,2]
["2-10",3,95,70,25090,862.9,25,0.503,361,736,1097,null,6]
["Итого",{"$f":"SUM(B15:B24)","v":54.3},{"$nulls":8},{"$f":"SUM(K15:K24)","v":11918}]
[]
["С.О.3"]
["3-1",7.4,95,70,2696,92.7,10,0.33800000000000002,1365,997,2362,null,18]
["3-2",14.98,95,70,5496,189,15,0.30599999999999999,1392,91,1483,null,2]
["3-3",9.8000000000000007,95,70,7836,269.5,15,0.437,1730,1296,3026,null,14]
["Итого",{"$f":"SUM(B28:B30)","v":32.180000000000007},{"$nulls":8},{"$f":"SUM(K28:K30)","v":6871}]
[]
[]
[]
[]
[]
[]
["Гидравлический расчет ИТП храма"]
["№ контура","Длина, L, м","Tп, 0С","Tо, 0С","Тепловая мощность, Q, Вт","Расход, кг/ч","Диаметр условного прохода, d, мм","Скорость теплоносителя, ѵ, м/с","Линейные потери давления на трение, RL, Па","Потери давления на местные сопротивления, Z, Па","Суммарные потери давления, ∆P, Па"]
["Подача",5,null,null,null,2054,32,0.73199999999999998,873,1430,2303,null,"кран шаровый 1"]
["Теплообменник",{"$nulls":9},5100,null,"тройник на поворот 0.5"]
["Обратка",5,null,null,null,2054,32,0.73199999999999998,873,3900,4773,null,"внезапное расширение 1"]
[{"$nulls":9},"Итого",{"$f":"SUM(K40:K42)","v":12176},null,"кран шаровый 1"]
[{"$nulls":12},"отвод гнутый х2  1"]
["Суммарные потери давления системы отопления: ",{"$nulls":9},{"$f":"K43+K12","v":29111},null,"теплообменник              5100 Па"]
[{"$nulls":12},"отвод гнутый х2  1"]
[{"$nulls":12},"кран шаровый 1"]
[{"$nulls":12},"фильтр 10"]
[{"$nulls":12},"кран шаровый 1"]
[{"$nulls":12},"внезапное сужение 0.5"]
[{"$nulls":12},"тройник на поворот 0.5"]
[{"$nulls":12},"кран шаровый 1"]