{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Пример расчёта теплопотребления"],"not_rendered":{"charts":0,"images":2,"macros":1,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Пример расчёта теплопотребления","index":0,"n_rows":37,"n_cols":12,"rows_kept":37,"cut":false,"hidden":false,"merged":[[7,1,7,11],[2,1,2,11],[1,0,1,12],[0,0,0,12],[5,0,5,11],[9,0,9,11],[21,0,21,11],[27,0,27,11],[31,1,33,1],[32,11,33,11],[32,10,33,10],[32,5,33,5],[31,2,31,11],[31,0,33,0]],"flags":["formulas_cached_only"]}
["Расчет "]
[" "]
[null,"  расход тепла  при отоплении  здания  "]
[null,null,null,"Отопление ."]
[null,"         - максимальная часовая нагрузка на отопление:"]
[]
[]
[null,"          - расход тепловой энергии по месяцам:"]
[]
[]
[null,"             где:"]
[null,null,"α      -","поправочный коэффициент на расчетную температуру наружного воздуха"]
[null,null,"qо    -","удельная отопительная характеристика здания"]
[null,null,"Vн    -","наружный строительный объем здания, м3"]
[null,null,"kи    -","коэффициент, учитывающий потери тепла на ветер (инфильтрацию)"]
[null,null,"tвн    -","средняя расчетная температура воздуха внутри отапливаемых помещений"]
[null,null,"tср    -","средняя температура наружн. воздуха за расчетный период"]
[null,null,"tро    -","расчетная температура наружного воздуха для отопления (- 19 оС)"]
[null,null,"N     -","число дней в расчетном периоде"]
[null,null,"T      -","число часов работы отопления в сутки (24 часа)"]
[]
["Максимальная часовая нагрузка на отопление"]
[]
["№","Объект","α","qо       ","Vн    ","kи","tвн ","tро  ","Qо Гкал/час"]
[1,"максимальная часовая нагрузка на отопление:",1.194,0.53,4680,1.07,18,-19,0.1172]
[2]
[]
["Потребление теплоэнергии с разбивкой по месяцам.  "]
[]
[{"$nulls":7}," "]
[]
["№","Объект","Месяц/средняя температура наружного воздуха, оС"]
[null,null,"Янв.","Февр.","Март","I кв","Апр.","Окт.","Нбр.","Дкб.","IV кв","Год"]
[null,null,"-3,2","-2,3","+1,3",null,"+9,3","+9,6","+4,1","-0,5"]
[1,"Расход тепла  ",49.96140972972973,43.21068972972973,39.35639351351351,132.52849297297297,19.84164324324324,19.796030270270272,31.701016216216214,43.5984,95.09544648648648,247.4655827027027]
[2]
[3]