{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Лист1"],"not_rendered":{"charts":1,"images":0,"macros":0,"external_links":1,"defined_names":1,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Лист1","index":0,"n_rows":52,"n_cols":20,"rows_kept":52,"cut":false,"hidden":false,"merged":[[11,11,11,12],[1,1,1,14],[15,19,18,19],[1,16,1,19],[3,19,14,19]],"flags":["formulas_cached_only"]}
[]
[null,"Температурный режим",{"$nulls":14},"Исходные данные"]
[null,"Т н. возд","φ"," Т1п","Т1"," Т2",{"$nulls":8},"U",null,"Наименование","Обозн","Знач"]
[null,8,0.21818181818181817,50,41.21718550992185,35.762640055376394,{"$nulls":8},1.6101826565143282,null,"Температура наружного воздуха начала/конца",null,8,"                             вводится"]
[null,7,0.23636363636363636,50,42.66717441880337,36.75808350971246,{"$nulls":8},1.2409397137409688,null,"Расчётная температура наружного воздуха","Тнр",-35]
[null,6,0.2545454545454545,50,44.09847612424545,37.73483976060909,{"$nulls":8},0.9273823233328583,null,"Расчётная температура внутреннего воздуха","Твр",20]
[null,5,0.2727272727272727,50,45.51268379732372,38.694501979141904,{"$nulls":8},0.6581397097258553,null,"Расчётная температура в подающем тр-де теплосети","Т1п",95]
[null,4,0.2909090909090909,50,46.91115796040498,39.638430687677705,{"$nulls":8},0.4247157804443155,null,"Расчётная температура в подающем тр-де отопления","Т1р",95]
[null,3,0.3090909090909091,50,48.29507285399721,40.56780012672448,{"$nulls":8},0.22063763065918415,null,"Расчётная температура в обратном тр-де отопления","Т2р",70]
[null,2,0.32727272727272727,50,49.665451380140915,41.483633198322735,{"$nulls":8},0.040889275760554816,null,"Относительная поверхность нагрева","f",1]
[null,1,0.34545454545454546,51.023191915285416,51.023191915285416,42.386828278921776,{"$nulls":8},0,null,"Относительный расход теплоносителя","g",1]
[null,0,0.36363636363636365,52.36908921282442,52.36908921282442,43.278180121915334,"Средн тем-ра воды в т/сети","Тем-pа воды до котла",null,null,"Тем-pа воды за котлом","Диапазон",null,"Степень отк клап",0,null,"Инфильтрация","i",0]
[null,-1,0.38181818181818183,53.70385092843123,53.70385092843123,44.15839638297668,38.48991278264912,60,60.054545454545455,3.4583159898476623,60.08072727272727,57.08072727272727,63.08072727272727,22.429993797594623,0,null,"Относительные внутренние тепловыделения","w",0]
[null,-2,0.4,55.02811084953578,55.02811084953578,45.02811084953578,39.71262896425792,60,60.05909090909091,2.948047406048662,60.08745454545455,57.08745454545455,63.08745454545455,25.328976507929863,0,null,"Константа (0,25; 0,32)","n",0.25]
[null,-3,0.41818181818181815,56.34243960613131,56.34243960613131,45.887894151585854,40.91665794242727,60,60.06363636363636,2.51361089476143,60.094181818181816,57.094181818181816,63.094181818181816,28.460749637671494,0,null,"Нижняя температурная срезка в подающем трубопроводе","Тсрез",50]
[null,-4,0.43636363636363634,57.64735343100825,57.64735343100825,46.738262521917335,42.10359288823281,60,60.06818181818182,2.139606376392523,60.10090909090909,57.10090909090909,63.10090909090909,31.851126546284508,0,null,"Расчётная разность температур наружного воздуха",null,55,"вычисляется"]
[null,-5,0.45454545454545453,58.94332139104807,58.94332139104807,47.57968502741171,43.27479432404134,60,60.07272727272727,1.8145157804443157,60.10763636363637,57.10763636363637,63.10763636363637,35.53009036041483,0,null,"Расчётная разность температур теплоносителя отопления",null,25]
[null,-6,0.4727272727272727,60.23077140685534,60.23077140685534,48.41258958867353,44.431436490360845,60,60.07727272727273,1.5295552777180064,60.114363636363635,57.114363636363635,63.114363636363635,39.53264072972275,0,null,"Температурный напор в отопительном приборе","Ө",62.5]
[null,-7,0.4909090909090909,61.51009530250066,61.51009530250066,49.23736802977339,45.57454228923183,60,60.08181818181818,1.2779114979827775,60.12109090909091,57.12109090909091,63.12109090909091,43.89986182016106,0,null,"Расчётный коэффициент смешения","U",0]
[null,-8,0.509090909090909,62.781653071741175,62.781653071741175,50.05438034446845,46.705010097103596,60,60.086363636363636,1.0542198834932675,60.127818181818185,57.127818181818185,63.127818181818185,48.68028043324493,0]
[null,-9,0.5272727272727272,64.04577650590139,64.04577650590139,50.863958324083214,47.82363466736987,60,60.09090909090909,0.8542001865893141,60.13454545454545,57.13454545454545,63.13454545454545,53.93160928537267,0]
[null,-10,0.5454545454545454,65.30277229762036,65.30277229762036,51.66640866125673,48.931123655703956,60,60.095454545454544,0.6743965694024426,60.14127272727273,57.14127272727273,63.14127272727273,59.72300817343882,0]
[null,-11,0.5636363636363636,66.55292471111542,66.55292471111542,52.46201562020633,50.02811084953578,60,60.1,0.5119889150464225,60.148,57.148,63.148,66.13805101668335,0]
[null,-12,0.5818181818181818,67.79649789151851,67.79649789151851,53.251043346063966,51.11516687885858,60,60.10454545454545,0.3646536028917879,60.15472727272727,57.15472727272727,63.15472727272727,73.27866924477658,0]
[null,-13,0.6,69.03373787181087,69.03373787181087,54.03373787181087,52.19280797646279,60,60.10909090909091,0.2304592688242439,60.161454545454546,57.161454545454546,63.161454545454546,81.27046748613974,0]
[null,-14,0.6181818181818182,70.26487432490697,70.26487432490697,54.81032887036151,53.26150320922989,60,60.11363636363637,0.1077877175877699,60.16818181818182,57.16818181818182,63.16818181818182,90.27000246739692,0]
[null,-15,0.6363636363636364,71.49012209978467,71.49012209978467,55.581031190693764,54.32168049776443,48.41258958867353,48.530771406855344,{"$error":"#REF!"},{"$error":"#REF!"},{"$error":"#REF!"},{"$error":"#REF!"},{"$error":"#REF!"},0]
[null,-16,0.6545454545454545,72.70968257368082,72.70968257368082,56.34604621004445,55.373731666137026,49.23736802977339,49.36009530250067,{"$error":"#REF!"},{"$error":"#REF!"},{"$error":"#REF!"},{"$error":"#REF!"},{"$error":"#REF!"},0]
[null,-17,0.6727272727272727,73.92374484686728,73.92374484686728,57.10556302868547,56.418016708104815,50.05438034446845,50.181653071741174,{"$error":"#REF!"},{"$error":"#REF!"},{"$error":"#REF!"},{"$error":"#REF!"},{"$error":"#REF!"},0]
[null,-18,0.6909090909090909,75.13248680208808,75.13248680208808,57.8597595293608,57.4548674149923,50.863958324083214,50.9957765059014,{"$error":"#REF!"},{"$error":"#REF!"},{"$error":"#REF!"},{"$error":"#REF!"},{"$error":"#REF!"},0]
[null,-19,0.7090909090909091,76.33607604714143,76.33607604714143,58.6088033198687,58.48459047943855,51.66640866125673,51.802772297620365,{"$error":"#REF!"},{"$error":"#REF!"},{"$error":"#REF!"},{"$error":"#REF!"},{"$error":"#REF!"},0]
{"$rows_empty":12}
[null,-1]
[null,-2]
[null,-3]
[null,-4]
[null,-5]
[null,-6]
[null,-7]
[null,-8]
[null,-9]