{"text_format":"2","workbook":"xls","n_sheets":3,"sheets":["Лист1","Лист2","Лист3"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":0,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Лист1","index":0,"n_rows":64,"n_cols":19,"rows_kept":64,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["Помещение","Наим, огражд","a, м","б, м","площадь, м2","теплопередачи,\nК, Вт/(м2*0С)","положения, n,\nВт/(м2*0С)","tв","tн","Разность температур\n(tв-tн)*n","Основные теплопо-\nтери, Qосн, Вт","на ориен-\nтацию, β1","Пр, β2","1+∑β","Тепло-потери\nQт.п, Вт","Qин, Вт","∑Q"]
[8,"нс",3,3.2,9.600000000000001,0.4,1,16,-28,44,168.96000000000004,0.15,null,1.15,194.30400000000003,null,194.30400000000003]
[null,"окн",0.9,1.4,1.26,1.5,1,16,-28,44,83.16000000000001,0.15,null,1.15,95.634,null,289.93800000000005]
[null,"дв",0.9,2.1,1.8900000000000001,0.52,1,16,-28,44,43.2432,0.15,null,1.15,49.729679999999995,null,339.66768]
[null,"пол",3,4.4,13.200000000000001,0.4,0.6,16,-28,44,139.39200000000002,0.15,null,1.15,160.3008,null,499.96848]
[null,"перекр",3,4.4,13.200000000000001,0.35,0.9,16,-28,44,182.95200000000003,0.15,null,1.15,210.3948,null,710.36328]
[10,"нс",1.2,3.2,3.84,0.4,1,25,-28,53,81.408,0.15,null,1.15,93.61919999999999,null,803.98248]
[null,"пол",1.2,4.3,5.159999999999999,0.4,0.6,25,-28,53,65.63519999999998,0.15,null,1.15,75.48047999999997,null,879.46296]
[null,"перекр",1.2,4.3,5.159999999999999,0.35,0.9,25,-28,53,86.14619999999998,0.15,null,1.15,99.06812999999997,null,978.53109]
[9,"нс",6.15,3.2,19.680000000000003,0.4,1,20,-28,48,377.8560000000001,0.15,null,1.15,434.5344000000001,null,1413.06549]
[null,"нс",6.6,3.2,21.12,0.4,1,20,-28,48,405.504,0.2,null,1.2,486.6048,null,1899.67029]
[null,"окн",4.5,1.9,8.549999999999999,1.5,1,20,-28,48,615.5999999999999,0.15,null,1.15,707.9399999999998,null,2607.6102899999996]
[null,"дверь",0.9,2.1,1.8900000000000001,0.52,1,20,-28,48,47.174400000000006,0.15,null,1.15,54.25056,null,2661.8608499999996]
[null,"пол1",3.4,2.5,8.5,0.4,0.6,20,-28,48,97.92,0.15,null,1.15,112.60799999999999,null,2774.4688499999997]
[null,"пол2",2,8.8,17.6,0.4,0.6,20,-28,48,202.752,0.15,null,1.15,233.16479999999999,null,3007.6336499999998]
[null,"перекр1",3.4,2.5,8.5,0.35,0.9,20,-28,48,128.51999999999998,0.15,null,1.15,147.79799999999997,null,3155.4316499999995]
[null,"перекр2",2,8.8,17.6,0.35,0.9,20,-28,48,266.112,0.15,null,1.15,306.0288,null,3461.4604499999996,null,"Qобщ"]
["НС",1,6.97,3.2,22.304000000000002,0.4,1,18,-28,46,410.39360000000005,0.2,null,1.2,492.47232,null,3953.9327699999994]
["НС",null,3.5,3.2,11.200000000000001,0.4,1,18,-28,46,206.08,0.15,null,1.15,236.992,null,4190.92477]
["Окно",null,1.5,1.4,2.0999999999999996,1.5,1,18,-28,46,144.89999999999998,0.15,null,1.15,166.63499999999996,null,4357.55977]
["Дверь",null,0.9,2.1,1.8900000000000001,0.52,1,18,-28,46,45.208800000000004,0.15,null,1.15,51.99012,null,4409.54989,null,8144.857539999999]
["Пол",null,6.97,3.5,24.395,0.4,0.6,18,-28,46,269.3208,0.15,null,1.15,309.71892,null,4719.2688100000005]
["НС",4,1.8,3.2,5.760000000000001,0.4,1,16,-28,44,101.376,0.15,null,1.15,116.58239999999999,null,4835.851210000001]
["окно",null,0.75,1.4,1.0499999999999998,1.5,1,16,-28,44,69.29999999999998,0.15,null,1.15,79.69499999999998,null,4915.54621]
["пол",null,1.8,3.4,6.12,0.4,0.6,16,-28,44,64.6272,0.15,null,1.15,74.32128,null,4989.8674900000005]
["нс",7,4,3.2,12.8,0.4,1,16,-28,44,225.28000000000003,0.15,null,1.15,259.072,null,5248.939490000001,null,14470.666230000003]
["окно",null,1.3,1.4,1.8199999999999998,1.5,1,18,-28,46,125.57999999999998,0.15,null,1.15,144.41699999999997,null,5393.356490000001]
["пол",null,4,4.4,17.6,0.4,0.6,18,-28,46,194.304,0.15,null,1.15,223.44959999999998,null,5616.806090000001]
[6,"нс",3,3.2,9.600000000000001,0.4,1,18,-28,46,176.64000000000004,0.15,null,1.15,203.13600000000002,null,5819.942090000001]
[null,"пол",3,2.4,7.199999999999999,0.4,0.6,18,-28,46,79.488,0.15,null,1.15,91.4112,null,5911.353290000001]
[null,"пол",5.7,1.2,6.84,0.4,0.6,18,-28,46,75.51360000000001,0.15,null,1.15,86.84064000000001,null,5998.193930000001]
[null,"пол",0.9,1.8,1.62,0.4,0.6,18,-28,46,17.884800000000006,0.15,null,1.15,20.567520000000005,null,6018.761450000001]
[3,"нс",5.6,3.2,17.919999999999998,0.4,1,18,-28,46,329.72799999999995,0.15,null,1.15,379.1871999999999,null,6397.948650000001]
[null,"нс",6,3.2,19.200000000000003,0.4,1,18,-28,46,353.2800000000001,0.2,null,1.2,423.9360000000001,null,6821.884650000001]
[null,"окно",3,1.4,4.199999999999999,1.5,1,18,-28,46,289.79999999999995,0.15,null,1.15,333.2699999999999,null,7155.15465]
[null,"дверь",0.9,2.1,1.8900000000000001,0.52,1,18,-28,46,45.208800000000004,0.15,null,1.15,51.99012,null,7207.144770000001]
[null,"пол",5.6,6,33.599999999999994,0.4,0.6,18,-28,46,370.9439999999999,0.15,null,1.15,426.58559999999983,null,7633.73037]
[2,"нс",16.6,3.2,53.120000000000005,0.4,1,20,-28,48,1019.9040000000002,0.2,null,1.2,1223.8848000000003,null,8857.615170000001]
[null,"окно",6,1.4,8.399999999999999,1.5,1,20,-28,48,604.8,0.15,null,1.15,695.5199999999999,null,9553.135170000001]
[null,"пол",1,35.54,35.54,0.4,0.6,20,-28,48,409.4208,0.15,null,1.15,470.8339199999999,null,10023.96909]
[21,"нс",4.5,3,13.5,0.4,1,20,-28,48,259.20000000000005,0.15,null,1.15,298.08000000000004,null,10322.04909]
[null,"окно",1.5,1.4,2.0999999999999996,1.5,1,20,-28,48,151.2,0.15,null,1.15,173.87999999999997,null,10495.92909]
[null,"дверь",0.9,2.1,1.8900000000000001,0.52,1,20,-28,48,47.174400000000006,0.15,null,1.15,54.25056,null,10550.17965]
[null,"перекр",4.5,3.8,17.099999999999998,0.35,0.9,20,-28,48,258.55199999999996,0.15,null,1.15,297.3347999999999,null,10847.51445]
[16,"нс",2.7,3,8.100000000000001,0.4,1,18,-28,46,149.04000000000002,0.15,null,1.15,171.39600000000002,null,11018.910450000001]
[null,"нс",5.2,3,15.600000000000001,0.4,1,18,-28,46,287.0400000000001,0.2,null,1.2,344.4480000000001,null,11363.358450000002]
[null,"окно",0.8,1.4,1.1199999999999999,1.5,1,18,-28,46,77.27999999999999,0.15,null,1.15,88.87199999999997,null,11452.230450000001]
[null,"перекр1",8.4,1.4,11.76,0.35,0.9,18,-28,46,170.4024,0.15,null,1.15,195.96275999999997,null,11648.193210000001]
[null,"перекр2",3.8,2.7,10.26,0.35,0.9,18,-28,46,148.6674,0.15,null,1.15,170.96750999999998,null,11819.160720000002]
[17,"нс",4.3,3,12.899999999999999,0.4,1,20,-28,48,247.68,0.15,null,1.15,284.832,null,12103.992720000002]
[null,"нс",4.3,3,12.899999999999999,0.4,1,20,-28,48,247.68,0.2,null,1.2,297.216,null,12401.208720000002]
[null,"окно",1.5,1.4,2.0999999999999996,1.5,1,20,-28,48,151.2,0.15,null,1.15,173.87999999999997,null,12575.088720000002]
[null,"перекр",4.3,4.3,18.49,0.35,0.9,20,-28,48,279.56879999999995,0.15,null,1.15,321.50411999999994,null,12896.592840000001]
[18,"нс",2.8,3,8.399999999999999,0.4,1,25,-28,53,178.07999999999998,0.15,null,1.15,204.79199999999997,null,13101.38484]
[null,"перекр",2.8,4.3,12.04,0.35,0.9,25,-28,53,201.00779999999997,0.15,null,1.15,231.15896999999995,null,13332.543810000001]
[19,"нс",4.6,3,13.799999999999999,0.4,1,20,-28,48,264.96,0.15,null,1.15,304.70399999999995,null,13637.24781]
[null,"нс",5.3,3,15.899999999999999,0.4,1,20,-28,48,305.28,0.2,null,1.2,366.33599999999996,null,14003.58381]
[null,"окно",1.5,1.4,2.0999999999999996,1.5,1,20,-28,48,151.2,0.15,null,1.15,173.87999999999997,null,14177.46381]
[null,"пер1",3.4,5.3,18.02,0.35,0.9,20,-28,48,272.4624,0.15,null,1.15,313.33176,null,14490.795569999998]
[null,"пер2",1.2,4.4,5.28,0.35,0.9,20,-28,48,79.8336,0.15,null,1.15,91.80864,null,14582.604209999998]
[20,"нс",7.9,3,23.700000000000003,0.4,1,20,-28,48,455.0400000000001,0.15,null,1.15,523.296,null,15105.900209999998]
[null,"нс",8.9,3,26.700000000000003,0.4,1,20,-28,48,512.6400000000001,0.2,null,1.2,615.1680000000001,null,15721.068209999998]
[null,"окно",3,1.4,4.199999999999999,1.5,1,20,-28,48,302.4,0.15,null,1.15,347.75999999999993,null,16068.828209999998]
[null,"перекр",5.8,6.2,35.96,0.35,0.9,20,-28,48,543.7152000000001,0.15,null,1.15,625.2724800000001,null,16694.10069]

{"sheet":"Лист2","index":1,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}

{"sheet":"Лист3","index":2,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}