{"text_format":"2","workbook":"xlsx","n_sheets":3,"sheets":["Лист1","Лист2","Лист3"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":0,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Лист1","index":0,"n_rows":140,"n_cols":16,"rows_kept":140,"cut":false,"hidden":false,"merged":[[0,0,0,5],[0,7,0,12]]}
["75-57",{"$nulls":6},"90-60"]
["Пом.","Символ","Размер","nсек","L","Φr",null,"Пом.","Символ","Размер","nсек","L","Φr"]
["","","","сек","м","Вт",null,"","","","сек","м","Вт"]
["7","PROFIL-10K-60",1.2,12,1.2000000000000002,826.38085990650723,null,"7","PROFIL-10K-60",1,10,1,821.91345561291712,null,{"$f":"(C4-J4)/C4","v":0.16666666666666663},{"$f":"IF(O4>0,O4,0.2)","v":0.16666666666666663}]
["1","PROFIL-11K-60",1.1000000000000001,11,1.1000000000000001,1122.6038322598251,null,"1","PROFIL-10K-60",1.6,16,1.6,1126.8025304958135,null,{"$f":"(C5-J5)/C5","v":-0.45454545454545453},{"$f":"IF(O5>0,O5,0.2)","v":0.2}]
["8","PROFIL-10K-60",1.4,14,1.4,952.17694859473136,null,"8","PROFIL-10K-60",1.2,12,1.2000000000000002,939.33029290893273,null,0.14285714285714282,0.14285714285714282]
["161","PROFIL-12K-60",1.6,16,1.6,1665.5062319854942,null,"161","PROFIL-11K-60",1.6,16,1.6,1658.1580438819167,null,0,0.2]
["161","PROFIL-12K-60",1.6,16,1.6,1669.9658163230747,null,"161","PROFIL-11K-60",1.6,16,1.6,1665.0830878012921,null,0,0.2]
["165","PROFIL-12K-60",1.6,16,1.6,1666.9676778424207,null,"165","PROFIL-11K-60",1.6,16,1.6,1660.4224873858968,null,0,0.2]
["165","PROFIL-12K-60",1.6,16,1.6,1671.4324197547046,null,"165","PROFIL-11K-60",1.6,16,1.6,1667.3593356119197,null,0,0.2]
["162","PROFIL-12K-60",2,20,2,2114.5653741688116,null,"162","PROFIL-11K-60",2,20,2,2096.4308662838052,null,0,0.2]
["164","PROFIL-12K-60",2,20,2,2088.3203245327136,null,"164","PROFIL-11K-60",2,20,2,2062.6378769288426,null,0,0.2]
["203","PROFIL-10K-60",1.1000000000000001,11,1.1000000000000001,522.28271328902372,null,"203","PROFIL-10K-60",0.9,9,0.9,517.64130333174694,null,0.18181818181818185,0.18181818181818185]
["203","PROFIL-10K-60",1.1000000000000001,11,1.1000000000000001,520.99136190427726,null,"203","PROFIL-10K-60",0.9,9,0.9,518.8867525287759,null,0.18181818181818185,0.18181818181818185]
["203","PROFIL-10K-60",1.1000000000000001,11,1.1000000000000001,521.99212905548848,null,"203","PROFIL-10K-60",0.9,9,0.9,519.5921195403314,null,0.18181818181818185,0.18181818181818185]
["203","PROFIL-10K-60",1.1000000000000001,11,1.1000000000000001,519.53564238118315,null,"203","PROFIL-10K-60",0.9,9,0.9,516.22635372797242,null,0.18181818181818185,0.18181818181818185]
["204","PROFIL-11K-60",1.3,13,1.3,1013.9319345829084,null,"204","PROFIL-11K-60",1.1000000000000001,11,1.1000000000000001,1006.2359869625019,null,0.1538461538461538,0.1538461538461538]
["207","PROFIL-11K-60",1.2,12,1.2000000000000002,931.70265957881293,null,"207","PROFIL-10K-60",1.6,16,1.6,931.79265934243949,null,-0.33333333333333348,0.2]
["208","PROFIL-11K-60",1.6,16,1.6,1170.6899320280925,null,"208","PROFIL-11K-60",1.2,12,1.2000000000000002,1155.2171830825844,null,0.25000000000000006,0.25000000000000006]
["212","PROFIL-11K-60",1.6,16,1.6,1181.6643825192859,null,"212","PROFIL-11K-60",1.2,12,1.2000000000000002,1173.7545694231237,null,0.25000000000000006,0.25000000000000006]
["213","PROFIL-11K-60",1.8,18,1.8,1350.0120996367673,null,"213","PROFIL-11K-60",1.4,14,1.4,1337.5678719614898,null,0.22222222222222229,0.22222222222222229]
["214","PROFIL-11K-60",1.6,16,1.6,1186.1895639194531,null,"214","PROFIL-11K-60",1.3,13,1.3,1181.2390370857127,null,0.18750000000000003,0.18750000000000003]
["234","PROFIL-11K-60",1.6,16,1.6,1208.7033098441755,null,"234","PROFIL-11K-60",1.3,13,1.3,1204.1028624181051,null,0.18750000000000003,0.18750000000000003]
["235","PROFIL-11K-60",1.8,18,1.8,1361.7283486478527,null,"235","PROFIL-11K-60",1.4,14,1.4,1347.1257001282042,null,0.22222222222222229,0.22222222222222229]
["237","PROFIL-11K-60",1.6,16,1.6,1184.953405451746,null,"237","PROFIL-11K-60",1.2,12,1.2000000000000002,1178.6799773830448,null,0.25000000000000006,0.25000000000000006]
["240","PROFIL-11K-60",1.6,16,1.6,1188.5212707374881,null,"240","PROFIL-11K-60",1.3,13,1.3,1177.3085020906694,null,0.18750000000000003,0.18750000000000003]
["241","PROFIL-11K-60",1.2,12,1.2000000000000002,892.14902262031956,null,"241","PROFIL-10K-60",1.6,16,1.6,887.62852986801465,null,-0.33333333333333348,0.2]
["244","PROFIL-11K-60",1.3,13,1.3,1001.6352665258901,null,"244","PROFIL-11K-60",1.1000000000000001,11,1.1000000000000001,996.99011588994347,null,0.1538461538461538,0.1538461538461538]
["245","PROFIL-10K-60",1.1000000000000001,11,1.1000000000000001,501.11979857685918,null,"245","PROFIL-10K-60",0.9,9,0.9,497.96538526099414,null,0.18181818181818185,0.18181818181818185]
["245","PROFIL-10K-60",1.1000000000000001,11,1.1000000000000001,501.3583770589064,null,"245","PROFIL-10K-60",0.9,9,0.9,497.20902688757917,null,0.18181818181818185,0.18181818181818185]
["245","PROFIL-10K-60",1.1000000000000001,11,1.1000000000000001,500.42512136456833,null,"245","PROFIL-10K-60",0.9,9,0.9,497.44912672839928,null,0.18181818181818185,0.18181818181818185]
["245","PROFIL-10K-60",1.1000000000000001,11,1.1000000000000001,500.18131057266925,null,"245","PROFIL-10K-60",0.9,9,0.9,497.05490505306631,null,0.18181818181818185,0.18181818181818185]
["249","PROFIL-10K-60",1.1000000000000001,11,1.1000000000000001,498.53346900853239,null,"249","PROFIL-10K-60",0.9,9,0.9,493.92686517217817,null,0.18181818181818185,0.18181818181818185]
["249","PROFIL-10K-60",1.1000000000000001,11,1.1000000000000001,500.29303939861336,null,"249","PROFIL-10K-60",0.9,9,0.9,496.74374579489762,null,0.18181818181818185,0.18181818181818185]
["249","PROFIL-10K-60",1.1000000000000001,11,1.1000000000000001,501.18930331362611,null,"249","PROFIL-10K-60",0.9,9,0.9,497.06982218971024,null,0.18181818181818185,0.18181818181818185]
["249","PROFIL-10K-60",1.1000000000000001,11,1.1000000000000001,500.43273028056927,null,"249","PROFIL-10K-60",0.9,9,0.9,495.6197946961496,null,0.18181818181818185,0.18181818181818185]
["250","PROFIL-11K-60",1.3,13,1.3,1000.754968969983,null,"250","PROFIL-11K-60",1.1000000000000001,11,1.1000000000000001,994.66406673716142,null,0.1538461538461538,0.1538461538461538]
["252","PROFIL-11K-60",1.4,14,1.4,1065.3068390509638,null,"252","PROFIL-11K-60",1.1000000000000001,11,1.1000000000000001,1062.5686356558824,null,0.21428571428571416,0.21428571428571416]
["253","PROFIL-11K-60",1.3,13,1.3,972.04284040784955,null,"253","PROFIL-10K-60",1.6,16,1.6,960.37589205909796,null,-0.23076923076923078,0.2]
["257","PROFIL-11K-60",1.2,12,1.2000000000000002,909.14886359457989,null,"257","PROFIL-10K-60",1.6,16,1.6,906.40854187503737,null,-0.33333333333333348,0.2]
["258","PROFIL-11K-60",1.3,13,1.3,1014.649116173027,null,"258","PROFIL-11K-60",1,10,1,998.34934266159087,null,0.23076923076923078,0.23076923076923078]
["260","PROFIL-11K-60",1.4,14,1.4,1092.2217215015512,null,"260","PROFIL-11K-60",1.1000000000000001,11,1.1000000000000001,1070.2223543251587,null,0.21428571428571416,0.21428571428571416]
["261","PROFIL-11K-60",1.6,16,1.6,1110.4847911196041,null,"261","PROFIL-11K-60",1.2,12,1.2000000000000002,1103.3412759298283,null,0.25000000000000006,0.25000000000000006]
["218","PROFIL-11K-60",1.4,14,1.4,1081.0254291693595,null,"218","PROFIL-11K-60",1.2,12,1.2000000000000002,1088.3369863932664,null,0.14285714285714282,0.14285714285714282]
["219","PROFIL-11K-60",1.6,16,1.6,1117.794643421681,null,"219","PROFIL-11K-60",1.2,12,1.2000000000000002,1098.7207122777804,null,0.25000000000000006,0.25000000000000006]
["221","PROFIL-11K-60",1.3,13,1.3,971.49491032245567,null,"221","PROFIL-10K-60",1.6,16,1.6,956.09993464391118,null,-0.23076923076923078,0.2]
["222","PROFIL-11K-60",1.2,12,1.2000000000000002,909.08856563653444,null,"222","PROFIL-10K-60",1.6,16,1.6,904.5906150836081,null,-0.33333333333333348,0.2]
["226","PROFIL-11K-60",1.4,14,1.4,1100.6589744124174,null,"226","PROFIL-11K-60",1.2,12,1.2000000000000002,1101.3431857634034,null,0.14285714285714282,0.14285714285714282]
["227","PROFIL-11K-60",1.3,13,1.3,996.40735171117194,null,"227","PROFIL-11K-60",1.1000000000000001,11,1.1000000000000001,995.83441153372962,null,0.1538461538461538,0.1538461538461538]
["229","PROFIL-11K-60",1.3,13,1.3,1013.644962014691,null,"229","PROFIL-11K-60",1.1000000000000001,11,1.1000000000000001,1005.0363685970563,null,0.1538461538461538,0.1538461538461538]
["230","PROFIL-10K-60",1.1000000000000001,11,1.1000000000000001,522.27521040352372,null,"230","PROFIL-10K-60",0.9,9,0.9,520.23782942158277,null,0.18181818181818185,0.18181818181818185]
["230","PROFIL-10K-60",1.1000000000000001,11,1.1000000000000001,521.86497634867555,null,"230","PROFIL-10K-60",0.9,9,0.9,519.93657640453785,null,0.18181818181818185,0.18181818181818185]
["230","PROFIL-10K-60",1.1000000000000001,11,1.1000000000000001,521.78075397763291,null,"230","PROFIL-10K-60",0.9,9,0.9,519.79294145154734,null,0.18181818181818185,0.18181818181818185]
["230","PROFIL-10K-60",1.1000000000000001,11,1.1000000000000001,523.67715330682142,null,"230","PROFIL-10K-60",0.9,9,0.9,518.25386340703528,null,0.18181818181818185,0.18181818181818185]
["303","PROFIL-10K-60",1.1000000000000001,11,1.1000000000000001,522.04238989986379,null,"303","PROFIL-10K-60",0.9,9,0.9,520.23265257988987,null,0.18181818181818185,0.18181818181818185]
["303","PROFIL-10K-60",1.1000000000000001,11,1.1000000000000001,520.75451686019915,null,"303","PROFIL-10K-60",0.9,9,0.9,518.6146134436907,null,0.18181818181818185,0.18181818181818185]
["303","PROFIL-10K-60",1.1000000000000001,11,1.1000000000000001,521.75477697727172,null,"303","PROFIL-10K-60",0.9,9,0.9,520.31750405445155,null,0.18181818181818185,0.18181818181818185]
["303","PROFIL-10K-60",1.1000000000000001,11,1.1000000000000001,519.53411142733705,null,"303","PROFIL-10K-60",0.9,9,0.9,515.93645547741005,null,0.18181818181818185,0.18181818181818185]
["304","PROFIL-11K-60",1.3,13,1.3,1013.4763342344136,null,"304","PROFIL-11K-60",1.1000000000000001,11,1.1000000000000001,1005.7436667591124,null,0.1538461538461538,0.1538461538461538]
["307","PROFIL-11K-60",1.2,12,1.2000000000000002,931.27591709283615,null,"307","PROFIL-10K-60",1.6,16,1.6,931.15910053492348,null,-0.33333333333333348,0.2]
["308","PROFIL-11K-60",1.6,16,1.6,1170.1633761419305,null,"308","PROFIL-11K-60",1.2,12,1.2000000000000002,1154.4451930649768,null,0.25000000000000006,0.25000000000000006]
["312","PROFIL-11K-60",1.6,16,1.6,1181.1298394161342,null,"312","PROFIL-11K-60",1.2,12,1.2000000000000002,1172.9718738457921,null,0.25000000000000006,0.25000000000000006]
["313","PROFIL-11K-60",1.8,18,1.8,1349.4065517056113,null,"313","PROFIL-11K-60",1.4,14,1.4,1337.0963071174672,null,0.22222222222222229,0.22222222222222229]
["314","PROFIL-11K-60",1.6,16,1.6,1185.651902071208,null,"314","PROFIL-11K-60",1.3,13,1.3,1180.4597308009277,null,0.18750000000000003,0.18750000000000003]
["334","PROFIL-11K-60",1.6,16,1.6,1208.5168251031266,null,"334","PROFIL-11K-60",1.3,13,1.3,1203.2932206313476,null,0.18750000000000003,0.18750000000000003]
["335","PROFIL-11K-60",1.8,18,1.8,1361.3108064513106,null,"335","PROFIL-11K-60",1.4,14,1.4,1346.2299901882868,null,0.22222222222222229,0.22222222222222229]
["337","PROFIL-11K-60",1.6,16,1.6,1184.4029110260776,null,"337","PROFIL-11K-60",1.2,12,1.2000000000000002,1177.8798801780451,null,0.25000000000000006,0.25000000000000006]
["340","PROFIL-11K-60",1.6,16,1.6,1187.9595249551903,null,"340","PROFIL-11K-60",1.3,13,1.3,1182.14923309286,null,0.18750000000000003,0.18750000000000003]
["341","PROFIL-11K-60",1.2,12,1.2000000000000002,891.72566597787898,null,"341","PROFIL-10K-60",1.6,16,1.6,887.26160153030935,null,{"$f":"(C69-J69)/C69","v":-0.33333333333333348},{"$f":"IF(O69>0,O69,0.2)","v":0.2}]
["344","PROFIL-11K-60",1.3,13,1.3,1001.1594561198591,null,"344","PROFIL-11K-60",1.1000000000000001,11,1.1000000000000001,996.34352381116105,null,0.1538461538461538,0.1538461538461538]
["345","PROFIL-10K-60",1.1000000000000001,11,1.1000000000000001,500.88010771184349,null,"345","PROFIL-10K-60",0.9,9,0.9,497.81569187996297,null,0.18181818181818185,0.18181818181818185]
["345","PROFIL-10K-60",1.1000000000000001,11,1.1000000000000001,501.11840829264702,null,"345","PROFIL-10K-60",0.9,9,0.9,497.05531501480078,null,0.18181818181818185,0.18181818181818185]
["345","PROFIL-10K-60",1.1000000000000001,11,1.1000000000000001,500.18577339480896,null,"345","PROFIL-10K-60",0.9,9,0.9,497.12014176681527,null,0.18181818181818185,0.18181818181818185]
["345","PROFIL-10K-60",1.1000000000000001,11,1.1000000000000001,499.94209867062472,null,"345","PROFIL-10K-60",0.9,9,0.9,496.72621670914424,null,0.18181818181818185,0.18181818181818185]
["349","PROFIL-10K-60",1.1000000000000001,11,1.1000000000000001,500.63211267664445,null,"349","PROFIL-10K-60",0.9,9,0.9,493.60914705074958,null,0.18181818181818185,0.18181818181818185]
["349","PROFIL-10K-60",1.1000000000000001,11,1.1000000000000001,500.14783004257288,null,"349","PROFIL-10K-60",0.9,9,0.9,496.59574667019893,null,0.18181818181818185,0.18181818181818185]
["349","PROFIL-10K-60",1.1000000000000001,11,1.1000000000000001,501.05534464927086,null,"349","PROFIL-10K-60",0.9,9,0.9,497.2875947194014,null,0.18181818181818185,0.18181818181818185]
["349","PROFIL-10K-60",1.1000000000000001,11,1.1000000000000001,500.24790836449444,null,"349","PROFIL-10K-60",0.9,9,0.9,495.47218929877164,null,0.18181818181818185,0.18181818181818185]
["350","PROFIL-11K-60",1.3,13,1.3,1000.3452922432938,null,"350","PROFIL-11K-60",1.1000000000000001,11,1.1000000000000001,994.03890136873906,null,0.1538461538461538,0.1538461538461538]
["352","PROFIL-11K-60",1.4,14,1.4,1068.0099219349613,null,"352","PROFIL-11K-60",1.1000000000000001,11,1.1000000000000001,1062.3612420733791,null,0.21428571428571416,0.21428571428571416]
["353","PROFIL-11K-60",1.3,13,1.3,971.71199969191662,null,"353","PROFIL-10K-60",1.6,16,1.6,963.48544469075591,null,-0.23076923076923078,0.2]
["357","PROFIL-11K-60",1.2,12,1.2000000000000002,908.84009285321565,null,"357","PROFIL-10K-60",1.6,16,1.6,905.79373214571376,null,-0.33333333333333348,0.2]
["358","PROFIL-11K-60",1.3,13,1.3,1017.4295128269347,null,"358","PROFIL-11K-60",1,10,1,997.67894395329961,null,0.23076923076923078,0.23076923076923078]
["360","PROFIL-11K-60",1.4,14,1.4,1091.7051917015285,null,"360","PROFIL-11K-60",1.1000000000000001,11,1.1000000000000001,1069.5080698791191,null,0.21428571428571416,0.21428571428571416]
["361","PROFIL-11K-60",1.6,16,1.6,1109.9664621783547,null,"361","PROFIL-11K-60",1.2,12,1.2000000000000002,1102.600403132793,null,0.25000000000000006,0.25000000000000006]
["318","PROFIL-11K-60",1.4,14,1.4,1084.8349685438179,null,"318","PROFIL-11K-60",1.2,12,1.2000000000000002,1087.6145670576568,null,0.14285714285714282,0.14285714285714282]
["319","PROFIL-11K-60",1.6,16,1.6,1117.5680042105896,null,"319","PROFIL-11K-60",1.2,12,1.2000000000000002,1098.0026294735831,null,0.25000000000000006,0.25000000000000006]
["321","PROFIL-11K-60",1.3,13,1.3,971.06244298600393,null,"321","PROFIL-10K-60",1.6,16,1.6,955.62918430139348,null,-0.23076923076923078,0.2]
["322","PROFIL-11K-60",1.2,12,1.2000000000000002,908.67753308558213,null,"322","PROFIL-10K-60",1.6,16,1.6,909.20653513367517,null,-0.33333333333333348,0.2]
["326","PROFIL-11K-60",1.4,14,1.4,1100.156662797865,null,"326","PROFIL-11K-60",1.2,12,1.2000000000000002,1101.0071070008705,null,0.14285714285714282,0.14285714285714282]
["327","PROFIL-11K-60",1.3,13,1.3,995.95164718895057,null,"327","PROFIL-11K-60",1.1000000000000001,11,1.1000000000000001,995.18837812159347,null,0.1538461538461538,0.1538461538461538]
["329","PROFIL-11K-60",1.3,13,1.3,1013.196349453262,null,"329","PROFIL-11K-60",1.1000000000000001,11,1.1000000000000001,1004.7293512700023,null,0.1538461538461538,0.1538461538461538]
["330","PROFIL-10K-60",1.1000000000000001,11,1.1000000000000001,522.04017744826376,null,"330","PROFIL-10K-60",0.9,9,0.9,520.04570830527791,null,0.18181818181818185,0.18181818181818185]
["330","PROFIL-10K-60",1.1000000000000001,11,1.1000000000000001,521.63552248467568,null,"330","PROFIL-10K-60",0.9,9,0.9,519.59289903073136,null,0.18181818181818185,0.18181818181818185]
["330","PROFIL-10K-60",1.1000000000000001,11,1.1000000000000001,521.55134275524938,null,"330","PROFIL-10K-60",0.9,9,0.9,519.44937028864354,null,0.18181818181818185,0.18181818181818185]
["330","PROFIL-10K-60",1.1000000000000001,11,1.1000000000000001,523.8782693174669,null,"330","PROFIL-10K-60",0.9,9,0.9,518.05614772784418,null,0.18181818181818185,0.18181818181818185]
["403","PROFIL-10K-60",1.3,13,1.3,599.01725379515585,null,"403","PROFIL-10K-60",1,10,1,595.37683827552121,null,0.23076923076923078,0.23076923076923078]
["403","PROFIL-10K-60",1.3,13,1.3,597.90992579519548,null,"403","PROFIL-10K-60",1,10,1,592.99718820149394,null,0.23076923076923078,0.23076923076923078]
["403","PROFIL-10K-60",1.3,13,1.3,599.03754593497604,null,"403","PROFIL-10K-60",1,10,1,594.62386674905019,null,0.23076923076923078,0.23076923076923078]
["403","PROFIL-10K-60",1.3,13,1.3,598.90122991795977,null,"403","PROFIL-10K-60",1,10,1,590.86377069173432,null,0.23076923076923078,0.23076923076923078]
["404","PROFIL-11K-60",1.8,18,1.8,1280.4960615760933,null,"404","PROFIL-11K-60",1.3,13,1.3,1255.1063402993982,null,0.27777777777777779,0.27777777777777779]
["407","PROFIL-11K-60",1.4,14,1.4,1095.4104213463836,null,"407","PROFIL-11K-60",1.2,12,1.2000000000000002,1092.652568309966,null,0.14285714285714282,0.14285714285714282]
["408","PROFIL-11K-60",1.8,18,1.8,1308.7454507617867,null,"408","PROFIL-11K-60",1.4,14,1.4,1298.6632686926994,null,0.22222222222222229,0.22222222222222229]
["412","PROFIL-11K-60",2,20,2,1478.414928193806,null,"412","PROFIL-11K-60",1.6,16,1.6,1472.1661531477307,null,0.19999999999999996,0.19999999999999996]
["414","PROFIL-11K-60",1.4,14,1.4,1021.1592133707464,null,"414","PROFIL-11K-60",1.1000000000000001,11,1.1000000000000001,1015.023073345418,null,0.21428571428571416,0.21428571428571416]
["434","PROFIL-11K-60",1.4,14,1.4,1085.031980012606,null,"434","PROFIL-11K-60",1.2,12,1.2000000000000002,1086.435496486763,null,0.14285714285714282,0.14285714285714282]
["437","PROFIL-11K-60",2,20,2,1483.8863347502481,null,"437","PROFIL-11K-60",1.6,16,1.6,1479.8088921741796,null,0.19999999999999996,0.19999999999999996]
["441","PROFIL-11K-60",1.4,14,1.4,1049.7170564035439,null,"441","PROFIL-11K-60",1.1000000000000001,11,1.1000000000000001,1050.315327959165,null,0.21428571428571416,0.21428571428571416]
["444","PROFIL-11K-60",1.6,16,1.6,1209.0279431574766,null,"444","PROFIL-11K-60",1.3,13,1.3,1192.6684054756597,null,0.18750000000000003,0.18750000000000003]
["445","PROFIL-10K-60",1.2,12,1.2000000000000002,579.46330527789382,null,"445","PROFIL-10K-60",1,10,1,574.68671743666243,null,0.16666666666666663,0.16666666666666663]
["445","PROFIL-10K-60",1.3,13,1.3,580.8413988025377,null,"445","PROFIL-10K-60",1,10,1,578.65518526927428,null,0.23076923076923078,0.23076923076923078]
["445","PROFIL-10K-60",1.2,12,1.2000000000000002,579.09967039442995,null,"445","PROFIL-10K-60",1,10,1,577.3008184298983,null,0.16666666666666663,0.16666666666666663]
["445","PROFIL-10K-60",1.2,12,1.2000000000000002,578.90165259402704,null,"445","PROFIL-10K-60",1,10,1,577.76705302161827,null,0.16666666666666663,0.16666666666666663]
["449","PROFIL-10K-60",1.3,13,1.3,583.59642211152243,null,"449","PROFIL-10K-60",1,10,1,580.13234143180807,null,0.23076923076923078,0.23076923076923078]
["449","PROFIL-10K-60",1.3,13,1.3,583.40792961160287,null,"449","PROFIL-10K-60",1,10,1,579.14795229446861,null,0.23076923076923078,0.23076923076923078]
["449","PROFIL-10K-60",1.2,12,1.2000000000000002,584.78277952799692,null,"449","PROFIL-10K-60",1,10,1,579.92544158385817,null,0.16666666666666663,0.16666666666666663]
["449","PROFIL-10K-60",1.3,13,1.3,586.52091381354353,null,"449","PROFIL-10K-60",1,10,1,578.10401753310236,null,0.23076923076923078,0.23076923076923078]
["450","PROFIL-11K-60",1.6,16,1.6,1201.2523351326784,null,"450","PROFIL-11K-60",1.3,13,1.3,1189.4442073181785,null,0.18750000000000003,0.18750000000000003]
["452","PROFIL-11K-60",1.8,18,1.8,1276.107086146292,null,"452","PROFIL-11K-60",1.3,13,1.3,1270.4401504799073,null,0.27777777777777779,0.27777777777777779]
["453","PROFIL-11K-60",1.6,16,1.6,1162.4727024478684,null,"453","PROFIL-11K-60",1.2,12,1.2000000000000002,1146.7443951465282,null,0.25000000000000006,0.25000000000000006]
["457","PROFIL-11K-60",1.6,16,1.6,1156.7820100104559,null,"457","PROFIL-11K-60",1.2,12,1.2000000000000002,1157.1137143684839,null,0.25000000000000006,0.25000000000000006]
["458","PROFIL-11K-60",1.8,18,1.8,1326.1140634036674,null,"458","PROFIL-11K-60",1.3,13,1.3,1305.2913928436585,null,0.27777777777777779,0.27777777777777779]
["460","PROFIL-11K-60",1.8,18,1.8,1396.9094248948991,null,"460","PROFIL-11K-60",1.4,14,1.4,1366.8675369910959,null,0.22222222222222229,0.22222222222222229]
["461","PROFIL-11K-60",1.8,18,1.8,1348.7958171685502,null,"461","PROFIL-11K-60",1.4,14,1.4,1342.2050094781646,null,0.22222222222222229,0.22222222222222229]
["418","PROFIL-11K-60",1.8,18,1.8,1340.0170948307971,null,"418","PROFIL-11K-60",1.4,14,1.4,1336.8698939629191,null,0.22222222222222229,0.22222222222222229]
["419","PROFIL-11K-60",1.8,18,1.8,1396.8666613658891,null,"419","PROFIL-11K-60",1.6,16,1.6,1385.7430444420893,null,0.11111111111111108,0.11111111111111108]
["421","PROFIL-11K-60",1.8,18,1.8,1349.7420810566935,null,"421","PROFIL-11K-60",1.4,14,1.4,1325.3102095679724,null,0.22222222222222229,0.22222222222222229]
["422","PROFIL-11K-60",1.6,16,1.6,1153.4110183041323,null,"422","PROFIL-11K-60",1.2,12,1.2000000000000002,1149.9481341882954,null,0.25000000000000006,0.25000000000000006]
["426","PROFIL-11K-60",1.8,18,1.8,1305.1421922694803,null,"426","PROFIL-11K-60",1.4,14,1.4,1284.3856180520916,null,0.22222222222222229,0.22222222222222229]
["427","PROFIL-11K-60",1.6,16,1.6,1214.7211326247302,null,"427","PROFIL-11K-60",1.3,13,1.3,1212.0968668448468,null,0.18750000000000003,0.18750000000000003]
["429","PROFIL-11K-60",1.8,18,1.8,1336.761039710982,null,"429","PROFIL-11K-60",1.4,14,1.4,1320.1079415700399,null,0.22222222222222229,0.22222222222222229]
["430","PROFIL-10K-60",1.3,13,1.3,609.99039168480658,null,"430","PROFIL-10K-60",1.1000000000000001,11,1.1000000000000001,607.922115226149,null,0.1538461538461538,0.1538461538461538]
["430","PROFIL-10K-60",1.3,13,1.3,609.5633179617555,null,"430","PROFIL-10K-60",1.1000000000000001,11,1.1000000000000001,606.31842092043905,null,{"$f":"(C133-J133)/C133","v":0.1538461538461538},{"$f":"IF(O133>0,O133,0.2)","v":0.1538461538461538}]
["430","PROFIL-10K-60",1.3,13,1.3,609.47385932794759,null,"430","PROFIL-10K-60",1.1000000000000001,11,1.1000000000000001,606.15525980238579,null,0.1538461538461538,0.1538461538461538]
["430","PROFIL-10K-60",1.3,13,1.3,606.1797771666877,null,"430","PROFIL-10K-60",1.1000000000000001,11,1.1000000000000001,605.80053580030437,null,0.1538461538461538,0.1538461538461538]
["413","PROFIL-11K-60",1.8,18,1.8,1374.9047789161054,null,"413","PROFIL-11K-60",1.4,14,1.4,1353.4209523582801,null,0.22222222222222229,0.22222222222222229]
["435","PROFIL-11K-60",1.8,18,1.8,1290.7369409091116,null,"435","PROFIL-11K-60",1.3,13,1.3,1274.0020913761048,null,0.27777777777777779,0.27777777777777779]
["440","PROFIL-11K-60",1.8,18,1.8,1342.5691800211944,null,"440","PROFIL-11K-60",1.4,14,1.4,1326.735304989576,null,0.22222222222222229,0.22222222222222229]
[]
[{"$nulls":15},{"$f":"AVERAGE(P4:P139)","v":0.19738799266577031}]

{"sheet":"Лист2","index":1,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[]}

{"sheet":"Лист3","index":2,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[]}