{"text_format":"2","workbook":"xlsx","n_sheets":1,"sheets":["Лист1"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Лист1","index":0,"n_rows":10,"n_cols":38,"rows_kept":10,"cut":false,"hidden":false,"merged":[[9,31,11,31],[9,32,11,32],[9,33,11,33],[9,34,11,34],[9,36,11,36],[9,25,11,25],[9,26,11,26],[9,27,11,27],[9,28,11,28],[9,29,11,29],[9,30,11,30],[9,19,11,19],[9,20,11,20],[9,21,11,21],[9,22,11,22],[9,23,11,23],[9,24,11,24],[9,13,11,13],[9,14,11,14],[9,15,11,15],[9,16,11,16],[9,17,11,17],[9,18,11,18],[9,7,11,7],[9,8,11,8],[9,9,11,9],[9,10,11,10],[9,11,11,11],[9,12,11,12],[6,32,8,32],[6,33,8,33],[6,34,8,34],[6,36,8,36],[9,1,11,1],[9,2,11,2],[9,3,11,3],[9,4,11,4],[9,5,11,5],[9,6,11,6],[6,26,8,26],[6,27,8,27],[6,28,8,28],[6,29,8,29],[6,30,8,30],[6,31,8,31],[6,20,8,20],[6,21,8,21],[6,22,8,22],[6,23,8,23],[6,24,8,24],[6,25,8,25],[6,14,8,14],[6,15,8,15],[6,16,8,16],[6,17,8,17],[6,18,8,18],[6,19,8,19],[6,8,8,8],[6,9,8,9],[6,10,8,10],[6,11,8,11],[6,12,8,12],[6,13,8,13],[1,36,3,36],[1,37,3,37],[5,1,5,37],[6,1,8,1],[6,2,8,2],[6,3,8,3],[6,4,8,4],[6,5,8,5],[6,6,8,6],[6,7,8,7],[1,26,2,30],[1,31,3,31],[1,32,3,32],[1,33,3,33],[1,34,3,34],[1,35,3,35],[1,19,3,19],[1,20,3,20],[1,21,3,21],[1,22,3,22],[1,23,3,23],[1,24,2,25],[1,13,3,13],[1,14,3,14],[1,15,3,15],[1,16,3,16],[1,17,3,17],[1,18,3,18],[1,7,3,7],[1,8,3,8],[1,9,3,9],[1,10,3,10],[1,11,3,11],[1,12,3,12],[1,1,3,1],[1,2,3,2],[1,3,3,3],[1,4,3,4],[1,5,3,5],[1,6,3,6]]}
[]
[null,"№ помещения","Температура помещения","Расчетные теплопотери, Вт","Приведенные теплопотери, Вт","Температура подачи","Температура обратки","Средняя температура","Тепловой напор","Для расчета (тср/т.п)1+п","n","Расход теплоноситея, кг/ч","Для расчета 2 (Расход необх/360)р","р","в","Коэфф учета направления потока","С","Необходимая тепловая мощность, Вт","Кол-во отоп приборов, шт","Необходимая мощность 1 прибора, Вт","Нормированный тепловой напор","Коэфф пересчета","Мощность 1 прибора, Вт  расчетный","Мощность 1 прибора, Вт (каталог) ближайший","Габарит установки",null,"Характеристики и тип прибора (каталог)",{"$nulls":4},"Фактичекая тепловая мощность, Вт","Погрешность на мощность приборов, %","Разница мощности, Вт","Расход теплоносителя через 1 прибор, кг/ч","Расход теплоносителя через 1 прибор, кг/ч","Расход теплоносителя через через группу, кг/ч","Расход теплоносителя через группу, кг/ч"]
[]
[{"$nulls":24},"Высота","Длина","секц","Кол-во секц","Кол-во секц","Длина  секции","длина радиатора"]
[null,1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,16,17,18,19,20,21,22,23,24,25,26,27,28,29,"ширина",31,32,33,34,35,36,37]
[]
[null,"2",20,{"$f":"[1]Лист2!S19+[1]Лист2!S7","v":7168.0262419471992},{"$f":"ROUNDUP(D7,-1)","v":7170},90,70,{"$f":"(F7+G7)/2","v":80},{"$f":"H7-C7","v":60},{"$f":"POWER(H7/I7,1+K7)","v":1.4535178100924679},0.3,{"$f":"0.001*E7/(4.19*(F7-G7))*3600","v":308.01909307875889},{"$f":"POWER(L7/360,N7)","v":1},0,0.99,1,1,{"$f":"E7*J7*O7*M7*P7*Q7","v":10317.505471379365},5,{"$f":"R7/S7","v":2063.5010942758731},70,{"$f":"POWER(I7/U7,1.3)","v":0.81840669500528684},{"$f":"T7/V7","v":2521.3638975210765},2700,0,0,167,{"$f":"X7/AA7","v":16.167664670658684},{"$f":"ROUNDUP(AB7,-0.1)","v":17},80,{"$f":"AD7*AC7","v":1360},{"$f":"X7*S7","v":13500},{"$f":"(AF7-R7)/R7*100%","v":0.30845581206124251},{"$f":"AF7-R7","v":3182.4945286206348},{"$f":"W7*0.86/20","v":108.41864759340629},null,{"$f":"AI7*S7","v":542.09323796703143}]
[]
[]
[null,"2",20,7168,{"$f":"ROUNDUP(D10,-1)","v":7170},90,70,{"$f":"(F10+G10)/2","v":80},{"$f":"H10-C10","v":60},{"$f":"POWER(H10/I10,1+K10)","v":1.4535178100924679},0.3,{"$f":"0.001*E10/(4.19*(F10-G10))*3600","v":308.01909307875889},{"$f":"POWER(L10/360,N10)","v":0.9976635997435932},1.4999999999999999E-2,0.99,0.94,1,{"$f":"E10*J10*O10*M10*P10*Q10","v":9675.7956700135219},5,{"$f":"R10/S10","v":1935.1591340027044},70,{"$f":"POWER(I10/U10,1.3)","v":0.81840669500528684},{"$f":"T10/V10","v":2364.5446033285484},1950,0,0,167,{"$f":"X10/AA10","v":11.676646706586826},{"$f":"ROUNDUP(AB10,-0.1)","v":12},80,{"$f":"AD10*AC10","v":960},{"$f":"X10*S10","v":9750},{"$f":"(AF10-R10)/R10*100%","v":7.6690674872813237E-3},{"$f":"AF10-R10","v":74.204329986478115},{"$f":"W10*0.86/20","v":101.67541794312758},null,{"$f":"AI10*S10","v":508.37708971563791}]