{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["оголенные внутри помещений "],"not_rendered":{"charts":3,"images":0,"macros":0,"external_links":1,"defined_names":5,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"оголенные внутри помещений ","index":0,"n_rows":59,"n_cols":14,"rows_kept":59,"cut":false,"hidden":false,"merged":[[0,1,1,1],[0,2,0,13]],"flags":["formulas_cached_only"]}
[null,"Перепад температур, оC","Тепловые потери трубопровода, ккал/ч м (кДж/ч м), при условном диаметре, мм"]
[null,null,15,20,25,32,40,50,70,80,100,125,150,200]
[null,30,22,28,35,44,48,54,68,80,97,119,143,173]
[null,32,23,30,37,47,50,58,73,85,103,127,152,185]
[null,34,25,32,39,50,53,61,77,91,110,135,162,196]
[null,36,26,33,42,53,56,65,82,95,116,143,171,208]
[null,38,28,35,44,56,60,68,86,102,123,151,181,219]
[null,40,29,37,46,59,63,72,91,107,129,159,190,231]
[null,42,31,39,49,63,67,76,97,114,137,169,202,242]
[null,44,33,42,52,66,71,81,103,121,145,179,214,254]
[null,46,34,44,54,70,75,85,108,127,154,189,226,265]
[null,48,36,46,57,73,79,90,114,134,162,199,238,277]
[null,50,38,48,60,77,83,94,120,140,170,209,250,288]
[null,52,40,51,63,81,87,99,126,147,179,220,263,300]
[null,54,42,53,66,85,91,104,132,155,188,230,276,312]
[null,56,44,56,70,88,95,108,139,162,197,241,289,323]
[null,58,46,58,73,92,99,113,145,170,206,252,302,335]
[null,60,48,61,76,96,104,113,151,177,215,263,315,347]
{"$rows_empty":40}
[30,219,0.6880087911361648,221.05722459204975,189.88815592457073]