{"text_format":"2","workbook":"xlsx","n_sheets":3,"sheets":["Лист1","Лист2","Лист3"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":0,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Лист1","index":0,"n_rows":8,"n_cols":2,"rows_kept":8,"cut":false,"hidden":false,"merged":[]}
["Ассимиляция теплоизбытков (для тёплого периода)."]
[10.25,"Nу, кВт"]
[0.87,"КПД насосов"]
[0.8,"Коэф. загрузки"]
[{"$f":"A2*(1-A3)/A3*A4","v":1.2252873563218392},"Q, кВт"]
[40,"Темп-ра в помещении (не более)"]
[26,"Темп-ра наружная (пар-тры Б)"]
[{"$f":"3.6*A5*1000/(1.005*1.2*(A6-A7))","v":261.25529985540288},"м3/ч"]

{"sheet":"Лист2","index":1,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[]}

{"sheet":"Лист3","index":2,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[]}