{"text_format":"2","workbook":"xls","n_sheets":2,"sheets":["теплотехника","Теплопотери"],"not_rendered":{"charts":0,"images":0,"macros":1,"external_links":1,"defined_names":2,"comments":10,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"теплотехника","index":0,"n_rows":60,"n_cols":7,"rows_kept":60,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
[]
[null,null,"ТЕПЛОТЕХНИЧЕСКИЙ РАСЧЕТ"]
[]
[null,null,"НАРУЖНАЯ СТЕНА1"]
[]
[null,"№ п/п","наименование","Rслоя, м2.оС/Вт","d, мм","l, Вт/моС","r ,кг/м3"]
[null,"1."]
[null,"2."]
[null,"3."]
[null,"4.","ютонг",2.5,500,0.2]
[null,"4."]
[]
[null,"Сопротивление теплопередаче всех слоёв:",null,2.5,"м2 .оС/Вт"]
[null,"·","сопротивление теплопередаче на внутренней пов-сти ограждения",0.1149425287356322,"м2 .оС/Вт"]
[null,"·","сопротивление теплопередаче на наружной пов-сти ограждения",0.043478260869565216,"м2 .оС/Вт"]
[null,null,"Rстена   =",2.6584207896051977,"м2 .оС/Вт"]
[null,null,"kстена   =",0.37616317323056675,"Вт/м2.оС"]
[]
[]
[null,null,"НАРУЖНАЯ СТЕНА2"]
[]
[null,"№ п/п","наименование","Rслоя, м2.оС/Вт","d, мм","l, Вт/моС","r ,кг/м3"]
[null,"1.","Термодревисина",0.0625,25,0.4]
[null,"2.","Воздушный зазор",0.12]
[null,"3.","Поротерм",3.1677018633540373,510,0.161]
[null,"4.","Минвата",0,0,0.046]
[null,"4."]
[]
[null,"Сопротивление теплопередаче всех слоёв:",null,3.3502018633540374,"м2 .оС/Вт"]
[null,"·","сопротивление теплопередаче на внутренней пов-сти ограждения",0.1149425287356322,"м2 .оС/Вт"]
[null,"·","сопротивление теплопередаче на наружной пов-сти ограждения",0.043478260869565216,"м2 .оС/Вт"]
[null,null,"Rстена   =",3.508622652959235,"м2 .оС/Вт"]
[null,null,"kстена   =",0.28501212552925353,"Вт/м2.оС"]
[]
[]
[null,null,"КРОВЛЯ"]
[]
[null,"№ п/п","наименование","Rслоя, м2.оС/Вт","d, мм","l, Вт/моС","r ,кг/м3"]
[null,"1.","Мин.вата",4.347826086956522,200,0.046]
[null,"2."]
[]
[]
[null,"Сопротивление теплопередаче всех слоёв:",null,4.347826086956522,"м2 .оС/Вт"]
[null,"·","сопротивление теплопередаче на внутренней пов-сти ограждения",0.1149425287356322,"м2 .оС/Вт"]
[null,"·","сопротивление теплопередаче на наружной пов-сти ограждения",0.043478260869565216,"м2 .оС/Вт"]
[null,null,"Rкровля   =",4.50624687656172,"м2 .оС/Вт"]
[null,null,"kкровля   =",0.22191416213818338,"Вт/м2.оС"]
[]
[null,null,"ОСНОВАНИЕ"]
[]
[null,"№ п/п","наименование","Rслоя, м2.оС/Вт","d, мм","l, Вт/моС","r ,кг/м3"]
[null,"1."]
[null,"2.","Пеноплекс",1.5625,50,0.032]
[null,"3."]
[]
[null,"Сопротивление теплопередаче всех слоёв:",null,1.5625,"м2 .оС/Вт"]
[null,"·","сопротивление теплопередаче на внутренней пов-сти ограждения",0.1149425287356322,"м2 .оС/Вт"]
[null,"·","сопротивление теплопередаче на наружной пов-сти ограждения",0.043478260869565216,"м2 .оС/Вт"]
[null,null,"Rстена   =",1.7209207896051975,"м2 .оС/Вт"]
[null,null,"kстена   =",0.5810842695609562,"Вт/м2.оС"]

{"sheet":"Теплопотери","index":1,"n_rows":30,"n_cols":21,"rows_kept":30,"cut":false,"hidden":false,"merged":[[6,1,7,1],[6,17,7,17],[3,0,3,1],[4,0,4,1],[6,2,6,7],[4,4,4,19],[5,0,5,19],[6,13,6,16],[6,19,7,19],[6,9,7,9],[6,11,7,11],[6,8,7,8],[29,12,29,14],[10,0,10,19],[9,0,9,19],[6,18,7,18],[6,0,7,0],[6,12,7,12],[7,4,7,5],[6,10,7,10]],"flags":["formulas_cached_only"]}
[]
[null,null,null,"тип ограждения","НС1","ОК1","ДН","ПТ1","ПЛ1","ПЛ2","ПЛ3","ПЛ4"]
[null,null,null,"k, Вт/(м2С)",0.37616317323056675,1.2905034934361,1.6238368267694332,0.22191416213818338,0.27303754266211605,0.17057569296375266,0.0984009840098401,0.0642570281124498]
["москва",null,null,"n",1,1,1,1.3,1,1,1,1]
[-28,null,"град",null,"сопротивления окон, дверей уменьшены на величину сопротивления стены (для облегчения расчета)"]
["ВЕДОМОСТЬ РАСЧЕТА ТЕПЛОПОТЕРЬ "]
["№ пом.","tв, С","Хар-ка ограждения",{"$nulls":5},"расч. наруж. температура, tн С","Dt","Коэф-т теплопередачи, k, Вт/(м2С)","коэф-т n","основные теплопотери, Вт Qo=k*A*(tв-tн)*n","дополнительные теплопотери",null,null,null,"на инфильтрацию, Вт","Бытовые тепловыделения, Вт, Qбыт=21*Ап","Полные теплопотери, Вт"]
[null,null,"Тип","ориентация","Размеры ограждений, м",null,"кол-во, шт.","Площадь А, м2",{"$nulls":5},"с учетом ориентации","при наличие 2х и более стен","на открывание дверей","на неотапливаемые полы"]
[1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,16,17,16,17,18]
[]
["план 1 этажа"]
["гостиная",20,"НС1","С ",32.2,4.5,1,144.9,-28,48,0.37616317323056675,1,2620,0.1,null,null,null,0.1,null,3150]
[null,20,"ОК1","С ",1.4,1.8,4,10.08,-28,48,1.2905034934361,1,630,0.1,null,null,null,0.1,null,760]
[null,20,"ОК1","С ",1.9,1.8,2,6.84,-28,48,1.2905034934361,1,430,0.1,null,null,null,0.1,null,520]
[null,20,"ПТ1","С ",11.6,9,1,104.39999999999999,-28,48,0.22191416213818338,1.3,1450,0.1,null,null,null,0.1,null,1740]
[{"$nulls":18},"всего теплопотерь:",6170,6170]
[]
[]
[]
[]
[{"$nulls":4},1360,453.696]
[]
[]
[{"$nulls":18},"Всего по этажу",0,0]
[]
[]
[]
[]
[]
[{"$nulls":6},"ВСЕГО ПО ЗДАНИЮ",{"$nulls":8},"Вт"]