{"text_format":"2","workbook":"xlsx","n_sheets":1,"sheets":["Lapas1"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":0,"defined_names":0,"comments":1,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Lapas1","index":0,"n_rows":12,"n_cols":9,"rows_kept":12,"cut":false,"hidden":false,"merged":[]}
[]
[{"$nulls":4},{"$f":"IF($AA$5=1,\" \",\"Концентрация\")","v":"Концентрация"},0.3]
[{"$nulls":4},"Температура теплоносителя",70,"°С"]
[]
[]
[null,null,"Теплоноситель",null,null,"тем-ра замерзания, ºС"," Плотность, кг/м3","Теплоемкость, Дж/(кг*К)","Вязкость, м2/с"]
[null,null,"Вода",null,null,0,{"$f":"999.840377+0.0611638*$F$3-0.0077702*$F$3^2+0.00004266*$F$3^3-0.00000012*$F$3^4","v":977.79904299999998},{"$f":"4216.55956404788-3.41468886028714*$F$3+0.118928750860574*$F$3^2-0.00218284779894615*$F$3^3+0.0000237891891163297*$F$3^4-1.38782227132789E-07*$F$3^5+3.43018824949952E-10*$F$3^6","v":4189.8483912835982},{"$f":" (0.616*EXP(-$F$3/15.12)+1.023*EXP(-$F$3/50.165)+0.153)*10^-6","v":4.1244417828098801E-7}]
[null,null,"Раствор этиленгликоля",null,null,{"$f":"(1-0.06982*$F$2-0.3578*$F$2^2)*273.15-273.15","v":-14.517376200000001},{"$f":"658.49825-54.81501*$F$2+664.71643*273.15/($F$3+273.15)+232.72605*$F$2*273.15/($F$3+273.15)-322.61661*(273.15/($F$3+273.15))^2","v":1022.3296339851215},{"$f":"(5.36449+0.78863*$F$2-2.59001*273.15/($F$3+273.15)-2.73187*$F$2*273.15/($F$3+273.15)+1.43759*(273.15/($F$3+273.15))^2)*1000","v":3797.9320164085225},{"$f":"EXP(-4.63024-2.14817*$F$2-12.70106*273.15/($F$3+273.15)+5.40536*$F$2*273.15/($F$3+273.15)+10.9899*(273.15/($F$3+273.15))^2)/$G$8","v":7.828310372615195E-7}]
[null,null,"Раствор пропиленгликоля",null,null,{"$f":"(1-0.03736*$F$2-0.4005*$F$2^2)*273.15-273.15","v":-12.907156950000001},{"$f":"508.41109-182.4082*$F$2+965.76507*273.15/($F$3+273.15)+280.29104*$F$2*273.15/($F$3+273.15)-472.2551*(273.15/($F$3+273.15))^2","v":990.14499667667701},{"$f":"(4.47642+0.60863*$F$2-0.71497*273.15/($F$3+273.15)-1.93855*$F$2*273.15/($F$3+273.15)+0.47873*(273.15/($F$3+273.15))^2)*1000","v":3930.2940786566778},{"$f":"EXP(-1.02798-10.03298*$F$2-19.93497*273.15/($F$3+273.15)+14.65802*$F$2*273.15/($F$3+273.15)+14.6205*(273.15/($F$3+273.15))^2)/$G$9","v":7.9909581714293223E-7}]
[null,null,"Другое"]
[null,null,"Другое"]
[null,null,"Другое"]