{"text_format":"2","workbook":"xls","n_sheets":3,"sheets":["Лист1","Лист2","Лист3"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":0,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Лист1","index":0,"n_rows":73,"n_cols":61,"rows_kept":73,"cut":false,"hidden":false,"merged":[[8,8,8,9],[8,10,8,11],[8,14,8,16],[8,17,8,18],[0,4,0,58],[2,1,2,8],[2,11,2,24],[3,1,3,6],[3,11,3,19],[8,19,8,22],[8,23,8,25],[8,26,8,27],[8,28,8,30],[4,1,4,5],[4,11,4,15],[6,15,6,28],[8,0,8,1],[8,3,8,4],[8,5,8,7],[9,17,9,18],[9,19,9,22],[8,42,8,43],[8,44,8,45],[8,46,8,47],[8,48,8,50],[8,31,8,32],[8,36,8,37],[8,38,8,39],[8,40,8,41],[9,0,9,1],[9,3,9,4],[9,5,9,7],[9,8,9,9],[9,10,9,11],[9,14,9,16],[9,23,9,25],[9,26,9,27],[9,28,9,30],[9,31,9,32],[8,51,8,52],[8,53,8,54],[9,44,9,45],[9,46,9,47],[9,48,9,50],[9,51,9,52],[9,36,9,37],[9,38,9,39],[9,40,9,41],[9,42,9,43],[9,53,9,54],[10,0,10,1],[10,3,10,4],[10,5,10,7],[10,8,10,9],[10,10,10,11],[10,14,10,16],[10,17,10,18],[10,19,10,22],[10,23,10,25],[10,51,10,52],[10,53,10,54],[10,38,10,39],[10,40,10,41],[10,42,10,43],[10,44,10,45],[11,0,11,1],[11,3,11,4],[11,5,11,7],[11,8,11,9],[10,46,10,47],[10,48,10,50],[10,26,10,27],[10,28,10,30],[10,31,10,32],[10,36,10,37],[11,23,11,25],[11,26,11,27],[11,28,11,30],[11,31,11,32],[11,10,11,11],[11,14,11,16],[11,17,11,18],[11,19,11,22],[11,44,11,45],[11,46,11,47],[11,48,11,50],[11,51,11,52],[11,36,11,37],[11,38,11,39],[11,40,11,41],[11,42,11,43],[11,53,11,54],[12,0,12,1],[12,3,12,4],[12,5,12,7],[12,8,12,9],[12,10,12,11],[12,14,12,16],[12,17,12,18],[12,19,12,22],[12,23,12,25],[12,51,12,52],[12,53,12,54],[12,38,12,39],[12,40,12,41],[12,42,12,43],[12,44,12,45],[13,0,13,1],[13,3,13,4],[13,5,13,7],[13,8,13,9],[12,46,12,47],[12,48,12,50],[12,26,12,27],[12,28,12,30],[12,31,12,32],[12,36,12,37],[13,23,13,25],[13,26,13,27],[13,28,13,30],[13,31,13,32],[13,10,13,11],[13,14,13,16],[13,17,13,18],[13,19,13,22],[13,44,13,45],[13,46,13,47],[13,48,13,50],[13,51,13,52],[13,36,13,37],[13,38,13,39],[13,40,13,41],[13,42,13,43],[13,53,13,54],[14,0,14,1],[14,3,14,4],[14,5,14,7],[14,8,14,9],[14,10,14,11],[14,14,14,16],[14,17,14,18],[14,19,14,22],[14,23,14,25],[14,51,14,52],[14,53,14,54],[14,38,14,39],[14,40,14,41],[14,42,14,43],[14,44,14,45],[15,0,15,1],[15,3,15,4],[15,5,15,7],[15,8,15,9],[14,46,14,47],[14,48,14,50],[14,26,14,27],[14,28,14,30],[14,31,14,32],[14,36,14,37],[15,23,15,25],[15,26,15,27],[15,28,15,30],[15,31,15,32],[15,10,15,11],[15,14,15,16],[15,17,15,18],[15,19,15,22],[15,44,15,45],[15,46,15,47],[15,48,15,50],[15,51,15,52],[15,36,15,37],[15,38,15,39],[15,40,15,41],[15,42,15,43],[15,53,15,54],[16,0,16,1],[16,3,16,4],[16,5,16,7],[16,8,16,9],[16,10,16,11],[16,14,16,16],[16,17,16,18],[16,19,16,22],[16,23,16,25],[16,51,16,52],[16,53,16,54],[16,38,16,39],[16,40,16,41],[16,42,16,43],[16,44,16,45],[17,0,17,1],[17,3,17,4],[17,5,17,7],[17,8,17,9],[16,46,16,47],[16,48,16,50],[16,26,16,27],[16,28,16,30],[16,31,16,32],[16,36,16,37],[17,23,17,25],[17,26,17,27],[17,28,17,30],[17,31,17,32],[17,10,17,11],[17,14,17,16],[17,17,17,18],[17,19,17,22],[17,44,17,45],[17,46,17,47],[17,48,17,50],[17,51,17,52],[17,36,17,37],[17,38,17,39],[17,40,17,41],[17,42,17,43],[17,53,17,54],[18,0,18,1],[18,3,18,4],[18,5,18,7],[18,8,18,9],[18,10,18,11],[18,14,18,16],[18,17,18,18],[18,19,18,22],[18,23,18,25],[18,51,18,52],[18,53,18,54],[18,38,18,39],[18,40,18,41],[18,42,18,43],[18,44,18,45],[19,0,19,1],[19,3,19,4],[19,5,19,7],[19,8,19,9],[18,46,18,47],[18,48,18,50],[18,26,18,27],[18,28,18,30],[18,31,18,32],[18,36,18,37],[19,23,19,25],[19,26,19,27],[19,28,19,30],[19,31,19,32],[19,10,19,11],[19,14,19,16],[19,17,19,18],[19,19,19,22],[19,44,19,45],[19,46,19,47],[19,48,19,50],[19,51,19,52],[19,36,19,37],[19,38,19,39],[19,40,19,41],[19,42,19,43],[19,53,19,54],[20,0,20,1],[20,3,20,4],[20,5,20,7],[20,8,20,9],[20,10,20,11],[20,14,20,16],[20,17,20,18],[20,19,20,22],[20,23,20,25],[20,51,20,52],[20,53,20,54],[20,38,20,39],[20,40,20,41],[20,42,20,43],[20,44,20,45],[21,0,21,1],[21,3,21,4],[21,5,21,7],[21,8,21,9],[20,46,20,47],[20,48,20,50],[20,26,20,27],[20,28,20,30],[20,31,20,32],[20,36,20,37],[21,23,21,25],[21,26,21,27],[21,28,21,30],[21,31,21,32],[21,10,21,11],[21,14,21,16],[21,17,21,18],[21,19,21,22],[21,44,21,45],[21,46,21,47],[21,48,21,50],[21,51,21,52],[21,36,21,37],[21,38,21,39],[21,40,21,41],[21,42,21,43],[21,53,21,54],[22,0,22,1],[22,3,22,4],[22,5,22,7],[22,8,22,9],[22,10,22,11],[22,14,22,16],[22,17,22,18],[22,19,22,22],[22,23,22,25],[22,51,22,52],[22,53,22,54],[22,38,22,39],[22,40,22,41],[22,42,22,43],[22,44,22,45],[23,0,23,1],[23,3,23,4],[23,5,23,7],[23,8,23,9],[22,46,22,47],[22,48,22,50],[22,26,22,27],[22,28,22,30],[22,31,22,32],[22,36,22,37],[23,23,23,25],[23,26,23,27],[23,28,23,30],[23,31,23,32],[23,10,23,11],[23,14,23,16],[23,17,23,18],[23,19,23,22],[23,44,23,45],[23,46,23,47],[23,48,23,50],[23,51,23,52],[23,36,23,37],[23,38,23,39],[23,40,23,41],[23,42,23,43],[23,53,23,54],[24,0,24,1],[24,3,24,4],[24,5,24,7],[24,8,24,9],[24,10,24,11],[24,14,24,16],[24,17,24,18],[24,19,24,22],[24,23,24,25],[24,51,24,52],[24,53,24,54],[24,38,24,39],[24,40,24,41],[24,42,24,43],[24,44,24,45],[25,0,25,1],[25,3,25,4],[25,5,25,7],[25,8,25,9],[24,46,24,47],[24,48,24,50],[24,26,24,27],[24,28,24,30],[24,31,24,32],[24,36,24,37],[25,23,25,25],[25,26,25,27],[25,28,25,30],[25,31,25,32],[25,10,25,11],[25,14,25,16],[25,17,25,18],[25,19,25,22],[25,44,25,45],[25,46,25,47],[25,48,25,50],[25,51,25,52],[25,36,25,37],[25,38,25,39],[25,40,25,41],[25,42,25,43],[25,53,25,54],[26,0,26,1],[26,3,26,4],[26,5,26,7],[26,8,26,9],[26,10,26,11],[26,14,26,16],[26,17,26,18],[26,19,26,22],[26,23,26,25],[26,31,26,32],[27,0,27,1],[27,3,27,4],[27,5,27,7],[27,8,27,9],[27,10,27,11],[27,14,27,16],[27,17,27,18],[29,17,29,18],[27,19,27,22],[27,23,27,25],[27,26,27,27],[27,28,27,30],[26,26,26,27],[26,28,26,30],[30,3,30,4],[30,5,30,7],[30,8,30,9],[27,31,27,32],[29,0,29,1],[29,3,29,4],[29,5,29,7],[29,8,29,9],[29,10,29,11],[29,14,29,16],[33,22,33,62],[35,50,35,63],[37,4,37,58],[39,1,39,8],[39,11,39,24],[30,10,30,11],[30,14,30,16],[30,17,30,18],[32,22,32,61],[30,0,30,1],[45,14,45,17],[45,18,45,20],[45,21,45,23],[45,24,45,26],[40,1,40,6],[40,11,40,19],[41,1,41,5],[41,11,41,15],[45,27,45,29],[45,30,45,31],[45,32,45,33],[45,34,45,36],[43,15,43,28],[45,0,45,1],[45,3,45,4],[45,5,45,7],[45,8,45,9],[45,10,45,11],[45,45,45,46],[45,47,45,48],[45,49,45,51],[45,52,45,53],[45,37,45,38],[45,39,45,40],[45,41,45,42],[45,43,45,44],[45,54,45,55],[45,58,45,59],[46,0,46,1],[46,3,46,4],[46,5,46,7],[46,8,46,9],[46,10,46,11],[46,14,46,17],[46,18,46,20],[46,21,46,23],[46,39,46,40],[46,41,46,42],[46,24,46,26],[46,27,46,29],[46,30,46,31],[46,32,46,33],[46,58,46,59],[47,0,47,1],[47,3,47,4],[47,5,47,7],[47,8,47,9],[47,10,47,11],[47,14,47,17],[47,18,47,20],[46,43,46,44],[46,45,46,46],[47,21,47,23],[47,24,47,26],[47,27,47,29],[47,30,47,31],[46,52,46,53],[46,54,46,55],[46,47,46,48],[46,49,46,51],[46,34,46,36],[46,37,46,38],[47,54,47,55],[47,58,47,59],[47,41,47,42],[47,43,47,44],[47,45,47,46],[47,47,47,48],[48,0,48,1],[48,3,48,4],[48,5,48,7],[48,8,48,9],[47,49,47,51],[47,52,47,53],[47,32,47,33],[47,34,47,36],[47,37,47,38],[47,39,47,40],[48,24,48,26],[48,27,48,29],[48,30,48,31],[48,32,48,33],[48,10,48,11],[48,14,48,17],[48,18,48,20],[48,21,48,23],[48,43,48,44],[48,45,48,46],[48,47,48,48],[48,49,48,51],[48,34,48,36],[48,37,48,38],[48,39,48,40],[48,41,48,42],[48,52,48,53],[48,54,48,55],[48,58,48,59],[49,0,49,1],[49,3,49,4],[49,5,49,7],[49,8,49,9],[49,10,49,11],[49,14,49,17],[49,18,49,20],[49,32,49,33],[49,34,49,36],[49,37,49,38],[49,39,49,40],[49,21,49,23],[49,24,49,26],[49,27,49,29],[49,30,49,31],[49,49,49,51],[49,52,49,53],[49,54,49,55],[49,58,49,59],[49,41,49,42],[49,43,49,44],[49,45,49,46],[49,47,49,48],[50,10,50,11],[50,14,50,17],[50,18,50,20],[50,21,50,23],[50,0,50,1],[50,3,50,4],[50,5,50,7],[50,8,50,9],[50,39,50,40],[50,41,50,42],[50,24,50,26],[50,27,50,29],[50,30,50,31],[50,32,50,33],[50,58,50,59],[51,0,51,1],[51,3,51,4],[51,5,51,7],[51,8,51,9],[51,10,51,11],[51,14,51,17],[51,18,51,20],[50,43,50,44],[50,45,50,46],[51,21,51,23],[51,24,51,26],[51,27,51,29],[51,30,51,31],[50,52,50,53],[50,54,50,55],[50,47,50,48],[50,49,50,51],[50,34,50,36],[50,37,50,38],[51,54,51,55],[51,58,51,59],[51,41,51,42],[51,43,51,44],[51,45,51,46],[51,47,51,48],[52,0,52,1],[52,3,52,4],[52,5,52,7],[52,8,52,9],[51,49,51,51],[51,52,51,53],[51,32,51,33],[51,34,51,36],[51,37,51,38],[51,39,51,40],[52,24,52,26],[52,27,52,29],[52,30,52,31],[52,32,52,33],[52,10,52,11],[52,14,52,17],[52,18,52,20],[52,21,52,23],[52,43,52,44],[52,45,52,46],[52,47,52,48],[52,49,52,51],[52,34,52,36],[52,37,52,38],[52,39,52,40],[52,41,52,42],[52,52,52,53],[52,54,52,55],[52,58,52,59],[53,0,53,1],[53,3,53,4],[53,5,53,7],[53,8,53,9],[53,10,53,11],[53,14,53,17],[53,18,53,20],[53,32,53,33],[53,34,53,36],[53,37,53,38],[53,39,53,40],[53,21,53,23],[53,24,53,26],[53,27,53,29],[53,30,53,31],[53,49,53,51],[53,52,53,53],[53,54,53,55],[53,58,53,59],[53,41,53,42],[53,43,53,44],[53,45,53,46],[53,47,53,48],[54,10,54,11],[54,14,54,17],[54,18,54,20],[54,21,54,23],[54,0,54,1],[54,3,54,4],[54,5,54,7],[54,8,54,9],[54,39,54,40],[54,41,54,42],[54,24,54,26],[54,27,54,29],[54,30,54,31],[54,32,54,33],[54,58,54,59],[55,0,55,1],[55,3,55,4],[55,5,55,7],[55,8,55,9],[55,10,55,11],[55,14,55,17],[55,18,55,20],[54,43,54,44],[54,45,54,46],[55,21,55,23],[55,24,55,26],[55,27,55,29],[55,30,55,31],[54,52,54,53],[54,54,54,55],[54,47,54,48],[54,49,54,51],[54,34,54,36],[54,37,54,38],[55,54,55,55],[55,58,55,59],[55,41,55,42],[55,43,55,44],[55,45,55,46],[55,47,55,48],[56,0,56,1],[56,3,56,4],[56,5,56,7],[56,8,56,9],[55,49,55,51],[55,52,55,53],[55,32,55,33],[55,34,55,36],[55,37,55,38],[55,39,55,40],[56,24,56,26],[56,27,56,29],[56,30,56,31],[56,32,56,33],[56,10,56,11],[56,14,56,17],[56,18,56,20],[56,21,56,23],[56,43,56,44],[56,45,56,46],[56,47,56,48],[56,49,56,51],[56,34,56,36],[56,37,56,38],[56,39,56,40],[56,41,56,42],[56,52,56,53],[56,54,56,55],[56,58,56,59],[57,0,57,1],[57,3,57,4],[57,5,57,7],[57,8,57,9],[57,10,57,11],[57,14,57,17],[57,18,57,20],[57,32,57,33],[57,34,57,36],[57,37,57,38],[57,39,57,40],[57,21,57,23],[57,24,57,26],[57,27,57,29],[57,30,57,31],[57,49,57,51],[57,52,57,53],[57,54,57,55],[57,58,57,59],[57,41,57,42],[57,43,57,44],[57,45,57,46],[57,47,57,48],[58,10,58,11],[58,14,58,17],[58,18,58,20],[58,21,58,23],[58,0,58,1],[58,3,58,4],[58,5,58,7],[58,8,58,9],[58,39,58,40],[58,41,58,42],[58,24,58,26],[58,27,58,29],[58,30,58,31],[58,32,58,33],[58,58,58,59],[59,0,59,1],[59,3,59,4],[59,5,59,7],[59,8,59,9],[59,10,59,11],[59,14,59,17],[59,18,59,20],[58,43,58,44],[58,45,58,46],[59,21,59,23],[59,24,59,26],[59,27,59,29],[59,30,59,31],[58,52,58,53],[58,54,58,55],[58,47,58,48],[58,49,58,51],[58,34,58,36],[58,37,58,38],[59,54,59,55],[59,58,59,59],[59,41,59,42],[59,43,59,44],[59,45,59,46],[59,47,59,48],[60,0,60,1],[60,3,60,4],[60,5,60,7],[60,8,60,9],[59,49,59,51],[59,52,59,53],[59,32,59,33],[59,34,59,36],[59,37,59,38],[59,39,59,40],[60,24,60,26],[60,27,60,29],[60,30,60,31],[60,32,60,33],[60,10,60,11],[60,14,60,17],[60,18,60,20],[60,21,60,23],[60,43,60,44],[60,45,60,46],[60,47,60,48],[60,49,60,51],[60,34,60,36],[60,37,60,38],[60,39,60,40],[60,41,60,42],[60,52,60,53],[60,54,60,55],[60,58,60,59],[61,0,61,1],[61,3,61,4],[61,5,61,7],[61,8,61,9],[61,10,61,11],[61,14,61,17],[61,18,61,20],[61,32,61,33],[61,34,61,36],[61,37,61,38],[61,39,61,40],[61,21,61,23],[61,24,61,26],[61,27,61,29],[61,30,61,31],[61,49,61,51],[61,52,61,53],[61,54,61,55],[61,58,61,59],[61,41,61,42],[61,43,61,44],[61,45,61,46],[61,47,61,48],[62,10,62,11],[62,14,62,17],[62,18,62,20],[62,21,62,23],[62,0,62,1],[62,3,62,4],[62,5,62,7],[62,8,62,9],[62,39,62,40],[62,41,62,42],[62,24,62,26],[62,27,62,29],[62,30,62,31],[62,32,62,33],[62,58,62,59],[63,0,63,1],[63,3,63,4],[63,5,63,7],[63,8,63,9],[63,10,63,11],[63,14,63,17],[63,18,63,20],[62,43,62,44],[62,45,62,46],[63,21,63,23],[63,24,63,26],[63,27,63,29],[63,30,63,31],[62,52,62,53],[62,54,62,55],[62,47,62,48],[62,49,62,51],[62,34,62,36],[62,37,62,38],[64,32,64,33],[63,32,63,33],[63,34,63,36],[64,0,64,1],[64,3,64,4],[64,5,64,7],[64,8,64,9],[64,10,64,11],[64,14,64,17],[64,18,64,20],[66,14,66,17],[66,18,66,20],[66,21,66,23],[64,24,64,26],[64,27,64,29],[64,30,64,31],[64,21,64,23],[67,0,67,1],[67,3,67,4],[67,5,67,7],[67,8,67,9],[64,34,64,36],[66,0,66,1],[66,3,66,4],[66,5,66,7],[66,8,66,9],[66,10,66,11],[69,22,69,61],[70,22,70,62],[72,50,72,63],[67,10,67,11],[67,14,67,17],[67,18,67,20],[67,21,67,23]],"flags":["formulas_cached_only"]}
[{"$nulls":4},"Отчет составлен на основании архивных данных тепловычислителя ВКТ-7-04, зав. №00206746"]
[]
[null,"Температура холодной воды tхв: 5,00 °C",{"$nulls":9},"Суточные данные за период с 01.01.16 по 17.01.16"]
[null,"Номер активной базы данных: 1",{"$nulls":9},"Поставщик: МУП \"Тамбовинвестсервис\""]
[null,"Схема теплопотребления №3",{"$nulls":9},"Потребитель: Энгельса, 27"]
[]
[{"$nulls":15},"Тепловой ввод 1 (отопление)"]
[]
["Дата",null,"Qо, Гкал","Qг, Гкал",null,"M1, т",null,null,"M2, т",null,"Mг, т",null,"V1, м3","V2, м3","ВНР, ч",null,null,"ВОС, ч",null,"t1, °C",null,null,null,"t2, °C",null,null,"dt, °C",null,"P1,\nкгс/см2",null,null,"P2,\nкгс/см2",null,"НС\nQо","НС\nQг","НС\nM1","НС\nM2",null,"НС\nMг",null,"НС\nV1",null,"НС\nV2",null,"НС\nt1",null,"НС\nt2",null,"НС\ndt",null,null,"НС\nP1",null,"НС\nP2"]
["01.01.2016",null,1.469,0,null,40.88,null,null,40.88,null,0,null,42.56,41.13,"24",null,null,"0",null,85.61,null,null,null,49.71,null,null,35.9,null,6.66,null,null,5.76,null,0,0,0,0,null,0,null,0,null,0,null,0,null,0,null,0,null,null,0,null,0]
["02.01.2016",null,1.55,0,null,40.12,null,null,40.12,null,0,null,41.86,40.38,"24",null,null,"0",null,89.23,null,null,null,50.6,null,null,38.63,null,6.67,null,null,5.81,null,0,0,0,0,null,0,null,0,null,0,null,0,null,0,null,0,null,null,0,null,0]
["03.01.2016",null,1.756,0,null,42.46,null,null,42.46,null,0,null,44.52,42.84,"24",null,null,"0",null,95.47,null,null,null,54.19,null,null,41.28,null,6.87,null,null,5.86,null,0,0,0,0,null,0,null,0,null,0,null,0,null,0,null,0,null,null,0,null,0]
["04.01.2016",null,1.609,0,null,38.82,null,null,38.82,null,0,null,40.74,39.21,"24",null,null,"0",null,97.07,null,null,null,55.65,null,null,41.42,null,5.95,null,null,5.01,null,2,0,0,0,null,2,null,0,null,0,null,0,null,0,null,0,null,null,0,null,0]
["05.01.2016",null,1.824,0,null,43.8,null,null,43.8,null,0,null,46.06,44.29,"24",null,null,"0",null,97.86,null,null,null,56.29,null,null,41.57,null,6.77,null,null,5.69,null,0,0,0,0,null,0,null,0,null,0,null,0,null,0,null,0,null,null,0,null,0]
["06.01.2016",null,1.582,0,null,42.55,null,null,42.55,null,0,null,44.4,42.9,"24",null,null,"0",null,90.5,null,null,null,53.38,null,null,37.12,null,6.7,null,null,5.74,null,0,0,0,0,null,0,null,0,null,0,null,0,null,0,null,0,null,null,0,null,0]
["07.01.2016",null,1.328,0,null,41.21,null,null,41.21,null,0,null,42.71,41.51,"24",null,null,"0",null,81.15,null,null,null,48.92,null,null,32.23,null,6.62,null,null,5.77,null,0,0,0,0,null,0,null,0,null,0,null,0,null,0,null,0,null,null,0,null,0]
["08.01.2016",null,1.193,0,null,40.39,null,null,40.39,null,0,null,41.73,40.67,"24",null,null,"0",null,76.25,null,null,null,46.68,null,null,29.57,null,6.58,null,null,5.8,null,0,0,0,0,null,0,null,0,null,0,null,0,null,0,null,0,null,null,0,null,0]
["09.01.2016",null,1.144,0,null,46.11,null,null,46.11,null,0,null,47.48,46.39,"24",null,null,"0",null,71.56,null,null,null,46.66,null,null,24.9,null,6.92,null,null,5.89,null,0,0,0,0,null,0,null,0,null,0,null,0,null,0,null,0,null,null,0,null,0]
["10.01.2016",null,1.414,0,null,42.69,null,null,42.69,null,0,null,44.25,42.99,"24",null,null,"0",null,83.28,null,null,null,50.1,null,null,33.18,null,6.76,null,null,5.82,null,0,0,0,0,null,0,null,0,null,0,null,0,null,0,null,0,null,null,0,null,0]
["11.01.2016",null,1.653,0,null,39.64,null,null,39.64,null,0,null,41.49,40,"24",null,null,"0",null,95.52,null,null,null,53.94,null,null,41.58,null,6.72,null,null,5.85,null,0,0,0,0,null,0,null,0,null,0,null,0,null,0,null,0,null,null,0,null,0]
["12.01.2016",null,1.373,0,null,37.95,null,null,37.95,null,0,null,39.49,38.2,"24",null,null,"0",null,85.86,null,null,null,49.63,null,null,36.23,null,6.57,null,null,5.84,null,0,0,0,0,null,0,null,0,null,0,null,0,null,0,null,0,null,null,0,null,0]
["13.01.2016",null,1.001,0,null,41.99,null,null,41.99,null,0,null,43.19,42.13,"23",null,null,"1",null,67.67,null,null,null,43.75,null,null,23.92,null,6.9,null,null,5.98,null,4,4,4,4,null,4,null,4,null,4,null,0,null,0,null,0,null,null,0,null,0]
["14.01.2016",null,1.134,0,null,50.56,null,null,50.56,null,0,null,52.09,50.8,"24",null,null,"0",null,68.89,null,null,null,46.49,null,null,22.4,null,7.26,null,null,5.97,null,0,0,0,0,null,0,null,0,null,0,null,0,null,0,null,0,null,null,0,null,0]
["15.01.2016",null,1.339,0,null,52.09,null,null,52.09,null,0,null,53.93,52.45,"24",null,null,"0",null,76.25,null,null,null,50.54,null,null,25.71,null,7.33,null,null,5.9,null,0,0,0,0,null,0,null,0,null,0,null,0,null,0,null,0,null,null,0,null,0]
["16.01.2016",null,1.194,0,null,40.97,null,null,40.97,null,0,null,42.4,41.21,"24",null,null,"0",null,76.86,null,null,null,47.67,null,null,29.19,null,6.5,null,null,5.67,null,0,0,0,0,null,0,null,0,null,0,null,0,null,0,null,0,null,null,0,null,0]
["17.01.2016",null,1.048,0,null,40.12,null,null,40.12,null,0,null,41.37,40.32,"24",null,null,"0",null,70.5,null,null,null,44.35,null,null,26.15,null,6.46,null,null,5.7,null,0,0,0,0,null,0,null,0,null,0,null,0,null,0,null,0,null,null,0,null,0]
["Среднее",null,1.389,0,null,42.491,null,null,42.491,null,0,null,44.134,42.789,23.9,null,null,0.1,null,82.91,null,null,null,49.91,null,null,33,null,6.72,null,null,5.768]
["Итого",null,23.611,0,null,722.35,null,null,722.35,null,0,null,750.27,727.42,407,null,null,1,null,82.91,null,null,null,49.91,null,null,33,null,6.72,null,null,5.768]
[]
["На 01.01.16",null,110.193,0.022,null,4983.66,null,null,5879.92,null,-896.26,null,5115.69,5929.62,6847,null,null,29]
["На 17.01.16",null,133.804,0.022,null,5706.01,null,null,6602.27,null,-896.26,null,5865.96,6657.04,7254,null,null,30]
[]
[{"$nulls":22},"Ответственный за учет тепловой энергии: _____________________________"]
[{"$nulls":22},"Отчет принят   \"      \" ____________ 20___г.   ______________ /___________________________/"]
[]
[{"$nulls":50},"Страница 1 из 2"]
[]
[{"$nulls":4},"Отчет составлен на основании архивных данных тепловычислителя ВКТ-7-04, зав. №00206746"]
[]
[null,"Температура холодной воды tхв: 5,00 °C",{"$nulls":9},"Суточные данные за период с 01.01.16 по 17.01.16"]
[null,"Номер активной базы данных: 1",{"$nulls":9},"Поставщик: МУП \"Тамбовинвестсервис\""]
[null,"Схема теплопотребления №3",{"$nulls":9},"Потребитель: Энгельса, 27"]
[]
[{"$nulls":15},"Тепловой ввод 2 (отопление)"]
[]
["Дата",null,"Qо, Гкал","Qг, Гкал",null,"M1, т",null,null,"M2, т",null,"Mг, т",null,"V1, м3","V2, м3","V3, м3",null,null,null,"ВНР, ч",null,null,"ВОС, ч",null,null,"t1, °C",null,null,"t2, °C",null,null,"dt, °C",null,"P1,\nкгс/см2",null,"P2,\nкгс/см2",null,null,"НС\nQо",null,"НС\nQг",null,"НС\nM1",null,"НС\nM2",null,"НС\nMг",null,"НС\nV1",null,"НС\nV2",null,null,"НС\nV3",null,"НС\nt1",null,"НС\nt2","НС\ndt","НС\nP1",null,"НС\nP2"]
["01.01.2016",null,1.819,0.106,null,39.04,null,null,36.07,null,2.97,null,40.31,36.31,21.65,null,null,null,"24",null,null,"0",null,null,85.09,null,null,41.28,null,null,43.81,null,6,null,4,null,null,0,null,0,null,0,null,0,null,2,null,0,null,0,null,null,0,null,0,null,0,0,0,null,0]
["02.01.2016",null,1.914,0.109,null,38.36,null,null,35.4,null,2.96,null,39.67,35.64,25.18,null,null,null,"24",null,null,"0",null,null,88.65,null,null,41.63,null,null,47.02,null,6,null,4,null,null,0,null,0,null,0,null,0,null,2,null,0,null,0,null,null,0,null,0,null,0,0,0,null,0]
["03.01.2016",null,2.181,0.125,null,40.59,null,null,37.4,null,3.19,null,42.17,37.74,25.64,null,null,null,"24",null,null,"0",null,null,94.81,null,null,44.17,null,null,50.64,null,6,null,4,null,null,0,null,0,null,0,null,0,null,2,null,0,null,0,null,null,0,null,0,null,0,0,0,null,0]
["04.01.2016",null,2.018,0.116,null,37.05,null,null,34.15,null,2.9,null,38.54,34.54,22.86,null,null,null,"24",null,null,"0",null,null,96.31,null,null,45.14,null,null,51.17,null,6,null,4,null,null,2,null,0,null,0,null,0,null,2,null,0,null,0,null,null,0,null,0,null,0,0,0,null,0]
["05.01.2016",null,2.303,0.141,null,41.89,null,null,38.49,null,3.4,null,43.57,38.97,25.68,null,null,null,"24",null,null,"0",null,null,97.18,null,null,45.61,null,null,51.57,null,6,null,4,null,null,0,null,0,null,0,null,0,null,2,null,0,null,0,null,null,0,null,0,null,0,0,0,null,0]
["06.01.2016",null,2.011,0.12,null,40.61,null,null,37.5,null,3.11,null,42.04,37.83,26,null,null,null,"24",null,null,"0",null,null,89.96,null,null,43.44,null,null,46.52,null,6,null,4,null,null,0,null,0,null,0,null,0,null,2,null,0,null,0,null,null,0,null,0,null,0,0,0,null,0]
["07.01.2016",null,1.698,0.101,null,39.31,null,null,36.41,null,2.9,null,40.46,36.65,21.94,null,null,null,"24",null,null,"0",null,null,80.64,null,null,40.05,null,null,40.59,null,6,null,4,null,null,0,null,0,null,0,null,0,null,2,null,0,null,0,null,null,0,null,0,null,0,0,0,null,0]
["08.01.2016",null,1.527,0.094,null,38.5,null,null,35.75,null,2.75,null,39.52,35.99,23.93,null,null,null,"24",null,null,"0",null,null,75.78,null,null,38.46,null,null,37.32,null,6,null,4,null,null,0,null,0,null,0,null,0,null,2,null,0,null,0,null,null,0,null,0,null,0,0,0,null,0]
["09.01.2016",null,1.526,0.109,null,43.96,null,null,40.8,null,3.16,null,44.93,41.04,24.99,null,null,null,"24",null,null,"0",null,null,71.22,null,null,38.92,null,null,32.3,null,6,null,4,null,null,0,null,0,null,0,null,0,null,2,null,0,null,0,null,null,0,null,0,null,0,0,0,null,0]
["10.01.2016",null,1.792,0.104,null,40.66,null,null,37.77,null,2.89,null,41.91,38.01,29.11,null,null,null,"24",null,null,"0",null,null,82.69,null,null,41.15,null,null,41.54,null,6,null,4,null,null,0,null,0,null,0,null,0,null,2,null,0,null,0,null,null,0,null,0,null,0,0,0,null,0]
["11.01.2016",null,2.046,0.112,null,37.93,null,null,35.09,null,2.84,null,39.4,35.33,24.31,null,null,null,"24",null,null,"0",null,null,94.76,null,null,43.79,null,null,50.97,null,6,null,4,null,null,0,null,0,null,0,null,0,null,2,null,0,null,0,null,null,0,null,0,null,0,0,0,null,0]
["12.01.2016",null,1.722,0.095,null,36.27,null,null,33.53,null,2.74,null,37.46,33.77,23.69,null,null,null,"24",null,null,"0",null,null,85.29,null,null,40.49,null,null,44.8,null,6,null,4,null,null,0,null,0,null,0,null,0,null,2,null,0,null,0,null,null,0,null,0,null,0,0,0,null,0]
["13.01.2016",null,1.317,0.096,null,40,null,null,37.04,null,2.96,null,40.8,37.27,24.39,null,null,null,"23",null,null,"1",null,null,67.34,null,null,36.76,null,null,30.58,null,6,null,4,null,null,4,null,4,null,4,null,4,null,6,null,4,null,4,null,null,4,null,0,null,0,0,0,null,0]
["14.01.2016",null,1.519,0.12,null,48.17,null,null,44.66,null,3.51,null,49.17,44.9,26.2,null,null,null,"24",null,null,"0",null,null,68.58,null,null,39.51,null,null,29.07,null,6,null,4,null,null,0,null,0,null,0,null,0,null,2,null,0,null,0,null,null,0,null,0,null,0,0,0,null,0]
["15.01.2016",null,1.784,0.14,null,49.6,null,null,45.86,null,3.74,null,50.94,46.32,24.73,null,null,null,"24",null,null,"0",null,null,75.86,null,null,42.73,null,null,33.13,null,6,null,4,null,null,0,null,0,null,0,null,0,null,2,null,0,null,0,null,null,0,null,0,null,0,0,0,null,0]
["16.01.2016",null,1.532,0.102,null,39.1,null,null,36.19,null,2.91,null,40.11,36.44,27.45,null,null,null,"24",null,null,"0",null,null,76.42,null,null,39.69,null,null,36.73,null,6,null,4,null,null,0,null,0,null,0,null,0,null,2,null,0,null,0,null,null,0,null,0,null,0,0,0,null,0]
["17.01.2016",null,1.348,0.092,null,38.28,null,null,35.44,null,2.84,null,39.08,35.68,28.61,null,null,null,"24",null,null,"0",null,null,70.07,null,null,37.24,null,null,32.83,null,6,null,4,null,null,0,null,0,null,0,null,0,null,2,null,0,null,0,null,null,0,null,0,null,0,0,0,null,0]
["Среднее",null,1.768,0.111,null,40.548,null,null,37.503,null,3.045,null,41.769,37.79,25.08,null,null,null,23.9,null,null,0.1,null,null,82.39,null,null,41.18,null,null,41.21,null,6,null,4]
["Итого",null,30.057,1.882,null,689.32,null,null,637.55,null,51.77,null,710.08,642.43,426.36,null,null,null,407,null,null,1,null,null,82.39,null,null,41.18,null,null,41.21,null,6,null,4]
[]
["На 01.01.16",null,160.74,9.703,null,5520.36,null,null,5337.69,null,182.67,null,5644.89,5368.89,6578.69,null,null,null,6847,null,null,29]
["На 17.01.16",null,190.797,11.585,null,6209.68,null,null,5975.24,null,234.44,null,6354.97,6011.32,7005.05,null,null,null,7254,null,null,30]
[]
[{"$nulls":22},"Ответственный за учет тепловой энергии: _____________________________"]
[{"$nulls":22},"Отчет принят   \"      \" ____________ 20___г.   ______________ /___________________________/"]
[]
[{"$nulls":50},"Страница 2 из 2"]

{"sheet":"Лист2","index":1,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}

{"sheet":"Лист3","index":2,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}