{"text_format":"2","workbook":"xls","n_sheets":2,"sheets":["приборы","паспорта приборов"],"not_rendered":{"charts":0,"images":2,"macros":0,"external_links":3,"defined_names":3,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"приборы","index":0,"n_rows":32,"n_cols":13,"rows_kept":32,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
[null,null,null,"номинальный поток","температурный напор","n","c","m","Mпр","b","β3","p","Реальное значение теплоотдачи прибора (без учета остывания воды в трубах)"]
[300,10,"300-10",1200,62.5,0.26,1,0,0.011455847255369926,1,0.99,1,1029]
[300,11,"300-11",1320,62.5,0.26,1,0,0.012601431980906921,1,0.99,1,1132]
[300,12,"300-12",1440,62.5,0.26,1,0,0.013747016706443913,1,0.99,1,1235]
[300,13,"300-13",1560,62.5,0.26,1,0,0.014892601431980908,1,0.98,1,1325]
[300,14,"300-14",1680,62.5,0.26,1,0,0.016038186157517897,1,0.98,1,1427]
[300,15,"300-15",1800,62.5,0.26,1,0,0.01718377088305489,1,0.98,1,1529]
[300,16,"300-16",1920,62.5,0.26,1,0,0.018329355608591884,1,0.98,1,1631]
[300,17,"300-17",2040,62.5,0.26,1,0,0.019474940334128877,1,0.98,1,1733]
[300,18,"300-18",2160,62.5,0.26,1,0,0.02062052505966587,1,0.98,1,1835]
[300,19,"300-19",2280,62.5,0.26,1,0,0.021766109785202863,1,0.96,1,1897]
[300,20,"300-20",2400,62.5,0.26,1,0,0.022911694510739853,1,0.96,1,1997]
[300,4,"300-4",480,62.5,0.26,1,0,0.004582338902147971,1,1.025,1,426]
[300,5,"300-5",600,62.5,0.26,1,0,0.005727923627684963,1,1.015,1,527]
[300,6,"300-6",720,62.5,0.26,1,0,0.006873508353221956,1,1.015,1,633]
[300,7,"300-7",840,62.5,0.26,1,0,0.008019093078758949,1,1,1,728]
[300,8,"300-8",960,62.5,0.26,1,0,0.009164677804295942,1,1,1,832]
[300,9,"300-9",1080,62.5,0.26,1,0,0.010310262529832935,1,0.99,1,926]
[500,12,"500-12",1920,62.5,0.26,1,0,0.018329355608591884,1,0.99,1,1647]
[500,13,"500-13",2080,62.5,0.26,1,0,0.019856801909307872,1,0.98,1,1767]
[500,15,"500-15",2400,62.5,0.26,1,0,0.022911694510739853,1,0.98,1,2039]
[500,18,"500-18",2880,62.5,0.26,1,0,0.027494033412887826,1,0.98,1,2446]
[500,4,"500-4",640,62.5,0.26,1,0,0.006109785202863961,1,1.025,1,568]
[500,5,"500-5",800,62.5,0.26,1,0,0.007637231503579951,1,1.015,1,703]
[500,6,"500-6",960,62.5,0.26,1,0,0.009164677804295942,1,1.015,1,844]
[500,7,"500-7",1120,62.5,0.26,1,0,0.010692124105011934,1,1,1,970]
[500,8,"500-8",1280,62.5,0.26,1,0,0.012219570405727923,1,1,1,1109]
[]
["номинальный тепловой поток секции радиатора 300",{"$nulls":5},120,"Вт"]
["номинальный тепловой поток секции радиатора 500",{"$nulls":5},160,"Вт"]
["тепловой расчет приборов согласно производителю http://www.santehlit.ru/technology/rek2_4.shtml"]
["Q=Qну·(Θ/70)1+n·c·(Mпр/0,1)m·b·β3·p"]

{"sheet":"паспорта приборов","index":1,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}