{"text_format":"2","workbook":"xlsx","n_sheets":3,"sheets":["Лист1","Лист2","Лист3"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":0,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Лист1","index":0,"n_rows":14,"n_cols":22,"rows_kept":14,"cut":false,"hidden":false,"merged":[]}
["№ помещения","tв (C°)","№ стояка","№ отоп. Прибора","Qпр. ↑ (Вт)","Qпр. ↓ (Вт)","Qст","β1","β2","Gст","Gt","α","∑Qпред.","tср","∑Qф","∑Qр","n","φ","ψ","Q/φ*ψ (Вт)","A (м²)","Количество секций"]
[1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,16,17,18,19,20,21,22]
[102,20,2,"I",643.55999999999995,"-",{"$f":"SUM(E3:E12)","v":6387.5},1.06,1.04,{"$f":"(G3*H3*I3*3.6)/(25*4.2)","v":241.42560000000003},300,1,{"$f":"M4+E4","v":5743.9400000000005},{"$f":" 95 -(((M3+(0.5/L3*E3))*H3*I3)/(4.2*J3))","v":88.405392476625352},{"$f":" (K3*4.2*25)/(3.6)","v":8750},{"$f":" 0.01*(O3+M3+((0.5/L3)*E3))","v":148.15720000000002},0.25,1.07,"-",{"$f":" E3/(R3)","v":601.45794392523351},null,6]
[202,20,2,"I",580.22,"-",{"$f":"G3","v":6387.5},1.06,1.04,241.42560000000003,300,1,5163.72,{"$f":" 95 -(((M4+(0.5/L4*E4))*H4*I4)/(4.2*J4))","v":89.070634920634916},8750,142.03830000000002,0.25,1.07,"-",{"$f":" E4/(R4)","v":542.26168224299067},null,5]
[302,20,2,"I",590.20000000000005,"-",{"$f":"G4","v":6387.5},1.06,1.04,{"$f":"(G5*H5*I5*3.6)/(25*4.2)","v":241.42560000000003},300,1,4573.5200000000004,{"$f":" 95 -(((M5+(0.5/L5*E5))*H5*I5)/(4.2*J5))","v":89.706871058925856},{"$f":" (K5*4.2*25)/(3.6)","v":8750},{"$f":" 0.01*(O5+M5+((0.5/L5)*E5))","v":136.18620000000001},0.25,1.07,"-",{"$f":" E5/(R5)","v":551.58878504672896},null,5]
[402,20,2,"I",600.17999999999995,"-",6387.5,1.06,1.04,241.42560000000003,300,1,3973.3400000000006,90.353957382039567,8750,130.23430000000002,0.25,1.07,"-",560.91588785046724,null,6]
[502,20,2,"I",610.16999999999996,"-",6387.5,1.06,1.04,241.42560000000003,300,1,3363.1700000000005,{"$f":" 95 -(((M7+(0.5/L7*E7))*H7*I7)/(4.2*J7))","v":91.011899325940419},8750,{"$f":" 0.01*(O7+M7+((0.5/L7)*E7))","v":124.18254999999999},0.25,1.07,"-",570.25233644859804,null,6]
[602,20,2,"I",620.15,"-",6387.5,1.06,1.04,241.42560000000003,300,1,2743.0200000000004,91.680696890628397,8750,118.03095000000002,0.25,1.07,"-",579.57943925233644,null,6]
[702,20,2,"I",630.36,"-",6387.5,1.06,1.04,241.42560000000003,300,1,2112.6600000000003,92.360469667318981,8750,111.7784,0.25,1.07,"-",589.12149532710282,null,6]
[802,20,2,"I",640.11,"-",6387.5,1.06,1.04,241.42560000000003,300,1,{"$f":"M11+E11","v":1472.5500000000002},93.05109262883235,8750,105.42605,0.25,1.07,"-",598.23364485981301,null,6]
[902,20,2,"I",645.1,"-",{"$f":"G3","v":6387.5},1.06,1.04,{"$f":"(G11*H11*I11*3.6)/(25*4.2)","v":241.42560000000003},300,1,{"$f":"M12+E12","v":827.45},93.749728201783,{"$f":" (K11*4.2*25)/(3.6)","v":8750},99,0.25,1.07,"-",{"$f":" E11/(R11)","v":602.89719626168221},null,6]
[1002,20,2,"I",827.45,"-",{"$f":"G4","v":6387.5},1.06,1.04,{"$f":"(G12*H12*I12*3.6)/(25*4.2)","v":241.42560000000003},300,1,{"$f":"M13+E13","v":0},{"$f":" 95 -(((M12+(0.5/L12*E12))*H12*I12)/(4.2*J12))","v":94.550201130680577},8750,91.637250000000009,0.25,1.07,"-",{"$f":" E12/(R12)","v":773.31775700934577},null,{"$f":"T12/110","v":7.0301614273576885}]
[]
["При условии что отдача 1 секции чугунного радиатора ЧМ1-70-500 110Вт"]

{"sheet":"Лист2","index":1,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[]}

{"sheet":"Лист3","index":2,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[]}