{"text_format":"2","workbook":"xlsx","n_sheets":3,"sheets":["Лист1","Лист2","Лист3"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":0,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Лист1","index":0,"n_rows":46,"n_cols":20,"rows_kept":46,"cut":false,"hidden":false,"merged":[[7,17,7,18],[11,17,11,18],[45,17,45,18],[44,17,44,18],[16,0,18,0],[16,1,18,1],[16,19,18,19],[24,0,26,0],[24,1,26,1],[24,19,26,19],[0,12,1,12],[0,11,1,11],[0,10,1,10],[0,9,1,9],[0,1,1,1],[15,17,15,18],[3,0,6,0],[3,1,6,1],[3,19,6,19],[0,0,1,0],[0,18,1,18],[0,19,1,19],[0,7,1,8],[2,7,2,8],[0,6,1,6],[0,5,1,5],[0,4,1,4],[0,3,1,3],[0,2,1,2],[0,14,0,17],[0,13,1,13],[8,0,10,0],[8,1,10,1],[8,19,10,19],[12,0,14,0],[12,1,14,1],[12,19,14,19],[35,17,35,18],[19,17,19,18],[20,0,22,0],[20,1,22,1],[20,19,22,19],[23,17,23,18],[27,17,27,18],[28,0,30,0],[28,1,30,1],[28,19,30,19],[31,17,31,18],[32,0,34,0],[32,1,34,1],[32,19,34,19],[40,0,43,0],[40,1,43,1],[40,19,43,19],[36,0,38,0],[36,1,38,1],[36,19,38,19],[39,17,39,18]]}
["№ помещения","Назначение","Усл. Обозн. Ограждений","Ориентация по сторонам света","tв (C°)","tн (C°)","tв-tн (C°)","Размер ограждений",null,"F (м²)"," K (Вт/м²*С°)"," ΔK (Вт/м²*С°)","n","Основные теплопотери (Q Вт)","Дополнительные теплопотери",null,null,null,"Qполн","ΣQ"]
[{"$nulls":14},"Ориентация","Высота","Угол","1+ΣB"]
[1,2,3,4,5,6,7,8,null,9,10,11,12,13,14,15,16,17,18,19]
[101,"Комната","НС1","СЗ",20,-35,55,5,3.39,{"$f":"PRODUCT(H4,I4)","v":16.95},0.25,"-",1,{"$f":"PRODUCT(G4,J4,K4,M4,)","v":233.0625},0.1,0,0.05,{"$f":"SUM(1,O4:Q4)","v":1.1500000000000001},{"$f":"PRODUCT(N4,R4,)","v":268.02187500000002},{"$f":"SUM(S4:S7)","v":643.56167700000003}]
[null,null,"НС2","ЮЗ",20,-35,{"$f":"E5-F5","v":55},1.6,3.3849999999999998,5.4160000000000004,0.25,"-",1,74.47,0.05,0,0.05,1.1000000000000001,{"$f":"PRODUCT(N5,R5,)","v":81.917000000000002}]
[null,null,"О","СЗ",20,-35,55,1.8,1.5,2.7,1.54,1.29,1,{"$f":"PRODUCT(G6,J6,L6,M6,)","v":191.565},0.1,0,0.05,1.1500000000000001,{"$f":"PRODUCT(N6,R6,)","v":220.29975000000002}]
[null,null,"ПЛ","-",20,-35,55,4.58,3.83,17.541399999999999,0.19,"-",0.4,73.323052000000004,0,0,0,1,73.323052000000004]
[{"$nulls":17},"На 1 этаже",null,{"$f":"SUM(T4:T7)","v":643.56167700000003}]
[201,"Комната","НС1","СЗ",20,-35,55,5,3.39,{"$f":"PRODUCT(H9,I9)","v":16.95},0.25,"-",1,{"$f":"PRODUCT(G9,J9,K9,M9,)","v":233.0625},0.1,0.02,0.05,{"$f":"SUM(1,O9:Q9)","v":1.1700000000000002},{"$f":"PRODUCT(N9,R9,)","v":272.68312500000002},{"$f":"SUM(S9:S11)","v":580.22057500000005}]
[null,null,"НС2","ЮЗ",20,-35,{"$f":"E10-F10","v":55},1.6,3.3849999999999998,5.4160000000000004,0.25,"-",1,74.47,0.05,0.02,0.05,1.1200000000000001,{"$f":"PRODUCT(N10,R10,)","v":83.406400000000005}]
[null,null,"О","СЗ",20,-35,55,1.8,1.5,2.7,1.54,1.29,1,{"$f":"PRODUCT(G11,J11,L11,M11,)","v":191.565},0.1,0.02,0.05,1.1700000000000002,{"$f":"PRODUCT(N11,R11,)","v":224.13105000000002}]
[{"$nulls":17},"На 2 этаже",null,{"$f":"SUM(T9:T11)","v":580.22057500000005}]
[301,"Комната","НС1","СЗ",20,-35,55,5,3.39,{"$f":"PRODUCT(H13,I13)","v":16.95},0.25,"-",1,{"$f":"PRODUCT(G13,J13,K13,M13,)","v":233.0625},0.1,0.04,0.05,{"$f":"SUM(1,O13:Q13)","v":1.1900000000000002},{"$f":"PRODUCT(N13,R13,)","v":277.34437500000001},{"$f":"SUM(S13:S15)","v":590.20252500000004}]
[null,null,"НС2","ЮЗ",20,-35,{"$f":"E14-F14","v":55},1.6,3.3849999999999998,5.4160000000000004,0.25,"-",1,74.47,0.05,0.04,0.05,1.1400000000000001,{"$f":"PRODUCT(N14,R14,)","v":84.895800000000008}]
[null,null,"О","СЗ",20,-35,55,1.8,1.5,2.7,1.54,1.29,1,{"$f":"PRODUCT(G15,J15,L15,M15,)","v":191.565},0.1,0.04,0.05,1.1900000000000002,{"$f":"PRODUCT(N15,R15,)","v":227.96235000000004}]
[{"$nulls":17},"На 3 этаже",null,{"$f":"SUM(T13:T15)","v":590.20252500000004}]
[401,"Комната","НС1","СЗ",20,-35,55,5,3.39,{"$f":"PRODUCT(H17,I17)","v":16.95},0.25,"-",1,{"$f":"PRODUCT(G17,J17,K17,M17,)","v":233.0625},0.1,0.06,0.05,{"$f":"SUM(1,O17:Q17)","v":1.2100000000000002},{"$f":"PRODUCT(N17,R17,)","v":282.00562500000007},{"$f":"SUM(S17:S19)","v":600.18447500000013}]
[null,null,"НС2","ЮЗ",20,-35,{"$f":"E18-F18","v":55},1.6,3.3849999999999998,5.4160000000000004,0.25,"-",1,74.47,0.05,0.06,0.05,1.1600000000000001,{"$f":"PRODUCT(N18,R18,)","v":86.385200000000012}]
[null,null,"О","СЗ",20,-35,55,1.8,1.5,2.7,1.54,1.29,1,{"$f":"PRODUCT(G19,J19,L19,M19,)","v":191.565},0.1,0.06,0.05,1.2100000000000002,{"$f":"PRODUCT(N19,R19,)","v":231.79365000000004}]
[{"$nulls":17},"На 4 этаже",null,{"$f":"SUM(T17:T19)","v":600.18447500000013}]
[501,"Комната","НС1","СЗ",20,-35,55,5,3.39,{"$f":"PRODUCT(H21,I21)","v":16.95},0.25,"-",1,{"$f":"PRODUCT(G21,J21,K21,M21,)","v":233.0625},0.1,0.08,0.05,{"$f":"SUM(1,O21:Q21)","v":1.2300000000000002},{"$f":"PRODUCT(N21,R21,)","v":286.66687500000006},{"$f":"SUM(S21:S23)","v":610.16642500000012}]
[null,null,"НС2","ЮЗ",20,-35,{"$f":"E22-F22","v":55},1.6,3.3849999999999998,5.4160000000000004,0.25,"-",1,74.47,0.05,0.08,0.05,1.1800000000000002,{"$f":"PRODUCT(N22,R22,)","v":87.874600000000015}]
[null,null,"О","СЗ",20,-35,55,1.8,1.5,2.7,1.54,1.29,1,{"$f":"PRODUCT(G23,J23,L23,M23,)","v":191.565},0.1,0.08,0.05,1.2300000000000002,{"$f":"PRODUCT(N23,R23,)","v":235.62495000000004}]
[{"$nulls":17},"На 5 этаже",null,{"$f":"SUM(T21:T23)","v":610.16642500000012}]
[601,"Комната","НС1","СЗ",20,-35,55,5,3.39,{"$f":"PRODUCT(H25,I25)","v":16.95},0.25,"-",1,{"$f":"PRODUCT(G25,J25,K25,M25,)","v":233.0625},0.1,0.1,0.05,{"$f":"SUM(1,O25:Q25)","v":1.2500000000000002},{"$f":"PRODUCT(N25,R25,)","v":291.32812500000006},{"$f":"SUM(S25:S27)","v":620.1483750000001}]
[null,null,"НС2","ЮЗ",20,-35,{"$f":"E26-F26","v":55},1.6,3.3849999999999998,5.4160000000000004,0.25,"-",1,74.47,0.05,0.1,0.05,1.2000000000000002,{"$f":"PRODUCT(N26,R26,)","v":89.364000000000019}]
[null,null,"О","СЗ",20,-35,55,1.8,1.5,2.7,1.54,1.29,1,{"$f":"PRODUCT(G27,J27,L27,M27,)","v":191.565},0.1,0.1,0.05,1.2500000000000002,{"$f":"PRODUCT(N27,R27,)","v":239.45625000000004}]
[{"$nulls":17},"На 6 этаже",null,{"$f":"SUM(T25:T27)","v":620.1483750000001}]
[701,"Комната","НС1","СЗ",20,-35,55,5,3.39,{"$f":"PRODUCT(H29,I29)","v":16.95},0.25,"-",1,{"$f":"PRODUCT(G29,J29,K29,M29,)","v":233.0625},0.1,0.12,0.05,{"$f":"SUM(1,O29:Q29)","v":1.2700000000000002},{"$f":"PRODUCT(N29,R29,)","v":295.98937500000005},{"$f":"SUM(S29:S31)","v":630.36020300000007}]
[null,null,"НС2","ЮЗ",20,-35,{"$f":"E30-F30","v":55},1.6,3.3849999999999998,5.4160000000000004,0.25,"-",1,74.47,0.05,0.12,0.05,1.22,{"$f":"PRODUCT(N30,R30,)","v":90.853399999999993}]
[null,null,"О","СЗ",20,-35,55,1.8,1.5,2.7,1.54,1.29,1,{"$f":"PRODUCT(G31,J31,L31,M31,)","v":191.565},0.1,0.1212,0.05,1.2712000000000001,{"$f":"PRODUCT(N31,R31,)","v":243.51742800000002}]
[{"$nulls":17},"На 7 этаже",null,{"$f":"SUM(T29:T31)","v":630.36020300000007}]
[801,"Комната","НС1","СЗ",20,-35,55,5,3.39,{"$f":"PRODUCT(H33,I33)","v":16.95},0.25,"-",1,{"$f":"PRODUCT(G33,J33,K33,M33,)","v":233.0625},0.1,0.14000000000000001,0.05,{"$f":"SUM(1,O33:Q33)","v":1.2900000000000003},{"$f":"PRODUCT(N33,R33,)","v":300.65062500000005},{"$f":"SUM(S33:S35)","v":640.11227500000007}]
[null,null,"НС2","ЮЗ",20,-35,{"$f":"E34-F34","v":55},1.6,3.3849999999999998,5.4160000000000004,0.25,"-",1,74.47,0.05,0.14000000000000001,0.05,1.24,{"$f":"PRODUCT(N34,R34,)","v":92.342799999999997}]
[null,null,"О","СЗ",20,-35,55,1.8,1.5,2.7,1.54,1.29,1,{"$f":"PRODUCT(G35,J35,L35,M35,)","v":191.565},0.1,0.14000000000000001,0.05,1.2900000000000003,{"$f":"PRODUCT(N35,R35,)","v":247.11885000000004}]
[{"$nulls":17},"На 8 этаже",null,{"$f":"SUM(T33:T35)","v":640.11227500000007}]
[901,"Комната","НС1","СЗ",20,-35,55,5,3.39,{"$f":"PRODUCT(H37,I37)","v":16.95},0.25,"-",1,{"$f":"PRODUCT(G37,J37,K37,M37,)","v":233.0625},0.1,0.15,0.05,{"$f":"SUM(1,O37:Q37)","v":1.3},{"$f":"PRODUCT(N37,R37,)","v":302.98124999999999},{"$f":"SUM(S37:S39)","v":645.10325}]
[null,null,"НС2","ЮЗ",20,-35,{"$f":"E38-F38","v":55},1.6,3.3849999999999998,5.4160000000000004,0.25,"-",1,74.47,0.05,0.15,0.05,1.25,{"$f":"PRODUCT(N38,R38,)","v":93.087500000000006}]
[null,null,"О","СЗ",20,-35,55,1.8,1.5,2.7,1.54,1.29,1,{"$f":"PRODUCT(G39,J39,L39,M39,)","v":191.565},0.1,0.15,0.05,1.3,{"$f":"PRODUCT(N39,R39,)","v":249.03450000000001}]
[{"$nulls":17},"На 9 этаже",null,{"$f":"SUM(T37:T39)","v":645.10325}]
[1001,"Комната","НС1","СЗ",20,-35,55,5,3.39,{"$f":"PRODUCT(H41,I41)","v":16.95},0.25,"-",1,{"$f":"PRODUCT(G41,J41,K41,M41,)","v":233.0625},0.1,0.15,0.05,{"$f":"SUM(1,O41:Q41)","v":1.3},{"$f":"PRODUCT(N41,R41,)","v":302.98124999999999},{"$f":"SUM(S41:S44)","v":827.44610299999999}]
[null,null,"НС2","ЮЗ",20,-35,{"$f":"E42-F42","v":55},1.6,3.3849999999999998,5.4160000000000004,0.25,"-",1,74.47,0.05,0.15,0.05,1.25,{"$f":"PRODUCT(N42,R42,)","v":93.087500000000006}]
[null,null,"О","СЗ",20,-35,55,1.8,1.5,2.7,1.54,1.29,1,{"$f":"PRODUCT(G43,J43,L43,M43,)","v":191.565},0.1,0.15,0.05,1.3,{"$f":"PRODUCT(N43,R43,)","v":249.03450000000001}]
[null,null,"ПТ","-",20,-35,55,4.58,3.83,17.541399999999999,0.21,"-",0.9,{"$f":"PRODUCT(G44,J44,K44,M44,)","v":182.34285299999999},0,0,0,1,182.34285299999999]
[{"$nulls":17},"На 10 этаже",null,{"$f":"SUM(T41:T44)","v":827.44610299999999}]
[{"$nulls":17},"Дом",null,{"$f":"T4+T9+T13+T17+T21+T25+T29+T33+T37+T41","v":6387.5058830000007}]

{"sheet":"Лист2","index":1,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[]}

{"sheet":"Лист3","index":2,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[]}