{"text_format":"2","workbook":"xls","n_sheets":11,"sheets":["Общие результаты","Участки","Список помещений","Приборы","Контуры","Список элем.на приборах","Специф.Мат. - Трубы","Специф.Мат. - Клапаны и др.арма","Специф.Мат. - Радиаторы","Специф.Мат. - Изоляция","Сводка по трубам"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Общие результаты","index":0,"n_rows":32,"n_cols":14,"rows_kept":32,"cut":false,"hidden":false,"merged":[[0,0,0,4],[0,5,0,8],[1,0,1,4],[1,5,1,8],[2,0,2,4],[2,5,2,8],[3,0,3,4],[3,5,3,8],[4,0,4,4],[4,5,4,8],[5,0,5,4],[5,5,5,8],[6,0,6,4],[6,5,6,8],[7,0,7,4],[7,5,7,8],[8,0,8,2],[9,1,9,7],[9,8,9,11],[10,0,10,13],[11,1,11,5],[11,6,11,9],[12,1,12,5],[12,6,12,9],[12,10,12,12],[13,1,13,5],[13,6,13,9],[14,2,14,6],[14,7,14,10],[15,2,15,6],[15,7,15,10],[16,2,16,6],[16,7,16,10],[17,2,17,6],[17,7,17,10],[18,2,18,6],[18,7,18,10],[19,2,19,6],[19,7,19,10],[20,0,20,13],[21,1,21,5],[21,6,21,9],[22,2,22,6],[22,7,22,10],[23,2,23,6],[23,7,23,10],[24,2,24,6],[24,7,24,10],[25,0,25,13],[26,1,26,5],[26,6,26,9],[27,0,27,13],[28,1,28,7],[28,8,28,13],[29,1,29,5],[29,6,29,9],[30,0,30,13],[31,1,31,5],[31,6,31,9]],"flags":["formulas_cached_only"]}
["Кол-во источников",{"$nulls":4},1,null,null,null,"","","","",""]
["Общее кол-во приборов",{"$nulls":4},16]
["Общее кол-во участков",{"$nulls":4},68]
["Общее кол-во распределителей",{"$nulls":4},0]
["Общее кол-во насосов",{"$nulls":4},0]
["Общие теплопотери помещений Q [Вт]",{"$nulls":4},35586]
["Общая мощность других отопит.приборов [Вт]",{"$nulls":4},0]
["Общая треб.мощность отопит.приборов Qтреб [Вт]",{"$nulls":4},35586]
["Нормы расчетов:"]
[null,"Нормы подбора радиаторов",{"$nulls":6},"EN 442-2"]
["Источник: (без имени), Применение: Отопление, Рабочий агент: Вода"]
[null,"Отметка источника [м]",{"$nulls":4},0]
[null,"Темп-ра подачи и обратки [°C]",{"$nulls":4},70,null,null,null,50.4]
[null,"Полная мощность [Вт]",{"$nulls":4},37554]
[null,null,"Суммарная мощность радиаторов Qрад [Вт]",{"$nulls":4},35586]
[null,null,"Суммарная мощность П.О. Qп.о. [Вт]",{"$nulls":4},0]
[null,null,"Суммарная мощность других отопит.приборов [Вт]",{"$nulls":4},0]
[null,null,"Приток теплоты с участков, учтенный в балансе [Вт]",{"$nulls":4},0]
[null,null,"Неиспользованные теплопотери участков [Вт]",{"$nulls":4},1968]
[null,null,"Собств.теплопотери П.О. наружу [Вт]",{"$nulls":4},0]
[""]
[null,"Требуемый напор [кПа]",{"$nulls":4},13.3]
[null,null,"Потери давления в диктующ.трассе [кПа]",{"$nulls":4},13.3]
[null,null,"Потери давления в диктующ.приборе [кПа]",{"$nulls":4},0.2]
[null,null,"Сопрот-ние источника [кПа]",{"$nulls":4},0]
[""]
[null,"Расход в источнике [л/с] [кг/ч]",{"$nulls":4},1650.5]
[""]
[null,"Диктующий прибор",{"$nulls":6},"Р _б"]
[null,"Длина диктующей трассы [м]",{"$nulls":4},98.3]
[""]
[null,"Объём воды [дм³]",{"$nulls":4},348.3]

{"sheet":"Участки","index":1,"n_rows":124,"n_cols":36,"rows_kept":124,"cut":false,"hidden":false,"merged":[[0,2,0,3],[0,5,0,6],[0,8,0,11],[0,13,0,15],[0,17,0,19],[0,20,0,22],[0,23,0,25],[0,26,0,27],[0,28,0,29],[0,30,0,31],[0,33,0,34],[1,0,1,35],[2,1,2,35],[3,2,3,3],[3,5,3,6],[3,8,3,11],[3,13,3,15],[3,17,3,19],[3,20,3,22],[3,23,3,25],[3,26,3,27],[3,28,3,29],[3,30,3,31],[3,33,3,34],[4,2,4,3],[4,5,4,6],[4,8,4,11],[4,13,4,15],[4,17,4,19],[4,20,4,22],[4,23,4,25],[4,26,4,27],[4,28,4,29],[4,30,4,31],[4,33,4,34],[5,2,5,3],[5,5,5,6],[5,8,5,11],[5,13,5,15],[5,17,5,19],[5,20,5,22],[5,23,5,25],[5,26,5,27],[5,28,5,29],[5,30,5,31],[5,33,5,34],[6,2,6,3],[6,5,6,6],[6,8,6,11],[6,13,6,15],[6,17,6,19],[6,20,6,22],[6,23,6,25],[6,26,6,27],[6,28,6,29],[6,30,6,31],[6,33,6,34],[7,2,7,3],[7,5,7,6],[7,8,7,11],[7,13,7,15],[7,17,7,19],[7,20,7,22],[7,23,7,25],[7,26,7,27],[7,28,7,29],[7,30,7,31],[7,33,7,34],[8,2,8,3],[8,5,8,6],[8,8,8,11],[8,13,8,15],[8,17,8,19],[8,20,8,22],[8,23,8,25],[8,26,8,27],[8,28,8,29],[8,30,8,31],[8,33,8,34],[9,3,9,10],[9,11,9,14],[9,15,9,18],[9,19,9,21],[9,22,9,24],[9,25,9,28],[10,3,10,10],[10,11,10,14],[10,15,10,18],[10,19,10,21],[10,22,10,24],[10,25,10,28],[11,3,11,35],[12,2,12,3],[12,5,12,6],[12,8,12,11],[12,13,12,15],[12,17,12,19],[12,20,12,22],[12,23,12,25],[12,26,12,27],[12,28,12,29],[12,30,12,31],[12,33,12,34],[13,2,13,3],[13,5,13,6],[13,8,13,11],[13,13,13,15],[13,17,13,19],[13,20,13,22],[13,23,13,25],[13,26,13,27],[13,28,13,29],[13,30,13,31],[13,33,13,34],[14,2,14,3],[14,5,14,6],[14,8,14,11],[14,13,14,15],[14,17,14,19],[14,20,14,22],[14,23,14,25],[14,26,14,27],[14,28,14,29],[14,30,14,31],[14,33,14,34],[15,2,15,3],[15,5,15,6],[15,8,15,11],[15,13,15,15],[15,17,15,19],[15,20,15,22],[15,23,15,25],[15,26,15,27],[15,28,15,29],[15,30,15,31],[15,33,15,34],[16,3,16,10],[16,11,16,14],[16,15,16,18],[16,19,16,21],[16,22,16,24],[16,25,16,28],[17,3,17,10],[17,11,17,14],[17,15,17,18],[17,19,17,21],[17,22,17,24],[17,25,17,28],[18,3,18,35],[19,2,19,3],[19,5,19,6],[19,8,19,11],[19,13,19,15],[19,17,19,19],[19,20,19,22],[19,23,19,25],[19,26,19,27],[19,28,19,29],[19,30,19,31],[19,33,19,34],[20,2,20,3],[20,5,20,6],[20,8,20,11],[20,13,20,15],[20,17,20,19],[20,20,20,22],[20,23,20,25],[20,26,20,27],[20,28,20,29],[20,30,20,31],[20,33,20,34],[21,2,21,3],[21,5,21,6],[21,8,21,11],[21,13,21,15],[21,17,21,19],[21,20,21,22],[21,23,21,25],[21,26,21,27],[21,28,21,29],[21,30,21,31],[21,33,21,34],[22,2,22,3],[22,5,22,6],[22,8,22,11],[22,13,22,15],[22,17,22,19],[22,20,22,22],[22,23,22,25],[22,26,22,27],[22,28,22,29],[22,30,22,31],[22,33,22,34],[23,3,23,10],[23,11,23,14],[23,15,23,18],[23,19,23,21],[23,22,23,24],[23,25,23,28],[24,3,24,10],[24,11,24,14],[24,15,24,18],[24,19,24,21],[24,22,24,24],[24,25,24,28],[25,3,25,35],[26,2,26,3],[26,5,26,6],[26,8,26,11],[26,13,26,15],[26,17,26,19],[26,20,26,22],[26,23,26,25],[26,26,26,27],[26,28,26,29],[26,30,26,31],[26,33,26,34],[27,2,27,3],[27,5,27,6],[27,8,27,11],[27,13,27,15],[27,17,27,19],[27,20,27,22],[27,23,27,25],[27,26,27,27],[27,28,27,29],[27,30,27,31],[27,33,27,34],[28,2,28,3],[28,5,28,6],[28,8,28,11],[28,13,28,15],[28,17,28,19],[28,20,28,22],[28,23,28,25],[28,26,28,27],[28,28,28,29],[28,30,28,31],[28,33,28,34],[29,2,29,3],[29,5,29,6],[29,8,29,11],[29,13,29,15],[29,17,29,19],[29,20,29,22],[29,23,29,25],[29,26,29,27],[29,28,29,29],[29,30,29,31],[29,33,29,34],[30,3,30,10],[30,11,30,14],[30,15,30,18],[30,19,30,21],[30,22,30,24],[30,25,30,28],[31,3,31,10],[31,11,31,14],[31,15,31,18],[31,19,31,21],[31,22,31,24],[31,25,31,28],[32,3,32,35],[33,2,33,3],[33,5,33,6],[33,8,33,11],[33,13,33,15],[33,17,33,19],[33,20,33,22],[33,23,33,25],[33,26,33,27],[33,28,33,29],[33,30,33,31],[33,33,33,34],[34,2,34,3],[34,5,34,6],[34,8,34,11],[34,13,34,15],[34,17,34,19],[34,20,34,22],[34,23,34,25],[34,26,34,27],[34,28,34,29],[34,30,34,31],[34,33,34,34],[35,2,35,3],[35,5,35,6],[35,8,35,11],[35,13,35,15],[35,17,35,19],[35,20,35,22],[35,23,35,25],[35,26,35,27],[35,28,35,29],[35,30,35,31],[35,33,35,34],[36,2,36,3],[36,5,36,6],[36,8,36,11],[36,13,36,15],[36,17,36,19],[36,20,36,22],[36,23,36,25],[36,26,36,27],[36,28,36,29],[36,30,36,31],[36,33,36,34],[37,3,37,10],[37,11,37,14],[37,15,37,18],[37,19,37,21],[37,22,37,24],[37,25,37,28],[38,3,38,10],[38,11,38,14],[38,15,38,18],[38,19,38,21],[38,22,38,24],[38,25,38,28],[39,3,39,35],[40,2,40,3],[40,5,40,6],[40,8,40,11],[40,13,40,15],[40,17,40,19],[40,20,40,22],[40,23,40,25],[40,26,40,27],[40,28,40,29],[40,30,40,31],[40,33,40,34],[41,2,41,3],[41,5,41,6],[41,8,41,11],[41,13,41,15],[41,17,41,19],[41,20,41,22],[41,23,41,25],[41,26,41,27],[41,28,41,29],[41,30,41,31],[41,33,41,34],[42,2,42,3],[42,5,42,6],[42,8,42,11],[42,13,42,15],[42,17,42,19],[42,20,42,22],[42,23,42,25],[42,26,42,27],[42,28,42,29],[42,30,42,31],[42,33,42,34],[43,2,43,3],[43,5,43,6],[43,8,43,11],[43,13,43,15],[43,17,43,19],[43,20,43,22],[43,23,43,25],[43,26,43,27],[43,28,43,29],[43,30,43,31],[43,33,43,34],[44,3,44,10],[44,11,44,14],[44,15,44,18],[44,19,44,21],[44,22,44,24],[44,25,44,28],[45,3,45,10],[45,11,45,14],[45,15,45,18],[45,19,45,21],[45,22,45,24],[45,25,45,28],[46,3,46,35],[47,2,47,3],[47,5,47,6],[47,8,47,11],[47,13,47,15],[47,17,47,19],[47,20,47,22],[47,23,47,25],[47,26,47,27],[47,28,47,29],[47,30,47,31],[47,33,47,34],[48,2,48,3],[48,5,48,6],[48,8,48,11],[48,13,48,15],[48,17,48,19],[48,20,48,22],[48,23,48,25],[48,26,48,27],[48,28,48,29],[48,30,48,31],[48,33,48,34],[49,2,49,3],[49,5,49,6],[49,8,49,11],[49,13,49,15],[49,17,49,19],[49,20,49,22],[49,23,49,25],[49,26,49,27],[49,28,49,29],[49,30,49,31],[49,33,49,34],[50,2,50,3],[50,5,50,6],[50,8,50,11],[50,13,50,15],[50,17,50,19],[50,20,50,22],[50,23,50,25],[50,26,50,27],[50,28,50,29],[50,30,50,31],[50,33,50,34],[51,2,51,3],[51,5,51,6],[51,8,51,11],[51,13,51,15],[51,17,51,19],[51,20,51,22],[51,23,51,25],[51,26,51,27],[51,28,51,29],[51,30,51,31],[51,33,51,34],[52,3,52,10],[52,11,52,14],[52,15,52,18],[52,19,52,21],[52,22,52,24],[52,25,52,28],[53,3,53,10],[53,11,53,14],[53,15,53,18],[53,19,53,21],[53,22,53,24],[53,25,53,28],[54,3,54,35],[55,2,55,3],[55,5,55,6],[55,8,55,11],[55,13,55,15],[55,17,55,19],[55,20,55,22],[55,23,55,25],[55,26,55,27],[55,28,55,29],[55,30,55,31],[55,33,55,34],[56,2,56,3],[56,5,56,6],[56,8,56,11],[56,13,56,15],[56,17,56,19],[56,20,56,22],[56,23,56,25],[56,26,56,27],[56,28,56,29],[56,30,56,31],[56,33,56,34],[57,2,57,3],[57,5,57,6],[57,8,57,11],[57,13,57,15],[57,17,57,19],[57,20,57,22],[57,23,57,25],[57,26,57,27],[57,28,57,29],[57,30,57,31],[57,33,57,34],[58,2,58,3],[58,5,58,6],[58,8,58,11],[58,13,58,15],[58,17,58,19],[58,20,58,22],[58,23,58,25],[58,26,58,27],[58,28,58,29],[58,30,58,31],[58,33,58,34],[59,3,59,10],[59,11,59,14],[59,15,59,18],[59,19,59,21],[59,22,59,24],[59,25,59,28],[60,3,60,10],[60,11,60,14],[60,15,60,18],[60,19,60,21],[60,22,60,24],[60,25,60,28],[61,3,61,35],[62,2,62,3],[62,5,62,6],[62,8,62,11],[62,13,62,15],[62,17,62,19],[62,20,62,22],[62,23,62,25],[62,26,62,27],[62,28,62,29],[62,30,62,31],[62,33,62,34],[63,2,63,3],[63,5,63,6],[63,8,63,11],[63,13,63,15],[63,17,63,19],[63,20,63,22],[63,23,63,25],[63,26,63,27],[63,28,63,29],[63,30,63,31],[63,33,63,34],[64,2,64,3],[64,5,64,6],[64,8,64,11],[64,13,64,15],[64,17,64,19],[64,20,64,22],[64,23,64,25],[64,26,64,27],[64,28,64,29],[64,30,64,31],[64,33,64,34],[65,2,65,3],[65,5,65,6],[65,8,65,11],[65,13,65,15],[65,17,65,19],[65,20,65,22],[65,23,65,25],[65,26,65,27],[65,28,65,29],[65,30,65,31],[65,33,65,34],[66,3,66,10],[66,11,66,14],[66,15,66,18],[66,19,66,21],[66,22,66,24],[66,25,66,28],[67,3,67,10],[67,11,67,14],[67,15,67,18],[67,19,67,21],[67,22,67,24],[67,25,67,28],[68,3,68,10],[68,11,68,14],[68,15,68,18],[68,19,68,21],[68,22,68,24],[68,25,68,28],[69,3,69,35],[70,2,70,3],[70,5,70,6],[70,8,70,11],[70,13,70,15],[70,17,70,19],[70,20,70,22],[70,23,70,25],[70,26,70,27],[70,28,70,29],[70,30,70,31],[70,33,70,34],[71,2,71,3],[71,5,71,6],[71,8,71,11],[71,13,71,15],[71,17,71,19],[71,20,71,22],[71,23,71,25],[71,26,71,27],[71,28,71,29],[71,30,71,31],[71,33,71,34],[72,2,72,3],[72,5,72,6],[72,8,72,11],[72,13,72,15],[72,17,72,19],[72,20,72,22],[72,23,72,25],[72,26,72,27],[72,28,72,29],[72,30,72,31],[72,33,72,34],[73,2,73,3],[73,5,73,6],[73,8,73,11],[73,13,73,15],[73,17,73,19],[73,20,73,22],[73,23,73,25],[73,26,73,27],[73,28,73,29],[73,30,73,31],[73,33,73,34],[74,2,74,3],[74,5,74,6],[74,8,74,11],[74,13,74,15],[74,17,74,19],[74,20,74,22],[74,23,74,25],[74,26,74,27],[74,28,74,29],[74,30,74,31],[74,33,74,34],[75,3,75,10],[75,11,75,14],[75,15,75,18],[75,19,75,21],[75,22,75,24],[75,25,75,28],[76,3,76,10],[76,11,76,14],[76,15,76,18],[76,19,76,21],[76,22,76,24],[76,25,76,28],[77,3,77,35],[78,2,78,3],[78,5,78,6],[78,8,78,11],[78,13,78,15],[78,17,78,19],[78,20,78,22],[78,23,78,25],[78,26,78,27],[78,28,78,29],[78,30,78,31],[78,33,78,34],[79,2,79,3],[79,5,79,6],[79,8,79,11],[79,13,79,15],[79,17,79,19],[79,20,79,22],[79,23,79,25],[79,26,79,27],[79,28,79,29],[79,30,79,31],[79,33,79,34],[80,2,80,3],[80,5,80,6],[80,8,80,11],[80,13,80,15],[80,17,80,19],[80,20,80,22],[80,23,80,25],[80,26,80,27],[80,28,80,29],[80,30,80,31],[80,33,80,34],[81,2,81,3],[81,5,81,6],[81,8,81,11],[81,13,81,15],[81,17,81,19],[81,20,81,22],[81,23,81,25],[81,26,81,27],[81,28,81,29],[81,30,81,31],[81,33,81,34],[82,3,82,10],[82,11,82,14],[82,15,82,18],[82,19,82,21],[82,22,82,24],[82,25,82,28],[83,3,83,10],[83,11,83,14],[83,15,83,18],[83,19,83,21],[83,22,83,24],[83,25,83,28],[84,3,84,35],[85,2,85,3],[85,5,85,6],[85,8,85,11],[85,13,85,15],[85,17,85,19],[85,20,85,22],[85,23,85,25],[85,26,85,27],[85,28,85,29],[85,30,85,31],[85,33,85,34],[86,2,86,3],[86,5,86,6],[86,8,86,11],[86,13,86,15],[86,17,86,19],[86,20,86,22],[86,23,86,25],[86,26,86,27],[86,28,86,29],[86,30,86,31],[86,33,86,34],[87,2,87,3],[87,5,87,6],[87,8,87,11],[87,13,87,15],[87,17,87,19],[87,20,87,22],[87,23,87,25],[87,26,87,27],[87,28,87,29],[87,30,87,31],[87,33,87,34],[88,2,88,3],[88,5,88,6],[88,8,88,11],[88,13,88,15],[88,17,88,19],[88,20,88,22],[88,23,88,25],[88,26,88,27],[88,28,88,29],[88,30,88,31],[88,33,88,34],[89,3,89,10],[89,11,89,14],[89,15,89,18],[89,19,89,21],[89,22,89,24],[89,25,89,28],[90,3,90,10],[90,11,90,14],[90,15,90,18],[90,19,90,21],[90,22,90,24],[90,25,90,28],[91,3,91,35],[92,2,92,3],[92,5,92,6],[92,8,92,11],[92,13,92,15],[92,17,92,19],[92,20,92,22],[92,23,92,25],[92,26,92,27],[92,28,92,29],[92,30,92,31],[92,33,92,34],[93,2,93,3],[93,5,93,6],[93,8,93,11],[93,13,93,15],[93,17,93,19],[93,20,93,22],[93,23,93,25],[93,26,93,27],[93,28,93,29],[93,30,93,31],[93,33,93,34],[94,2,94,3],[94,5,94,6],[94,8,94,11],[94,13,94,15],[94,17,94,19],[94,20,94,22],[94,23,94,25],[94,26,94,27],[94,28,94,29],[94,30,94,31],[94,33,94,34],[95,2,95,3],[95,5,95,6],[95,8,95,11],[95,13,95,15],[95,17,95,19],[95,20,95,22],[95,23,95,25],[95,26,95,27],[95,28,95,29],[95,30,95,31],[95,33,95,34],[96,2,96,3],[96,5,96,6],[96,8,96,11],[96,13,96,15],[96,17,96,19],[96,20,96,22],[96,23,96,25],[96,26,96,27],[96,28,96,29],[96,30,96,31],[96,33,96,34],[97,3,97,10],[97,11,97,14],[97,15,97,18],[97,19,97,21],[97,22,97,24],[97,25,97,28],[98,3,98,10],[98,11,98,14],[98,15,98,18],[98,19,98,21],[98,22,98,24],[98,25,98,28],[99,3,99,35],[100,2,100,3],[100,5,100,6],[100,8,100,11],[100,13,100,15],[100,17,100,19],[100,20,100,22],[100,23,100,25],[100,26,100,27],[100,28,100,29],[100,30,100,31],[100,33,100,34],[101,2,101,3],[101,5,101,6],[101,8,101,11],[101,13,101,15],[101,17,101,19],[101,20,101,22],[101,23,101,25],[101,26,101,27],[101,28,101,29],[101,30,101,31],[101,33,101,34],[102,2,102,3],[102,5,102,6],[102,8,102,11],[102,13,102,15],[102,17,102,19],[102,20,102,22],[102,23,102,25],[102,26,102,27],[102,28,102,29],[102,30,102,31],[102,33,102,34],[103,2,103,3],[103,5,103,6],[103,8,103,11],[103,13,103,15],[103,17,103,19],[103,20,103,22],[103,23,103,25],[103,26,103,27],[103,28,103,29],[103,30,103,31],[103,33,103,34],[104,3,104,10],[104,11,104,14],[104,15,104,18],[104,19,104,21],[104,22,104,24],[104,25,104,28],[105,3,105,10],[105,11,105,14],[105,15,105,18],[105,19,105,21],[105,22,105,24],[105,25,105,28],[106,3,106,10],[106,11,106,14],[106,15,106,18],[106,19,106,21],[106,22,106,24],[106,25,106,28],[107,3,107,35],[108,2,108,3],[108,5,108,6],[108,8,108,11],[108,13,108,15],[108,17,108,19],[108,20,108,22],[108,23,108,25],[108,26,108,27],[108,28,108,29],[108,30,108,31],[108,33,108,34],[109,2,109,3],[109,5,109,6],[109,8,109,11],[109,13,109,15],[109,17,109,19],[109,20,109,22],[109,23,109,25],[109,26,109,27],[109,28,109,29],[109,30,109,31],[109,33,109,34],[110,3,110,10],[110,11,110,14],[110,15,110,18],[110,19,110,21],[110,22,110,24],[110,25,110,28],[111,3,111,10],[111,11,111,14],[111,15,111,18],[111,19,111,21],[111,22,111,24],[111,25,111,28],[112,3,112,35],[113,2,113,3],[113,5,113,6],[113,8,113,11],[113,13,113,15],[113,17,113,19],[113,20,113,22],[113,23,113,25],[113,26,113,27],[113,28,113,29],[113,30,113,31],[113,33,113,34],[114,2,114,3],[114,5,114,6],[114,8,114,11],[114,13,114,15],[114,17,114,19],[114,20,114,22],[114,23,114,25],[114,26,114,27],[114,28,114,29],[114,30,114,31],[114,33,114,34],[115,3,115,10],[115,11,115,14],[115,15,115,18],[115,19,115,21],[115,22,115,24],[115,25,115,28],[116,3,116,10],[116,11,116,14],[116,15,116,18],[116,19,116,21],[116,22,116,24],[116,25,116,28],[117,3,117,35],[118,2,118,3],[118,5,118,6],[118,8,118,11],[118,13,118,15],[118,17,118,19],[118,20,118,22],[118,23,118,25],[118,26,118,27],[118,28,118,29],[118,30,118,31],[118,33,118,34],[119,3,119,10],[119,11,119,14],[119,15,119,18],[119,19,119,21],[119,22,119,24],[119,25,119,28],[120,3,120,10],[120,11,120,14],[120,15,120,18],[120,19,120,21],[120,22,120,24],[120,25,120,28],[121,3,121,35],[122,2,122,3],[122,5,122,6],[122,8,122,11],[122,13,122,15],[122,17,122,19],[122,20,122,22],[122,23,122,25],[122,26,122,27],[122,28,122,29],[122,30,122,31],[122,33,122,34],[123,2,123,3],[123,5,123,6],[123,8,123,11],[123,13,123,15],[123,17,123,19],[123,20,123,22],[123,23,123,25],[123,26,123,27],[123,28,123,29],[123,30,123,31],[123,33,123,34]],"flags":["formulas_cached_only"]}
["","","ТУ",null,"Символ\nучастка","Символ\nподкл.уч.",null,"Q\n[Вт]","Диаметр\n[мм]",null,null,null,"L\n[м]","i\n[Па/м]",null,null,"ζ","i*L+Z\n[Па]",null,null,"Сопр.\n[Па]",null,null,"v\n[м/с]",null,null,"G\n[кг/ч]",null,"h изол\n[мм]",null,"Δt\n[K]",null,"tвход\n[°C]","q\n[Вт/м]",null,"Qуч\n[Вт]"]
["Источник: (без имени)"]
[null,"Группа: Элементы несгруппированные"]
[null,null,"П",null,1,"И",null,35586,"63 x 6.0",null,null,null,1.4,12,null,null,0.4,17,null,null,17,null,null,0.23,null,null,1651,null,25,null,0.01,null,70,16,null,23]
[null,null,"В",null,1,"И",null,35586,"63 x 6.0",null,null,null,1.8,13,null,null,0,23,null,null,23,null,null,0.23,null,null,1651,null,25,null,0.01,null,50.4,9,null,16]
[null,null,"В",null,"1_а",1,null,35586,"63 x 6.0",null,null,null,9.5,13,null,null,0.4,120,null,null,120,null,null,0.23,null,null,1651,null,25,null,0.05,null,50.5,9,null,87]
[null,null,"П",null,2,1,null,33362,"63 x 6.0",null,null,null,2.4,11,null,null,0.8,64,null,null,64,null,null,0.22,null,null,1549,null,25,null,0.02,null,70,16,null,39]
[null,null,"В",null,2,"1_а",null,2224,"16 x 2.0",null,null,null,0.7,81,null,null,1.4,136,null,null,136,null,null,0.23,null,null,94,null,20,null,0.03,null,47.5,4,null,3]
[null,null,"П",null,3,2,null,2224,"16 x 2.0",null,null,null,1.2,87,null,null,1.4,187,null,null,10644,null,null,0.26,null,null,101,null,20,null,0.08,null,70,8,null,10]
[null,null,null,"Тип",{"$nulls":7},"Диам. [мм] ",null,null,null,"Сопр. [Па]  ",null,null,null,"Xp ",null,null,"Aкл ",null,null,"Настройка "]
[null,null,null,"Клапан V-Exakt прямой",{"$nulls":7},15,null,null,null,10457,null,null,null,2,null,null,0.79,null,null,5]
[null,null,null,""]
[null,null,"В",null,3,"1_а",null,33362,"63 x 6.0",null,null,null,6.2,11,null,null,0.8,82,null,null,82,null,null,0.21,null,null,1557,null,25,null,0.03,null,50.7,9,null,58]
[null,null,"П",null,4,2,null,31138,"63 x 6.0",null,null,null,2.9,9,null,null,0.8,37,null,null,37,null,null,0.2,null,null,1448,null,25,null,0.03,null,70,14,null,41]
[null,null,"В",null,4,3,null,2224,"16 x 2.0",null,null,null,0.7,77,null,null,1.4,124,null,null,124,null,null,0.22,null,null,91,null,20,null,0.03,null,47.2,4,null,3]
[null,null,"П",null,5,4,null,2224,"16 x 2.0",null,null,null,1.2,87,null,null,1.4,183,null,null,10651,null,null,0.26,null,null,102,null,20,null,0.08,null,69.9,8,null,10]
[null,null,null,"Тип",{"$nulls":7},"Диам. [мм] ",null,null,null,"Сопр. [Па]  ",null,null,null,"Xp ",null,null,"Aкл ",null,null,"Настройка "]
[null,null,null,"Клапан V-Exakt прямой",{"$nulls":7},15,null,null,null,10468,null,null,null,2,null,null,0.79,null,null,5]
[null,null,null,""]
[null,null,"В",null,5,3,null,31138,"63 x 6.0",null,null,null,12.1,10,null,null,0.8,134,null,null,134,null,null,0.2,null,null,1466,null,25,null,0.07,null,51,8,null,96]
[null,null,"П",null,6,4,null,28914,"50 x 4.5",null,null,null,3,24,null,null,0.8,79,null,null,79,null,null,0.29,null,null,1346,null,25,null,0.03,null,69.9,14,null,42]
[null,null,"В",null,6,5,null,2224,"16 x 2.0",null,null,null,0.6,109,null,null,1.4,157,null,null,157,null,null,0.28,null,null,112,null,20,null,0.02,null,51.8,4,null,3]
[null,null,"П",null,7,6,null,2224,"16 x 2.0",null,null,null,1.2,87,null,null,1.4,224,null,null,10780,null,null,0.26,null,null,102,null,20,null,0.08,null,69.9,8,null,9]
[null,null,null,"Тип",{"$nulls":7},"Диам. [мм] ",null,null,null,"Сопр. [Па]  ",null,null,null,"Xp ",null,null,"Aкл ",null,null,"Настройка "]
[null,null,null,"Клапан V-Exakt прямой",{"$nulls":7},15,null,null,null,10556,null,null,null,2,null,null,0.79,null,null,5]
[null,null,null,""]
[null,null,"В",null,7,5,null,28914,"50 x 4.5",null,null,null,10.6,25,null,null,2.4,343,null,null,343,null,null,0.29,null,null,1354,null,25,null,0.06,null,50.9,8,null,85]
[null,null,"П",null,8,6,null,26690,"50 x 4.5",null,null,null,6,21,null,null,2.4,195,null,null,195,null,null,0.27,null,null,1244,null,25,null,0.06,null,69.9,14,null,83]
[null,null,"В",null,8,7,null,2224,"16 x 2.0",null,null,null,0.4,104,null,null,1.4,171,null,null,171,null,null,0.27,null,null,109,null,20,null,0.02,null,51.5,5,null,2]
[null,null,"П",null,9,8,null,2224,"16 x 2.0",null,null,null,1.2,88,null,null,1.4,222,null,null,10852,null,null,0.26,null,null,103,null,20,null,0.08,null,69.9,8,null,10]
[null,null,null,"Тип",{"$nulls":7},"Диам. [мм] ",null,null,null,"Сопр. [Па]  ",null,null,null,"Xp ",null,null,"Aкл ",null,null,"Настройка "]
[null,null,null,"Клапан V-Exakt прямой",{"$nulls":7},15,null,null,null,10630,null,null,null,2,null,null,0.8,null,null,5]
[null,null,null,""]
[null,null,"В",null,9,7,null,26690,"50 x 4.5",null,null,null,2.1,22,null,null,0.8,62,null,null,62,null,null,0.27,null,null,1246,null,25,null,0.01,null,50.9,8,null,17]
[null,null,"П",null,10,8,null,24466,"50 x 4.5",null,null,null,3.2,18,null,null,0.8,70,null,null,70,null,null,0.25,null,null,1141,null,25,null,0.03,null,69.9,14,null,44]
[null,null,"В",null,10,9,null,2224,"16 x 2.0",null,null,null,2.1,105,null,null,1.4,324,null,null,324,null,null,0.27,null,null,109,null,20,null,0.08,null,51.6,5,null,10]
[null,null,"П",null,11,10,null,2224,"16 x 2.0",null,null,null,1.2,89,null,null,1.4,209,null,null,10928,null,null,0.26,null,null,103,null,20,null,0.08,null,69.8,8,null,10]
[null,null,null,"Тип",{"$nulls":7},"Диам. [мм] ",null,null,null,"Сопр. [Па]  ",null,null,null,"Xp ",null,null,"Aкл ",null,null,"Настройка "]
[null,null,null,"Клапан V-Exakt прямой",{"$nulls":7},15,null,null,null,10719,null,null,null,2,null,null,0.81,null,null,5]
[null,null,null,""]
[null,null,"В",null,11,9,null,24466,"50 x 4.5",null,null,null,5.6,19,null,null,0.8,118,null,null,118,null,null,0.24,null,null,1137,null,25,null,0.04,null,50.9,8,null,45]
[null,null,"П",null,12,10,null,22242,"50 x 4.5",null,null,null,4.2,15,null,null,0.8,74,null,null,74,null,null,0.22,null,null,1039,null,25,null,0.05,null,69.8,14,null,58]
[null,null,"В",null,12,11,null,2224,"16 x 2.0",null,null,null,0.5,101,null,null,1.4,151,null,null,151,null,null,0.27,null,null,107,null,20,null,0.02,null,51.4,5,null,2]
[null,null,"П",null,13,12,null,2224,"16 x 2.0",null,null,null,1.3,90,null,null,1.4,204,null,null,10921,null,null,0.26,null,null,103,null,20,null,0.08,null,69.8,8,null,10]
[null,null,null,"Тип",{"$nulls":7},"Диам. [мм] ",null,null,null,"Сопр. [Па]  ",null,null,null,"Xp ",null,null,"Aкл ",null,null,"Настройка "]
[null,null,null,"Клапан V-Exakt прямой",{"$nulls":7},15,null,null,null,10716,null,null,null,2,null,null,0.81,null,null,5]
[null,null,null,""]
[null,null,"В",null,13,11,null,22242,"50 x 4.5",null,null,null,0.5,16,null,null,2,57,null,null,57,null,null,0.22,null,null,1030,null,25,null,0,null,50.8,8,null,4]
[null,null,"В",null,"13_а",13,null,22242,"50 x 4.5",null,null,null,7.3,16,null,null,0.4,113,null,null,113,null,null,0.22,null,null,1030,null,25,null,0.05,null,50.9,8,null,58]
[null,null,"П",null,14,12,null,20017,"50 x 4.5",null,null,null,6.3,12,null,null,0.8,89,null,null,89,null,null,0.2,null,null,935,null,25,null,0.08,null,69.8,14,null,88]
[null,null,"В",null,14,"13_а",null,2224,"16 x 2.0",null,null,null,0.3,99,null,null,1.4,128,null,null,128,null,null,0.26,null,null,106,null,20,null,0.01,null,51.3,5,null,2]
[null,null,"П",null,15,14,null,2224,"16 x 2.0",null,null,null,1.3,91,null,null,1.4,198,null,null,10995,null,null,0.26,null,null,104,null,20,null,0.08,null,69.7,8,null,10]
[null,null,null,"Тип",{"$nulls":7},"Диам. [мм] ",null,null,null,"Сопр. [Па]  ",null,null,null,"Xp ",null,null,"Aкл ",null,null,"Настройка "]
[null,null,null,"Клапан V-Exakt прямой",{"$nulls":7},15,null,null,null,10796,null,null,null,2,null,null,0.81,null,null,5]
[null,null,null,""]
[null,null,"В",null,15,"13_а",null,20017,"50 x 4.5",null,null,null,5.9,13,null,null,0.8,86,null,null,86,null,null,0.2,null,null,924,null,25,null,0.05,null,50.9,8,null,48]
[null,null,"П",null,16,14,null,17793,"40 x 4.0",null,null,null,5.8,33,null,null,0.9,198,null,null,198,null,null,0.29,null,null,831,null,20,null,0.08,null,69.7,13,null,77]
[null,null,"В",null,16,15,null,2224,"16 x 2.0",null,null,null,0.3,98,null,null,1.4,117,null,null,117,null,null,0.26,null,null,105,null,20,null,0.01,null,51.3,5,null,2]
[null,null,"П",null,17,16,null,2224,"16 x 2.0",null,null,null,1.2,92,null,null,1.7,269,null,null,11065,null,null,0.26,null,null,105,null,20,null,0.08,null,69.6,8,null,10]
[null,null,null,"Тип",{"$nulls":7},"Диам. [мм] ",null,null,null,"Сопр. [Па]  ",null,null,null,"Xp ",null,null,"Aкл ",null,null,"Настройка "]
[null,null,null,"Клапан V-Exakt прямой",{"$nulls":7},15,null,null,null,10796,null,null,null,2,null,null,0.81,null,null,5]
[null,null,null,""]
[null,null,"В",null,17,15,null,17793,"40 x 4.0",null,null,null,5.8,34,null,null,0.9,204,null,null,204,null,null,0.29,null,null,819,null,20,null,0.05,null,50.9,8,null,45]
[null,null,"П",null,18,16,null,15569,"40 x 4.0",null,null,null,5.9,26,null,null,1,174,null,null,174,null,null,0.26,null,null,727,null,20,null,0.09,null,69.6,13,null,79]
[null,null,"В",null,18,17,null,2224,"16 x 2.0",null,null,null,0.4,96,null,null,1.7,184,null,null,184,null,null,0.26,null,null,104,null,20,null,0.01,null,51.2,5,null,2]
[null,null,"П",null,19,18,null,2224,"16 x 2.0",null,null,null,1.2,93,null,null,2.5,277,null,null,10963,null,null,0.27,null,null,106,null,20,null,0.08,null,69.5,8,null,10]
[null,null,null,"Тип",{"$nulls":7},"Диам. [мм] ",null,null,null,"Сопр. [Па]  ",null,null,null,"Xp ",null,null,"Aкл ",null,null,"Настройка "]
[null,null,null,"Клапан V-Exakt прямой",{"$nulls":7},15,null,null,null,5343,null,null,null,2,null,null,0.4,null,null,6]
[null,null,null,"Клапан V-Exakt прямой",{"$nulls":7},15,null,null,null,5343,null,null,null,2,null,null,0.4,null,null,6]
[null,null,null,""]
[null,null,"В",null,19,17,null,15569,"40 x 4.0",null,null,null,6.3,27,null,null,1,190,null,null,190,null,null,0.25,null,null,715,null,20,null,0.06,null,50.9,8,null,50]
[null,null,"П",null,20,18,null,13345,"40 x 4.0",null,null,null,7.1,20,null,null,2.5,202,null,null,202,null,null,0.22,null,null,621,null,20,null,0.13,null,69.5,13,null,94]
[null,null,"В",null,20,19,null,2224,"16 x 2.0",null,null,null,0.4,95,null,null,1.7,160,null,null,160,null,null,0.26,null,null,103,null,20,null,0.01,null,51.2,5,null,2]
[null,null,"П",null,"20_а",20,null,13345,"40 x 4.0",null,null,null,0.5,20,null,null,0.5,10,null,null,10,null,null,0.22,null,null,621,null,20,null,0.01,null,69.4,13,null,6]
[null,null,"П",null,21,"20_а",null,2224,"16 x 2.0",null,null,null,1,95,null,null,1.5,198,null,null,10893,null,null,0.27,null,null,107,null,20,null,0.06,null,69.4,8,null,8]
[null,null,null,"Тип",{"$nulls":7},"Диам. [мм] ",null,null,null,"Сопр. [Па]  ",null,null,null,"Xp ",null,null,"Aкл ",null,null,"Настройка "]
[null,null,null,"Клапан V-Exakt прямой",{"$nulls":7},15,null,null,null,10695,null,null,null,2,null,null,0.8,null,null,5]
[null,null,null,""]
[null,null,"В",null,21,19,null,13345,"40 x 4.0",null,null,null,4.2,20,null,null,1,101,null,null,101,null,null,0.21,null,null,612,null,20,null,0.05,null,50.9,8,null,33]
[null,null,"П",null,22,"20_а",null,11121,"32 x 3.0",null,null,null,5.6,38,null,null,1.2,224,null,null,224,null,null,0.28,null,null,514,null,20,null,0.11,null,69.4,12,null,65]
[null,null,"В",null,22,21,null,2224,"16 x 2.0",null,null,null,0.3,94,null,null,1.5,128,null,null,128,null,null,0.26,null,null,103,null,20,null,0.01,null,51.1,5,null,1]
[null,null,"П",null,23,22,null,2224,"16 x 2.0",null,null,null,2.6,99,null,null,1.5,384,null,null,10607,null,null,0.27,null,null,109,null,20,null,0.16,null,69.3,8,null,20]
[null,null,null,"Тип",{"$nulls":7},"Диам. [мм] ",null,null,null,"Сопр. [Па]  ",null,null,null,"Xp ",null,null,"Aкл ",null,null,"Настройка "]
[null,null,null,"Клапан V-Exakt прямой",{"$nulls":7},15,null,null,null,10223,null,null,null,2,null,null,0.77,null,null,5]
[null,null,null,""]
[null,null,"В",null,23,21,null,11121,"32 x 3.0",null,null,null,3.2,39,null,null,1.2,136,null,null,136,null,null,0.27,null,null,509,null,20,null,0.04,null,50.9,7,null,22]
[null,null,"П",null,24,22,null,8897,"32 x 3.0",null,null,null,2.1,25,null,null,1.4,78,null,null,78,null,null,0.22,null,null,405,null,20,null,0.05,null,69.3,12,null,24]
[null,null,"В",null,24,23,null,2224,"16 x 2.0",null,null,null,0.3,94,null,null,0.7,139,null,null,139,null,null,0.26,null,null,103,null,20,null,0.01,null,51.1,5,null,2]
[null,null,"П",null,25,24,null,2224,"16 x 2.0",null,null,null,0.9,98,null,null,0.7,163,null,null,10746,null,null,0.27,null,null,109,null,20,null,0.06,null,69.2,8,null,7]
[null,null,null,"Тип",{"$nulls":7},"Диам. [мм] ",null,null,null,"Сопр. [Па]  ",null,null,null,"Xp ",null,null,"Aкл ",null,null,"Настройка "]
[null,null,null,"Клапан V-Exakt прямой",{"$nulls":7},15,null,null,null,10582,null,null,null,2,null,null,0.8,null,null,5]
[null,null,null,""]
[null,null,"В",null,25,23,null,8897,"32 x 3.0",null,null,null,2.4,27,null,null,3,142,null,null,142,null,null,0.22,null,null,407,null,20,null,0.04,null,50.9,7,null,16]
[null,null,"В",null,"25_а",25,null,8897,"32 x 3.0",null,null,null,1.9,27,null,null,0.7,51,null,null,51,null,null,0.22,null,null,407,null,20,null,0.03,null,50.9,7,null,13]
[null,null,"П",null,26,24,null,6672,"25 x 2.5",null,null,null,10.4,50,null,null,2.4,586,null,null,586,null,null,0.27,null,null,296,null,20,null,0.3,null,69.2,10,null,104]
[null,null,"В",null,26,"25_а",null,2224,"16 x 2.0",null,null,null,1.4,93,null,null,0.7,215,null,null,215,null,null,0.25,null,null,102,null,20,null,0.06,null,51.1,5,null,7]
[null,null,"П",null,27,26,null,2224,"16 x 2.0",null,null,null,1.1,103,null,null,0.8,245,null,null,10504,null,null,0.28,null,null,112,null,20,null,0.07,null,68.9,8,null,9]
[null,null,null,"Тип",{"$nulls":7},"Диам. [мм] ",null,null,null,"Сопр. [Па]  ",null,null,null,"Xp ",null,null,"Aкл ",null,null,"Настройка "]
[null,null,null,"Клапан V-Exakt прямой",{"$nulls":7},15,null,null,null,10259,null,null,null,2,null,null,0.77,null,null,5]
[null,null,null,""]
[null,null,"В",null,27,"25_а",null,6672,"25 x 2.5",null,null,null,4,56,null,null,2.4,270,null,null,270,null,null,0.27,null,null,305,null,20,null,0.07,null,50.9,6,null,23]
[null,null,"П",null,28,26,null,4448,"20 x 2.25",null,null,null,12.1,73,null,null,1.6,915,null,null,915,null,null,0.28,null,null,184,null,20,null,0.49,null,68.9,9,null,105]
[null,null,"В",null,28,27,null,2224,"16 x 2.0",null,null,null,0.2,93,null,null,0.8,153,null,null,153,null,null,0.25,null,null,102,null,20,null,0.01,null,51.1,5,null,1]
[null,null,"П",null,29,28,null,2224,"16 x 2.0",null,null,null,1.2,71,null,null,1.6,248,null,null,9921,null,null,0.23,null,null,91,null,20,null,0.08,null,68.4,8,null,9]
[null,null,null,"Тип",{"$nulls":7},"Диам. [мм] ",null,null,null,"Сопр. [Па]  ",null,null,null,"Xp ",null,null,"Aкл ",null,null,"Настройка "]
[null,null,null,"Клапан V-Exakt прямой",{"$nulls":7},15,null,null,null,4836,null,null,null,2,null,null,0.36,null,null,6]
[null,null,null,"Клапан V-Exakt прямой",{"$nulls":7},15,null,null,null,4836,null,null,null,2,null,null,0.36,null,null,6]
[null,null,null,""]
[null,null,"В",null,29,27,null,4448,"25 x 2.5",null,null,null,2.9,27,null,null,1.6,110,null,null,110,null,null,0.18,null,null,203,null,20,null,0.08,null,51,5,null,15]
[null,null,"П",null,30,28,null,2224,"16 x 2.0",null,null,null,6.2,76,null,null,7.2,677,null,null,5283,null,null,0.24,null,null,94,null,20,null,0.44,null,68.4,8,null,48]
[null,null,null,"Тип",{"$nulls":7},"Диам. [мм] ",null,null,null,"Сопр. [Па]  ",null,null,null,"Xp ",null,null,"Aкл ",null,null,"Настройка "]
[null,null,null,"Клапан V-Exakt прямой",{"$nulls":7},15,null,null,null,4606,null,null,null,2,null,null,0.35,null,null,6]
[null,null,null,""]
[null,null,"В",null,30,29,null,2224,"16 x 2.0",null,null,null,0.3,92,null,null,0.8,88,null,null,88,null,null,0.25,null,null,101,null,20,null,0.01,null,51,5,null,1]
[null,null,"П",null,"30_а",30,null,2224,"16 x 2.0",null,null,null,1.2,76,null,null,0,100,null,null,4704,null,null,0.24,null,null,94,null,20,null,0.08,null,68,8,null,9]
[null,null,null,"Тип",{"$nulls":7},"Диам. [мм] ",null,null,null,"Сопр. [Па]  ",null,null,null,"Xp ",null,null,"Aкл ",null,null,"Настройка "]
[null,null,null,"Клапан V-Exakt прямой",{"$nulls":7},15,null,null,null,4604,null,null,null,2,null,null,0.35,null,null,6]
[null,null,null,""]
[null,null,"П",null,31,1,null,2224,"16 x 2.0",null,null,null,1.6,87,null,null,2.8,268,null,null,10504,null,null,0.26,null,null,102,null,20,null,0.11,null,70,8,null,13]
[null,null,null,"Тип",{"$nulls":7},"Диам. [мм] ",null,null,null,"Сопр. [Па]  ",null,null,null,"Xp ",null,null,"Aкл ",null,null,"Настройка "]
[null,null,null,"Клапан V-Exakt прямой",{"$nulls":7},15,null,null,null,10236,null,null,null,2,null,null,0.77,null,null,5]
[null,null,null,""]
[null,null,"В",null,31,29,null,2224,"16 x 2.0",null,null,null,1.8,92,null,null,0.8,177,null,null,177,null,null,0.25,null,null,102,null,20,null,0.07,null,51,5,null,8]
[null,null,"В",null,"31_а",31,null,2224,"16 x 2.0",null,null,null,1.3,92,null,null,0,115,null,null,115,null,null,0.25,null,null,102,null,20,null,0.05,null,51,5,null,6]

{"sheet":"Список помещений","index":2,"n_rows":3,"n_cols":12,"rows_kept":3,"cut":false,"hidden":false,"merged":[[1,0,1,11]],"flags":["formulas_cached_only"]}
["","Символ\nПомещения","tв\n[°C]","Кол-во\nрадиаторов","Q\n[Вт]","Qтреб\n[Вт]","Qп.о.\n[Вт]","Qрад\n[Вт]","Результат\nQп.о.\n[Вт]","Результат\nQрад\n[Вт]","Результат\nQуч\n[Вт]","Покрытие теплопотерь\n[%]"]
["Этаж 0, Отметка 0.0м, Квартира По умолчанию"]
[null,"(без имени)",20,"16 р",0,35586,0,35586,0,35586,0,100]

{"sheet":"Приборы","index":3,"n_rows":21,"n_cols":23,"rows_kept":21,"cut":false,"hidden":false,"merged":[[0,9,0,10],[0,11,0,12],[0,13,0,15],[0,16,0,17],[0,18,0,19],[2,0,2,22],[3,1,3,22],[4,9,4,10],[4,11,4,12],[4,13,4,15],[4,16,4,17],[4,18,4,19],[5,9,5,10],[5,11,5,12],[5,13,5,15],[5,16,5,17],[5,18,5,19],[6,9,6,10],[6,11,6,12],[6,13,6,15],[6,16,6,17],[6,18,6,19],[7,9,7,10],[7,11,7,12],[7,13,7,15],[7,16,7,17],[7,18,7,19],[8,9,8,10],[8,11,8,12],[8,13,8,15],[8,16,8,17],[8,18,8,19],[9,9,9,10],[9,11,9,12],[9,13,9,15],[9,16,9,17],[9,18,9,19],[10,9,10,10],[10,11,10,12],[10,13,10,15],[10,16,10,17],[10,18,10,19],[11,9,11,10],[11,11,11,12],[11,13,11,15],[11,16,11,17],[11,18,11,19],[12,9,12,10],[12,11,12,12],[12,13,12,15],[12,16,12,17],[12,18,12,19],[13,9,13,10],[13,11,13,12],[13,13,13,15],[13,16,13,17],[13,18,13,19],[14,9,14,10],[14,11,14,12],[14,13,14,15],[14,16,14,17],[14,18,14,19],[15,9,15,10],[15,11,15,12],[15,13,15,15],[15,16,15,17],[15,18,15,19],[16,9,16,10],[16,11,16,12],[16,13,16,15],[16,16,16,17],[16,18,16,19],[17,9,17,10],[17,11,17,12],[17,13,17,15],[17,16,17,17],[17,18,17,19],[18,9,18,10],[18,11,18,12],[18,13,18,15],[18,16,18,17],[18,18,18,19],[19,9,19,10],[19,11,19,12],[19,13,19,15],[19,16,19,17],[19,18,19,19],[20,1,20,22]],"flags":["formulas_cached_only"]}
["","","Символ прибора","Символ\nпомещ.","tв\n[°C]","Qтреб\n[Вт]","Qподобр\n[Вт]","Qприт.\n[Вт]","G\n[кг/ч]","tп\n[°C]",null,"tо\n[°C]",null,"Тип\nрадиатора",null,null,"L\n[мм]",null,"H\n[мм]",null,"УВП\n","УВО\n","Q'/Q\n[%]"]
["","","","","","","","","","","","","","","","","","","","","","",""]
["Источник: (без имени)"]
[null,"Группа: Элементы несгруппированные"]
[null,null,"Р: _а","",20,2224,2224,0,106.9,69.3,null,51.4,null,"11/600",null,null,3000,null,600,null,21,12,100]
[null,null,"Р: _б","",20,2224,2224,0,105.7,69.4,null,51.3,null,"11/600",null,null,3000,null,600,null,19,14,100]
[null,null,"Р: _в","",20,2224,2224,0,104.8,69.5,null,51.3,null,"11/600",null,null,3000,null,600,null,17,16,100]
[null,null,"Р: _г","",20,2224,2224,0,104,69.6,null,51.2,null,"11/600",null,null,3000,null,600,null,15,18,100]
[null,null,"Р: _д","",20,2224,2224,0,103.3,69.7,null,51.2,null,"11/600",null,null,3000,null,600,null,13,20,100]
[null,null,"Р: _е","",20,2224,2224,0,102.8,69.7,null,51.1,null,"11/600",null,null,3000,null,600,null,11,22,100]
[null,null,"Р: _ж","",20,2224,2224,0,102.5,69.8,null,51.1,null,"11/600",null,null,3000,null,600,null,9,24,100]
[null,null,"Р: _з","",20,2224,2224,0,101.9,69.8,null,51.1,null,"11/600",null,null,3000,null,600,null,7,26,100]
[null,null,"Р: _и","",20,2224,2224,0,109.1,69.1,null,51.6,null,"11/600",null,null,3000,null,600,null,23,10,100]
[null,null,"Р: _й","",20,2224,2224,0,101.7,69.9,null,51.1,null,"11/600",null,null,3000,null,600,null,5,28,100]
[null,null,"Р: _к","",20,2224,2224,0,101.5,69.9,null,51,null,"11/600",null,null,3000,null,600,null,3,30,100]
[null,null,"Р: _л","",20,2224,2224,0,108.5,69.2,null,51.5,null,"11/600",null,null,3000,null,600,null,25,8,100]
[null,null,"Р: _м","",20,2224,2224,0,112,68.8,null,51.8,null,"11/600",null,null,3000,null,600,null,27,6,100]
[null,null,"Р: _н","",20,2224,2224,0,90.5,68.3,null,47.2,null,"22/600",null,null,2000,null,600,null,29,4,100]
[null,null,"Р: _о","",20,2224,2224,0,93.7,67.9,null,47.5,null,"22/600",null,null,2000,null,600,null,"30_а",2,100]
[null,null,"Р: _п","",20,2224,2224,0,101.5,69.9,null,51,null,"11/600",null,null,3000,null,600,null,31,"31_а",100]
[null,""]

{"sheet":"Контуры","index":4,"n_rows":198,"n_cols":16,"rows_kept":198,"cut":false,"hidden":false,"merged":[[1,0,1,15],[2,1,2,15],[28,2,28,11],[30,1,30,15],[31,1,31,15],[37,2,37,12],[39,2,39,11],[41,1,41,15],[42,1,42,15],[48,2,48,12],[50,2,50,11],[52,1,52,15],[53,1,53,15],[73,2,73,12],[75,2,75,11],[77,1,77,15],[78,1,78,15],[83,2,83,12],[85,2,85,11],[87,1,87,15],[88,1,88,15],[93,2,93,12],[95,2,95,11],[97,1,97,15],[98,1,98,15],[103,2,103,12],[105,2,105,11],[107,1,107,15],[108,1,108,15],[113,2,113,12],[115,2,115,11],[117,1,117,15],[118,1,118,15],[123,2,123,12],[125,2,125,11],[127,1,127,15],[128,1,128,15],[133,2,133,12],[135,2,135,11],[137,1,137,15],[138,1,138,15],[143,2,143,12],[145,2,145,11],[147,1,147,15],[148,1,148,15],[153,2,153,12],[155,2,155,11],[157,1,157,15],[158,1,158,15],[163,2,163,12],[165,2,165,11],[167,1,167,15],[168,1,168,15],[173,2,173,12],[175,2,175,11],[177,1,177,15],[178,1,178,15],[183,2,183,12],[185,2,185,11],[187,1,187,15],[188,1,188,15],[193,2,193,12],[195,2,195,11],[197,1,197,15]],"flags":["formulas_cached_only"]}
["","","Описание","Расход Q [Вт]","G\n[кг/ч]","L\n[м]","Диаметр\n[мм]","v\n[м/с]","i\n[Па/м]","ζ","Z\n[Па]","i*L+Z\n[Па]","Пот.давл.на фитингах\n[Па]","Полн.потери напора\n[Па]","Δt\n[K]","h изол\n[мм]"]
["Источник: (без имени)"]
[null,"Контур через радиатор _м"]
[null,null,"И",35586,1651,"","","","","","","","",0,"",""]
[null,null,"И (H треб.)","","","","","","","","","","",-13289,"",""]
[null,null,1,35586,1651,1.4,"63 x 6.0",0.23,12,0.4,0,17,0,17,0,25]
[null,null,2,33362,1549,2.4,"63 x 6.0",0.22,11,0.8,39,64,0,64,0,25]
[null,null,4,31138,1448,2.9,"63 x 6.0",0.2,9,0.8,9,37,0,37,0,25]
[null,null,6,28914,1346,3,"50 x 4.5",0.29,24,0.8,8,79,0,79,0,25]
[null,null,8,26690,1244,6,"50 x 4.5",0.27,21,2.4,72,195,0,195,0.1,25]
[null,null,10,24466,1141,3.2,"50 x 4.5",0.25,18,0.8,14,70,0,70,0,25]
[null,null,12,22242,1039,4.2,"50 x 4.5",0.22,15,0.8,12,74,0,74,0,25]
[null,null,14,20017,935,6.3,"50 x 4.5",0.2,12,0.8,10,89,0,89,0.1,25]
[null,null,16,17793,831,5.8,"40 x 4.0",0.29,33,0.9,8,198,0,198,0.1,20]
[null,null,18,15569,727,5.9,"40 x 4.0",0.26,26,1,21,174,0,174,0.1,20]
[null,null,20,13345,621,7.1,"40 x 4.0",0.22,20,2.5,63,202,0,202,0.1,20]
[null,null,"20_а",13345,621,0.5,"40 x 4.0",0.22,20,0.5,0,10,0,10,0,20]
[null,null,22,11121,514,5.6,"32 x 3.0",0.28,38,1.2,12,224,0,224,0.1,20]
[null,null,24,8897,405,2.1,"32 x 3.0",0.22,25,1.4,26,78,0,78,0.1,20]
[null,null,26,6672,296,10.4,"25 x 2.5",0.27,50,2.4,62,586,0,586,0.3,20]
[null,null,27,2224,112,1.1,"16 x 2.0",0.28,103,0.8,128,245,10259,10504,0.1,20]
[null,null,"Р",2224,112,"","","","","","","",0,203,17.1,""]
[null,null,"Р (H грав)","","","","","","","","","","",-28,"",""]
[null,null,6,2224,112,0.6,"16 x 2.0",0.28,109,1.4,88,157,0,157,0,20]
[null,null,5,31138,1466,12.1,"63 x 6.0",0.2,10,0.8,9,134,0,134,0.1,25]
[null,null,3,33362,1557,6.2,"63 x 6.0",0.21,11,0.8,10,82,0,82,0,25]
[null,null,"1_а",35586,1651,9.5,"63 x 6.0",0.23,13,0.4,0,120,0,120,0,25]
[null,null,1,35586,1651,1.8,"63 x 6.0",0.23,13,0,0,23,0,23,0,25]
[null,null,"",{"$nulls":9},"Сумма",0]
[]
[null,""]
[null,"Контур через радиатор _н"]
[null,null,28,4448,184,12.1,"20 x 2.25",0.28,73,1.6,28,915,0,915,0.5,20]
[null,null,29,2224,91,1.2,"16 x 2.0",0.23,71,1.6,166,248,9673,9921,0.1,20]
[null,null,"Р",2224,91,"","","","","","","",0,41,21.1,""]
[null,null,"Р (H грав)","","","","","","","","","","",-31,"",""]
[null,null,4,2224,91,0.7,"16 x 2.0",0.22,77,1.4,74,124,0,124,0,20]
[null,null,"На элементах, описаных ранее",{"$nulls":10},""]
[]
[null,null,"",{"$nulls":9},"Сумма",0]
[]
[null,""]
[null,"Контур через радиатор _о"]
[null,null,30,2224,94,6.2,"16 x 2.0",0.24,76,7.2,203,677,4606,5283,0.4,20]
[null,null,"30_а",2224,94,1.2,"16 x 2.0",0.24,76,0,11,100,4604,4704,0.1,20]
[null,null,"Р",2224,94,"","","","","","","",0,44,20.4,""]
[null,null,"Р (H грав)","","","","","","","","","","",-31,"",""]
[null,null,2,2224,94,0.7,"16 x 2.0",0.23,81,1.4,81,136,0,136,0,20]
[null,null,"На элементах, описаных ранее",{"$nulls":10},""]
[]
[null,null,"",{"$nulls":9},"Сумма",0]
[]
[null,""]
[null,"Контур через радиатор _п"]
[null,null,31,2224,102,1.6,"16 x 2.0",0.26,87,2.8,128,268,10236,10504,0.1,20]
[null,null,"Р",2224,102,"","","","","","","",0,167,18.8,""]
[null,null,"Р (H грав)","","","","","","","","","","",-30,"",""]
[null,null,"31_а",2224,102,1.3,"16 x 2.0",0.25,92,0,0,115,0,115,0.1,20]
[null,null,31,2224,102,1.8,"16 x 2.0",0.25,92,0.8,13,177,0,177,0.1,20]
[null,null,29,4448,203,2.9,"25 x 2.5",0.18,27,1.6,29,110,0,110,0.1,20]
[null,null,27,6672,305,4,"25 x 2.5",0.27,56,2.4,49,270,0,270,0.1,20]
[null,null,"25_а",8897,407,1.9,"32 x 3.0",0.22,27,0.7,0,51,0,51,0,20]
[null,null,25,8897,407,2.4,"32 x 3.0",0.22,27,3,78,142,0,142,0,20]
[null,null,23,11121,509,3.2,"32 x 3.0",0.27,39,1.2,11,136,0,136,0,20]
[null,null,21,13345,612,4.2,"40 x 4.0",0.21,20,1,15,101,0,101,0,20]
[null,null,19,15569,715,6.3,"40 x 4.0",0.25,27,1,20,190,0,190,0.1,20]
[null,null,17,17793,819,5.8,"40 x 4.0",0.29,34,0.9,8,204,0,204,0,20]
[null,null,15,20017,924,5.9,"50 x 4.5",0.2,13,0.8,10,86,0,86,0,25]
[null,null,"13_а",22242,1030,7.3,"50 x 4.5",0.22,16,0.4,0,113,0,113,0.1,25]
[null,null,13,22242,1030,0.5,"50 x 4.5",0.22,16,2,50,57,0,57,0,25]
[null,null,11,24466,1137,5.6,"50 x 4.5",0.24,19,0.8,14,118,0,118,0,25]
[null,null,9,26690,1246,2.1,"50 x 4.5",0.27,22,0.8,16,62,0,62,0,25]
[null,null,7,28914,1354,10.6,"50 x 4.5",0.29,25,2.4,74,343,0,343,0.1,25]
[null,null,"На элементах, описаных ранее",{"$nulls":10},""]
[]
[null,null,"",{"$nulls":9},"Сумма",0]
[]
[null,""]
[null,"Контур через радиатор _к"]
[null,null,3,2224,101,1.2,"16 x 2.0",0.26,87,1.4,83,187,10457,10644,0.1,20]
[null,null,"Р",2224,101,"","","","","","","",0,167,18.8,""]
[null,null,"Р (H грав)","","","","","","","","","","",-30,"",""]
[null,null,30,2224,101,0.3,"16 x 2.0",0.25,92,0.8,65,88,0,88,0,20]
[null,null,"На элементах, описаных ранее",{"$nulls":10},""]
[]
[null,null,"",{"$nulls":9},"Сумма",0]
[]
[null,""]
[null,"Контур через радиатор _й"]
[null,null,5,2224,102,1.2,"16 x 2.0",0.26,87,1.4,78,183,10468,10651,0.1,20]
[null,null,"Р",2224,102,"","","","","","","",0,168,18.8,""]
[null,null,"Р (H грав)","","","","","","","","","","",-30,"",""]
[null,null,28,2224,102,0.2,"16 x 2.0",0.25,93,0.8,130,153,0,153,0,20]
[null,null,"На элементах, описаных ранее",{"$nulls":10},""]
[]
[null,null,"",{"$nulls":9},"Сумма",0]
[]
[null,""]
[null,"Контур через радиатор _з"]
[null,null,7,2224,102,1.2,"16 x 2.0",0.26,87,1.4,123,224,10556,10780,0.1,20]
[null,null,"Р",2224,102,"","","","","","","",0,168,18.8,""]
[null,null,"Р (H грав)","","","","","","","","","","",-30,"",""]
[null,null,26,2224,102,1.4,"16 x 2.0",0.25,93,0.7,85,215,0,215,0.1,20]
[null,null,"На элементах, описаных ранее",{"$nulls":10},""]
[]
[null,null,"",{"$nulls":9},"Сумма",0]
[]
[null,""]
[null,"Контур через радиатор _ж"]
[null,null,9,2224,103,1.2,"16 x 2.0",0.26,88,1.4,112,222,10630,10852,0.1,20]
[null,null,"Р",2224,103,"","","","","","","",0,170,18.7,""]
[null,null,"Р (H грав)","","","","","","","","","","",-30,"",""]
[null,null,24,2224,103,0.3,"16 x 2.0",0.26,94,0.7,106,139,0,139,0,20]
[null,null,"На элементах, описаных ранее",{"$nulls":10},""]
[]
[null,null,"",{"$nulls":9},"Сумма",0]
[]
[null,""]
[null,"Контур через радиатор _е"]
[null,null,11,2224,103,1.2,"16 x 2.0",0.26,89,1.4,102,209,10719,10928,0.1,20]
[null,null,"Р",2224,103,"","","","","","","",0,171,18.6,""]
[null,null,"Р (H грав)","","","","","","","","","","",-30,"",""]
[null,null,22,2224,103,0.3,"16 x 2.0",0.26,94,1.5,100,128,0,128,0,20]
[null,null,"На элементах, описаных ранее",{"$nulls":10},""]
[]
[null,null,"",{"$nulls":9},"Сумма",0]
[]
[null,""]
[null,"Контур через радиатор _д"]
[null,null,13,2224,103,1.3,"16 x 2.0",0.26,90,1.4,93,204,10716,10921,0.1,20]
[null,null,"Р",2224,103,"","","","","","","",0,173,18.5,""]
[null,null,"Р (H грав)","","","","","","","","","","",-30,"",""]
[null,null,20,2224,103,0.4,"16 x 2.0",0.26,95,1.7,126,160,0,160,0,20]
[null,null,"На элементах, описаных ранее",{"$nulls":10},""]
[]
[null,null,"",{"$nulls":9},"Сумма",0]
[]
[null,""]
[null,"Контур через радиатор _г"]
[null,null,15,2224,104,1.3,"16 x 2.0",0.26,91,1.4,84,198,10796,10995,0.1,20]
[null,null,"Р",2224,104,"","","","","","","",0,175,18.4,""]
[null,null,"Р (H грав)","","","","","","","","","","",-29,"",""]
[null,null,18,2224,104,0.4,"16 x 2.0",0.26,96,1.7,150,184,0,184,0,20]
[null,null,"На элементах, описаных ранее",{"$nulls":10},""]
[]
[null,null,"",{"$nulls":9},"Сумма",0]
[]
[null,""]
[null,"Контур через радиатор _в"]
[null,null,17,2224,105,1.2,"16 x 2.0",0.26,92,1.7,155,269,10796,11065,0.1,20]
[null,null,"Р",2224,105,"","","","","","","",0,178,18.2,""]
[null,null,"Р (H грав)","","","","","","","","","","",-29,"",""]
[null,null,16,2224,105,0.3,"16 x 2.0",0.26,98,1.4,83,117,0,117,0,20]
[null,null,"На элементах, описаных ранее",{"$nulls":10},""]
[]
[null,null,"",{"$nulls":9},"Сумма",0]
[]
[null,""]
[null,"Контур через радиатор _б"]
[null,null,19,2224,106,1.2,"16 x 2.0",0.27,93,2.5,160,277,10686,10963,0.1,20]
[null,null,"Р",2224,106,"","","","","","","",0,181,18.1,""]
[null,null,"Р (H грав)","","","","","","","","","","",-29,"",""]
[null,null,14,2224,106,0.3,"16 x 2.0",0.26,99,1.4,93,128,0,128,0,20]
[null,null,"На элементах, описаных ранее",{"$nulls":10},""]
[]
[null,null,"",{"$nulls":9},"Сумма",0]
[]
[null,""]
[null,"Контур через радиатор _а"]
[null,null,21,2224,107,1,"16 x 2.0",0.27,95,1.5,106,198,10695,10893,0.1,20]
[null,null,"Р",2224,107,"","","","","","","",0,185,17.9,""]
[null,null,"Р (H грав)","","","","","","","","","","",-29,"",""]
[null,null,12,2224,107,0.5,"16 x 2.0",0.27,101,1.4,104,151,0,151,0,20]
[null,null,"На элементах, описаных ранее",{"$nulls":10},""]
[]
[null,null,"",{"$nulls":9},"Сумма",0]
[]
[null,""]
[null,"Контур через радиатор _и"]
[null,null,23,2224,109,2.6,"16 x 2.0",0.27,99,1.5,126,384,10223,10607,0.2,20]
[null,null,"Р",2224,109,"","","","","","","",0,193,17.5,""]
[null,null,"Р (H грав)","","","","","","","","","","",-29,"",""]
[null,null,10,2224,109,2.1,"16 x 2.0",0.27,105,1.4,103,324,0,324,0.1,20]
[null,null,"На элементах, описаных ранее",{"$nulls":10},""]
[]
[null,null,"",{"$nulls":9},"Сумма",0]
[]
[null,""]
[null,"Контур через радиатор _л"]
[null,null,25,2224,109,0.9,"16 x 2.0",0.27,98,0.7,74,163,10582,10746,0.1,20]
[null,null,"Р",2224,109,"","","","","","","",0,191,17.6,""]
[null,null,"Р (H грав)","","","","","","","","","","",-29,"",""]
[null,null,8,2224,109,0.4,"16 x 2.0",0.27,104,1.4,129,171,0,171,0,20]
[null,null,"На элементах, описаных ранее",{"$nulls":10},""]
[]
[null,null,"",{"$nulls":9},"Сумма",0]
[]
[null,""]

{"sheet":"Список элем.на приборах","index":5,"n_rows":115,"n_cols":7,"rows_kept":115,"cut":false,"hidden":false,"merged":[[1,0,1,6],[2,1,2,6],[3,2,3,6],[10,2,10,6],[17,2,17,6],[24,2,24,6],[31,2,31,6],[38,2,38,6],[45,2,45,6],[52,2,52,6],[59,2,59,6],[66,2,66,6],[73,2,73,6],[80,2,80,6],[87,2,87,6],[94,2,94,6],[101,2,101,6],[108,2,108,6]],"flags":["formulas_cached_only"]}
["","","","Каталог","Название элемента","Артикул по каталогу","Сопр.\n[Па]"]
["Источник: (без имени)"]
[null,"Группа: Элементы несгруппированные"]
[null,null,"Прибор в пом.\"(без имени)\", символ \"_а\", мощность=2224 [Вт], расход=106.9 [кг/ч]"]
[null,null,null,"Муфты и фасонные изделия бронзовые и стальные","Колено в/з равнопроходное - 1/2\"внут. - 1/2\"нар.","",14]
[null,null,null,"UPONOR - UNIPIPE","Пресс-соединение НР - 16 - 1/2\"нар.","90 22 20",14]
[null,null,null,"UPONOR - UNIPIPE","Декоративное кольцо - 16","43 30 16",0]
[null,null,null,"Муфты и фасонные изделия бронзовые и стальные","Колено в/з равнопроходное - 1/2\"внут. - 1/2\"нар.","",14]
[null,null,null,"UPONOR - UNIPIPE","Пресс-соединение НР - 16 - 1/2\"нар.","90 22 20",14]
[null,null,null,"UPONOR - UNIPIPE","Декоративное кольцо - 16","43 30 16",0]
[null,null,"Прибор в пом.\"(без имени)\", символ \"_б\", мощность=2224 [Вт], расход=105.7 [кг/ч]"]
[null,null,null,"Муфты и фасонные изделия бронзовые и стальные","Колено в/з равнопроходное - 1/2\"внут. - 1/2\"нар.","",14]
[null,null,null,"UPONOR - UNIPIPE","Пресс-соединение НР - 16 - 1/2\"нар.","90 22 20",14]
[null,null,null,"UPONOR - UNIPIPE","Декоративное кольцо - 16","43 30 16",0]
[null,null,null,"Муфты и фасонные изделия бронзовые и стальные","Колено в/з равнопроходное - 1/2\"внут. - 1/2\"нар.","",14]
[null,null,null,"UPONOR - UNIPIPE","Пресс-соединение НР - 16 - 1/2\"нар.","90 22 20",14]
[null,null,null,"UPONOR - UNIPIPE","Декоративное кольцо - 16","43 30 16",0]
[null,null,"Прибор в пом.\"(без имени)\", символ \"_в\", мощность=2224 [Вт], расход=104.8 [кг/ч]"]
[null,null,null,"Муфты и фасонные изделия бронзовые и стальные","Колено в/з равнопроходное - 1/2\"внут. - 1/2\"нар.","",14]
[null,null,null,"UPONOR - UNIPIPE","Пресс-соединение НР - 16 - 1/2\"нар.","90 22 20",14]
[null,null,null,"UPONOR - UNIPIPE","Декоративное кольцо - 16","43 30 16",0]
[null,null,null,"Муфты и фасонные изделия бронзовые и стальные","Колено в/з равнопроходное - 1/2\"внут. - 1/2\"нар.","",14]
[null,null,null,"UPONOR - UNIPIPE","Пресс-соединение НР - 16 - 1/2\"нар.","90 22 20",14]
[null,null,null,"UPONOR - UNIPIPE","Декоративное кольцо - 16","43 30 16",0]
[null,null,"Прибор в пом.\"(без имени)\", символ \"_г\", мощность=2224 [Вт], расход=104.0 [кг/ч]"]
[null,null,null,"Муфты и фасонные изделия бронзовые и стальные","Колено в/з равнопроходное - 1/2\"внут. - 1/2\"нар.","",13]
[null,null,null,"UPONOR - UNIPIPE","Пресс-соединение НР - 16 - 1/2\"нар.","90 22 20",13]
[null,null,null,"UPONOR - UNIPIPE","Декоративное кольцо - 16","43 30 16",0]
[null,null,null,"Муфты и фасонные изделия бронзовые и стальные","Колено в/з равнопроходное - 1/2\"внут. - 1/2\"нар.","",13]
[null,null,null,"UPONOR - UNIPIPE","Пресс-соединение НР - 16 - 1/2\"нар.","90 22 20",13]
[null,null,null,"UPONOR - UNIPIPE","Декоративное кольцо - 16","43 30 16",0]
[null,null,"Прибор в пом.\"(без имени)\", символ \"_д\", мощность=2224 [Вт], расход=103.3 [кг/ч]"]
[null,null,null,"Муфты и фасонные изделия бронзовые и стальные","Колено в/з равнопроходное - 1/2\"внут. - 1/2\"нар.","",13]
[null,null,null,"UPONOR - UNIPIPE","Пресс-соединение НР - 16 - 1/2\"нар.","90 22 20",13]
[null,null,null,"UPONOR - UNIPIPE","Декоративное кольцо - 16","43 30 16",0]
[null,null,null,"Муфты и фасонные изделия бронзовые и стальные","Колено в/з равнопроходное - 1/2\"внут. - 1/2\"нар.","",13]
[null,null,null,"UPONOR - UNIPIPE","Пресс-соединение НР - 16 - 1/2\"нар.","90 22 20",13]
[null,null,null,"UPONOR - UNIPIPE","Декоративное кольцо - 16","43 30 16",0]
[null,null,"Прибор в пом.\"(без имени)\", символ \"_е\", мощность=2224 [Вт], расход=102.8 [кг/ч]"]
[null,null,null,"Муфты и фасонные изделия бронзовые и стальные","Колено в/з равнопроходное - 1/2\"внут. - 1/2\"нар.","",13]
[null,null,null,"UPONOR - UNIPIPE","Пресс-соединение НР - 16 - 1/2\"нар.","90 22 20",13]
[null,null,null,"UPONOR - UNIPIPE","Декоративное кольцо - 16","43 30 16",0]
[null,null,null,"Муфты и фасонные изделия бронзовые и стальные","Колено в/з равнопроходное - 1/2\"внут. - 1/2\"нар.","",13]
[null,null,null,"UPONOR - UNIPIPE","Пресс-соединение НР - 16 - 1/2\"нар.","90 22 20",13]
[null,null,null,"UPONOR - UNIPIPE","Декоративное кольцо - 16","43 30 16",0]
[null,null,"Прибор в пом.\"(без имени)\", символ \"_ж\", мощность=2224 [Вт], расход=102.5 [кг/ч]"]
[null,null,null,"Муфты и фасонные изделия бронзовые и стальные","Колено в/з равнопроходное - 1/2\"внут. - 1/2\"нар.","",13]
[null,null,null,"UPONOR - UNIPIPE","Пресс-соединение НР - 16 - 1/2\"нар.","90 22 20",13]
[null,null,null,"UPONOR - UNIPIPE","Декоративное кольцо - 16","43 30 16",0]
[null,null,null,"Муфты и фасонные изделия бронзовые и стальные","Колено в/з равнопроходное - 1/2\"внут. - 1/2\"нар.","",13]
[null,null,null,"UPONOR - UNIPIPE","Пресс-соединение НР - 16 - 1/2\"нар.","90 22 20",13]
[null,null,null,"UPONOR - UNIPIPE","Декоративное кольцо - 16","43 30 16",0]
[null,null,"Прибор в пом.\"(без имени)\", символ \"_з\", мощность=2224 [Вт], расход=101.9 [кг/ч]"]
[null,null,null,"Муфты и фасонные изделия бронзовые и стальные","Колено в/з равнопроходное - 1/2\"внут. - 1/2\"нар.","",13]
[null,null,null,"UPONOR - UNIPIPE","Пресс-соединение НР - 16 - 1/2\"нар.","90 22 20",13]
[null,null,null,"UPONOR - UNIPIPE","Декоративное кольцо - 16","43 30 16",0]
[null,null,null,"Муфты и фасонные изделия бронзовые и стальные","Колено в/з равнопроходное - 1/2\"внут. - 1/2\"нар.","",13]
[null,null,null,"UPONOR - UNIPIPE","Пресс-соединение НР - 16 - 1/2\"нар.","90 22 20",13]
[null,null,null,"UPONOR - UNIPIPE","Декоративное кольцо - 16","43 30 16",0]
[null,null,"Прибор в пом.\"(без имени)\", символ \"_и\", мощность=2224 [Вт], расход=109.1 [кг/ч]"]
[null,null,null,"Муфты и фасонные изделия бронзовые и стальные","Колено в/з равнопроходное - 1/2\"внут. - 1/2\"нар.","",15]
[null,null,null,"UPONOR - UNIPIPE","Пресс-соединение НР - 16 - 1/2\"нар.","90 22 20",15]
[null,null,null,"UPONOR - UNIPIPE","Декоративное кольцо - 16","43 30 16",0]
[null,null,null,"Муфты и фасонные изделия бронзовые и стальные","Колено в/з равнопроходное - 1/2\"внут. - 1/2\"нар.","",15]
[null,null,null,"UPONOR - UNIPIPE","Пресс-соединение НР - 16 - 1/2\"нар.","90 22 20",15]
[null,null,null,"UPONOR - UNIPIPE","Декоративное кольцо - 16","43 30 16",0]
[null,null,"Прибор в пом.\"(без имени)\", символ \"_й\", мощность=2224 [Вт], расход=101.7 [кг/ч]"]
[null,null,null,"Муфты и фасонные изделия бронзовые и стальные","Колено в/з равнопроходное - 1/2\"внут. - 1/2\"нар.","",13]
[null,null,null,"UPONOR - UNIPIPE","Пресс-соединение НР - 16 - 1/2\"нар.","90 22 20",13]
[null,null,null,"UPONOR - UNIPIPE","Декоративное кольцо - 16","43 30 16",0]
[null,null,null,"Муфты и фасонные изделия бронзовые и стальные","Колено в/з равнопроходное - 1/2\"внут. - 1/2\"нар.","",13]
[null,null,null,"UPONOR - UNIPIPE","Пресс-соединение НР - 16 - 1/2\"нар.","90 22 20",13]
[null,null,null,"UPONOR - UNIPIPE","Декоративное кольцо - 16","43 30 16",0]
[null,null,"Прибор в пом.\"(без имени)\", символ \"_к\", мощность=2224 [Вт], расход=101.5 [кг/ч]"]
[null,null,null,"Муфты и фасонные изделия бронзовые и стальные","Колено в/з равнопроходное - 1/2\"внут. - 1/2\"нар.","",13]
[null,null,null,"UPONOR - UNIPIPE","Пресс-соединение НР - 16 - 1/2\"нар.","90 22 20",13]
[null,null,null,"UPONOR - UNIPIPE","Декоративное кольцо - 16","43 30 16",0]
[null,null,null,"Муфты и фасонные изделия бронзовые и стальные","Колено в/з равнопроходное - 1/2\"внут. - 1/2\"нар.","",13]
[null,null,null,"UPONOR - UNIPIPE","Пресс-соединение НР - 16 - 1/2\"нар.","90 22 20",13]
[null,null,null,"UPONOR - UNIPIPE","Декоративное кольцо - 16","43 30 16",0]
[null,null,"Прибор в пом.\"(без имени)\", символ \"_л\", мощность=2224 [Вт], расход=108.5 [кг/ч]"]
[null,null,null,"Муфты и фасонные изделия бронзовые и стальные","Колено в/з равнопроходное - 1/2\"внут. - 1/2\"нар.","",15]
[null,null,null,"UPONOR - UNIPIPE","Пресс-соединение НР - 16 - 1/2\"нар.","90 22 20",15]
[null,null,null,"UPONOR - UNIPIPE","Декоративное кольцо - 16","43 30 16",0]
[null,null,null,"Муфты и фасонные изделия бронзовые и стальные","Колено в/з равнопроходное - 1/2\"внут. - 1/2\"нар.","",15]
[null,null,null,"UPONOR - UNIPIPE","Пресс-соединение НР - 16 - 1/2\"нар.","90 22 20",15]
[null,null,null,"UPONOR - UNIPIPE","Декоративное кольцо - 16","43 30 16",0]
[null,null,"Прибор в пом.\"(без имени)\", символ \"_м\", мощность=2224 [Вт], расход=112.0 [кг/ч]"]
[null,null,null,"Муфты и фасонные изделия бронзовые и стальные","Колено в/з равнопроходное - 1/2\"внут. - 1/2\"нар.","",15]
[null,null,null,"UPONOR - UNIPIPE","Пресс-соединение НР - 16 - 1/2\"нар.","90 22 20",15]
[null,null,null,"UPONOR - UNIPIPE","Декоративное кольцо - 16","43 30 16",0]
[null,null,null,"Муфты и фасонные изделия бронзовые и стальные","Колено в/з равнопроходное - 1/2\"внут. - 1/2\"нар.","",15]
[null,null,null,"UPONOR - UNIPIPE","Пресс-соединение НР - 16 - 1/2\"нар.","90 22 20",15]
[null,null,null,"UPONOR - UNIPIPE","Декоративное кольцо - 16","43 30 16",0]
[null,null,"Прибор в пом.\"(без имени)\", символ \"_н\", мощность=2224 [Вт], расход=90.5 [кг/ч]"]
[null,null,null,"Муфты и фасонные изделия бронзовые и стальные","Колено в/з равнопроходное - 1/2\"внут. - 1/2\"нар.","",10]
[null,null,null,"UPONOR - UNIPIPE","Пресс-соединение НР - 16 - 1/2\"нар.","90 22 20",10]
[null,null,null,"UPONOR - UNIPIPE","Декоративное кольцо - 16","43 30 16",0]
[null,null,null,"Муфты и фасонные изделия бронзовые и стальные","Колено в/з равнопроходное - 1/2\"внут. - 1/2\"нар.","",10]
[null,null,null,"UPONOR - UNIPIPE","Пресс-соединение НР - 16 - 1/2\"нар.","90 22 20",10]
[null,null,null,"UPONOR - UNIPIPE","Декоративное кольцо - 16","43 30 16",0]
[null,null,"Прибор в пом.\"(без имени)\", символ \"_о\", мощность=2224 [Вт], расход=93.7 [кг/ч]"]
[null,null,null,"Муфты и фасонные изделия бронзовые и стальные","Колено в/з равнопроходное - 1/2\"внут. - 1/2\"нар.","",11]
[null,null,null,"UPONOR - UNIPIPE","Пресс-соединение НР - 16 - 1/2\"нар.","90 22 20",11]
[null,null,null,"UPONOR - UNIPIPE","Декоративное кольцо - 16","43 30 16",0]
[null,null,null,"Муфты и фасонные изделия бронзовые и стальные","Колено в/з равнопроходное - 1/2\"внут. - 1/2\"нар.","",11]
[null,null,null,"UPONOR - UNIPIPE","Пресс-соединение НР - 16 - 1/2\"нар.","90 22 20",11]
[null,null,null,"UPONOR - UNIPIPE","Декоративное кольцо - 16","43 30 16",0]
[null,null,"Прибор в пом.\"(без имени)\", символ \"_п\", мощность=2224 [Вт], расход=101.5 [кг/ч]"]
[null,null,null,"Муфты и фасонные изделия бронзовые и стальные","Колено в/з равнопроходное - 1/2\"внут. - 1/2\"нар.","",13]
[null,null,null,"UPONOR - UNIPIPE","Пресс-соединение НР - 16 - 1/2\"нар.","90 22 20",13]
[null,null,null,"UPONOR - UNIPIPE","Декоративное кольцо - 16","43 30 16",0]
[null,null,null,"Муфты и фасонные изделия бронзовые и стальные","Колено в/з равнопроходное - 1/2\"внут. - 1/2\"нар.","",13]
[null,null,null,"UPONOR - UNIPIPE","Пресс-соединение НР - 16 - 1/2\"нар.","90 22 20",13]
[null,null,null,"UPONOR - UNIPIPE","Декоративное кольцо - 16","43 30 16",0]

{"sheet":"Специф.Мат. - Трубы","index":6,"n_rows":44,"n_cols":7,"rows_kept":44,"cut":false,"hidden":false,"merged":[[2,0,2,6],[3,0,3,6],[4,1,4,6],[12,1,12,6],[40,0,40,6],[41,1,41,6]],"flags":["formulas_cached_only"]}
["","","","","","",""]
["","","Продукт","Размер","Код по каталогу","Количество","Единица"]
["Перечень труб, фасонных деталей и муфт"]
["UPONOR - UNIPIPE"]
[null,"Трубы - UPONOR - UNIPIPE"]
[null,null,"UNIPIPE белая в бухтах","16 x 2.0","70 01 60",39,"м"]
[null,null,"UNIPIPE белая в бухтах","20 x 2.25","70 02 00",13,"м"]
[null,null,"UNIPIPE белая в бухтах","25 x 2.5","70 02 50",18,"м"]
[null,null,"UNIPIPE белая в бухтах","32 x 3.0","70 03 20",16,"м"]
[null,null,"UNIPIPE белая в штангах","40 x 4.0","71 04 00",36,"м"]
[null,null,"UNIPIPE белая в штангах","50 x 4.5","71 05 00",55,"м"]
[null,null,"UNIPIPE белая в штангах","63 x 6.0","71 06 30",37,"м"]
[null,"Фитинги - UPONOR - UNIPIPE"]
[null,null,"Декоративное кольцо",16,"43 30 16",32,"шт."]
[null,null,"Пресс-муфта/редуктор","40 - 40","94 71 70",5,"шт."]
[null,null,"Пресс-муфта/редуктор","50 - 50","94 81 80",6,"шт."]
[null,null,"Пресс-муфта/редуктор","63 - 63","79 43 01",4,"шт."]
[null,null,"Пресс-муфта/редуктор","20 - 16","94 41 20",5,"шт."]
[null,null,"Пресс-муфта/редуктор","25 - 16","94 51 20",18,"шт."]
[null,null,"Пресс-муфта/редуктор","32 - 25","94 61 50",2,"шт."]
[null,null,"Пресс-муфта/редуктор","40 - 25","94 71 50",1,"шт."]
[null,null,"Пресс-муфта/редуктор","63 - 40","79 43 03",1,"шт."]
[null,null,"Пресс-соединение ВР","16 - 1/2\"внут.","90 23 20",4,"шт."]
[null,null,"Пресс-соединение НР","16 - 1/2\"нар.","90 22 20",35,"шт."]
[null,null,"Пресс-тройник ВР","20 - 1/2\"внут. - 20","93 43 24",1,"шт."]
[null,null,"Пресс-тройник/с редуктором","63 - 63 - 63","79 33 01",1,"шт."]
[null,null,"Пресс-тройник/с редуктором","25 - 16 - 16","93 51 22",1,"шт."]
[null,null,"Пресс-тройник/с редуктором","25 - 16 - 20","93 51 24",1,"шт."]
[null,null,"Пресс-тройник/с редуктором","25 - 16 - 25","93 51 25",1,"шт."]
[null,null,"Пресс-тройник/с редуктором","32 - 16 - 32","93 61 26",4,"шт."]
[null,null,"Пресс-тройник/с редуктором","40 - 20 - 40","93 71 47",4,"шт."]
[null,null,"Пресс-тройник/с редуктором","40 - 25 - 32","93 71 56",2,"шт."]
[null,null,"Пресс-тройник/с редуктором","50 - 25 - 40","93 81 57",2,"шт."]
[null,null,"Пресс-тройник/с редуктором","50 - 25 - 50","93 81 58",8,"шт."]
[null,null,"Пресс-тройник/с редуктором","63 - 25 - 50","79 33 22",2,"шт."]
[null,null,"Пресс-тройник/с редуктором","63 - 25 - 63","79 33 05",3,"шт."]
[null,null,"Пресс-угольник 90°","16 - 16","91 21 20",1,"шт."]
[null,null,"Пресс-угольник 90°","32 - 32","91 61 60",1,"шт."]
[null,null,"Пресс-угольник 90°","40 - 40","91 71 70",3,"шт."]
[null,null,"Пресс-угольник 90°","50 - 50","91 81 80",3,"шт."]
["Муфты и фасонные изделия бронзовые и стальные"]
[null,"Фитинги - Муфты и фасонные изделия бронзовые и стальные"]
[null,null,"Колено в/з равнопроходное","1/2\"внут. - 1/2\"нар.","",32,"шт."]
[null,null,"Ниппель дюймовый равнопроходной","1/2\"нар. - 1/2\"нар.","",1,"шт."]

{"sheet":"Специф.Мат. - Клапаны и др.арма","index":7,"n_rows":8,"n_cols":7,"rows_kept":8,"cut":false,"hidden":false,"merged":[[2,0,2,6],[3,0,3,6],[4,1,4,6],[6,1,6,6]],"flags":["formulas_cached_only"]}
["","","","","","",""]
["","","Продукт","Размер","Код по каталогу","Количество","Единица"]
["Комплект клапанов и арматуры"]
["HEIMEIER - клапаны термостатические и регулирующие"]
[null,"Клапаны - HEIMEIER - клапаны термостатические и регулирующие"]
[null,null,"Клапан V-Exakt прямой",15,"3502-02.000",19,"шт."]
[null,"Головки - HEIMEIER - клапаны термостатические и регулирующие"]
[null,null,"Головка термостат. К, станд., датчик встроен.","","6000-09.500",19,"шт."]

{"sheet":"Специф.Мат. - Радиаторы","index":8,"n_rows":7,"n_cols":9,"rows_kept":7,"cut":false,"hidden":false,"merged":[[2,0,2,8],[3,0,3,8],[4,1,4,8]],"flags":["formulas_cached_only"]}
["","","","","","","","",""]
["","","Продукт","H\n[мм]","L\n[мм]","D\n[мм]","Код по каталогу","Количество","Единица"]
["Список радиаторов"]
["KORADO Radik Klasik"]
[null,"Радиаторы правые с бок.подкл. - KORADO Radik Klasik"]
[null,null,"11/600",600,3000,63,"",14,"шт."]
[null,null,"22/600",600,2000,100,"",2,"шт."]

{"sheet":"Специф.Мат. - Изоляция","index":9,"n_rows":12,"n_cols":7,"rows_kept":12,"cut":false,"hidden":false,"merged":[[2,0,2,6],[3,0,3,6],[4,1,4,6]],"flags":["formulas_cached_only"]}
["","","","","","",""]
["","","Продукт","Размер","Код по каталогу","Количество","Единица"]
["Комплект изоляции"]
["                                                        "]
[null,"Изоляция -                                                         "]
[null,null,"Вспененный PU(полиуретан.) - Lambda (40°C) = 0,036W/mK внутр. диам. 18 мм","20 мм","",39,"м"]
[null,null,"Вспененный PU(полиуретан.) - Lambda (40°C) = 0,036W/mK внутр. диам. 22 мм","20 мм","",13,"м"]
[null,null,"Вспененный PU(полиуретан.) - Lambda (40°C) = 0,036W/mK внутр. диам. 25 мм","20 мм","",18,"м"]
[null,null,"Вспененный PU(полиуретан.) - Lambda (40°C) = 0,036W/mK внутр. диам. 35 мм","20 мм","",16,"м"]
[null,null,"Вспененный PU(полиуретан.) - Lambda (40°C) = 0,036W/mK внутр. диам. 42 мм","20 мм","",36,"м"]
[null,null,"Вспененный PU(полиуретан.) - Lambda (40°C) = 0,036W/mK внутр. диам. 54 мм","25 мм","",55,"м"]
[null,null,"Вспененный PU(полиуретан.) - Lambda (40°C) = 0,036W/mK внутр. диам. 63 мм","25 мм","",37,"м"]

{"sheet":"Сводка по трубам","index":10,"n_rows":8,"n_cols":11,"rows_kept":8,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["Тип","Артикул по каталогу","Сокращение","Изолированные\n[м]","В кожухе\n[м]","Неизолированные\n[м]","Заданные\n[м]","Выбранные\n[м]","Существующие\n[м]","Проектируемые\n[м]","Для П.О.\n[м]"]
["UNIPIPE белая в штангах63 x 6.0","71 06 30","UNIP_штан",36.3,0,0,0,36.3,0,36.3,0]
["UNIPIPE белая в штангах50 x 4.5","71 05 00","UNIP_штан",54.6,0,0,0,54.6,0,54.6,0]
["UNIPIPE белая в бухтах32 x 3.0","70 03 20","UNIP_бух",15.2,0,0,0,15.2,0,15.2,0]
["UNIPIPE белая в штангах40 x 4.0","71 04 00","UNIP_штан",35.5,0,0,0,35.5,0,35.5,0]
["UNIPIPE белая в бухтах25 x 2.5","70 02 50","UNIP_бух",17.3,0,0,0,17.3,0,17.3,0]
["UNIPIPE белая в бухтах16 x 2.0","70 01 60","UNIP_бух",38.7,0,0,0,38.7,0,38.7,0]
["UNIPIPE белая в бухтах20 x 2.25","70 02 00","UNIP_бух",12.1,0,0,0,12.1,0,12.1,0]