{"text_format":"2","workbook":"xls","n_sheets":3,"sheets":["Лист1","Лист2","Лист3"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":0,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Лист1","index":0,"n_rows":29,"n_cols":10,"rows_kept":29,"cut":false,"hidden":false,"merged":[[1,0,1,5]],"flags":["formulas_cached_only"]}
[]
["Таблица определения диаметров системы отопления  "]
[]
["№уч.","Q,","G,","Тп-То,","Дв,факт","V,факт",null,"Пояснения к таблице"]
[null,"Вт","кг/час","С","мм","м/с"]
[1,2,3,4,5,6,null,"1-номер расчетного участка"]
[1,5000,214.96130696474634,20,15,0.34537605089752327,null,"2-тепловая нагрузка участка, Вт (задавать самостоятельно)"]
[2,10000,429.9226139294927,20,20,0.3885480572597137,null,"3-расход теплоносителя на участке,кг/час"]
[3,20000,859.8452278589854,20,25,0.49734151329243353,null,"4-разность температур между подачей и обраткой, С (задавать самостоятельно)"]
[4,25000,1074.8065348237317,20,25,0.621676891615542,null,"5-фактический диаметр (задается самостоятельно )"]
[5,30000,1289.7678417884779,20,32,0.455329754601227,null,"6-фактическая скорость теплоносителя в трубопроводе, м/с"]
[6,50000,2149.6130696474634,20,40,0.48568507157464214]
[]
[]
[{"$nulls":7},"Допустимые скорости V, м/с в трубопроводах водяного отопления (ЩЕКИН с.189)"]
[]
[{"$nulls":7},"Ду,мм","Vmin,м/с","Vmax,м/с"]
[{"$nulls":7},10,0.25,0.3]
[{"$nulls":7},15,0.25,0.3]
[{"$nulls":7},20,0.25,0.65]
[{"$nulls":7},25,0.25,0.8]
[{"$nulls":7},32,0.25,1]
[{"$nulls":7},40,0.25,1.5]
[{"$nulls":7},50,0.25,1.5]
[{"$nulls":7},70,0.25,1.5]
[{"$nulls":7},80,0.25,1.5]
[{"$nulls":7},100,0.25,1.5]
[{"$nulls":7},125,0.25,1.5]
[{"$nulls":7},150,0.25,1.5]

{"sheet":"Лист2","index":1,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}

{"sheet":"Лист3","index":2,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}