{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Теплопотери на инфильтрац"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":2,"defined_names":1,"comments":1,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Теплопотери на инфильтрац","index":0,"n_rows":12,"n_cols":19,"rows_kept":12,"cut":false,"hidden":false,"merged":[[20,0,22,0],[20,1,22,1]],"flags":["formulas_cached_only"]}
[null,null,null,"Расход теплоты на нагрев инфильтрующегося воздуха",{"$nulls":9},"Таблица 3.1"]
["№ помещения","Наименование","Температура tв, C˚","Площадь ОК, А, м²","Воздухопрониц. ОК, Gн, кг/(м²·ч)","Сопротивление воздухопроницанию ОК, Rи, (м²·ч)/кг","Высота здания H, м","Удельный вес наружного воздуха γн, Н/м³","Удельный вес внутреннего воздуха γв, Н/м³","Разность давлений ΔP, Па","Расчётная высота h, м","Расчётная разность давлений Δpi, Па","Расход инфильтрующегося воздуха Gи, кг/ч","Теплопотери на инфильтрацию Qи, Вт","Пол"]
[1,2,3,4,5,6,7,8,9,10,11,12,13,14,{"$nulls":4},140]
[101,null,18,9,5,0.5456534317785945,23.2,14.550420168067227,11.900343642611684,44.72779159086314,3.65,64.07194607265586,57.84247569502419,860]
[102,null,16,12.6,5,0.5370305069268754,23.2,14.550420168067227,11.982698961937716,43.67693771626297,3.65,62.461899579831936,80.8886365107671,1160]
[104,null,18,3.6,5,0.5456534317785945,23.2,14.550420168067227,11.900343642611684,44.72779159086314,3.65,64.07194607265586,23.13699027800968,340,null,"tнб",-35,"2.04.05-91"]
[203,null,18,3.6,5,0.5456534317785945,23.2,14.550420168067227,11.900343642611684,44.72779159086314,7.25,54.5316705810159,20.767970520635338,310,null,"v",5,"2.04.05-91"]
[204,null,16,1.8,5,0.5370305069268754,23.2,14.550420168067227,11.982698961937716,43.67693771626297,7.25,53.21810323776569,10.379754730849019,150]
[205,"КР",16,3.6,5,0.5370305069268754,23.2,14.550420168067227,11.982698961937716,43.67693771626297,7.25,53.21810323776569,20.759509461698038,300]
[301,null,20,3.6,5,0.5540933825148834,23.2,14.550420168067227,11.819112627986348,45.764299337482434,10.85,45.994598119998855,18.24680637525182,280,{"$nulls":4},0]
[]
[109,null,16,3.6,7,0.13273484327703275,23.2,12.684981684981684,11.982698961937716,8.961127546041032,3,14.186111005488156,31.85290071116826,140]