{"text_format":"2","workbook":"xls","n_sheets":3,"sheets":["Расчет","Свойства воды","Труба Stabi"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":1,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Расчет","index":0,"n_rows":19,"n_cols":11,"rows_kept":19,"cut":false,"hidden":false,"merged":[[8,8,9,8],[8,10,9,10],[14,8,15,8],[14,10,15,10],[8,6,9,6],[14,6,15,6],[14,4,15,4],[14,5,15,5],[8,5,9,5],[8,4,9,4],[18,0,19,6],[14,0,15,0],[14,1,14,2],[8,1,8,2],[8,0,9,0]],"flags":["formulas_cached_only"]}
[{"$nulls":4},"Тепловая нагрузка Q",52000,"Вт","=",44712,"ккал/ч"]
[{"$nulls":4},"Δt",20,"°С"]
[]
[{"$nulls":4},"Расход теплоносителя V :",0.6344444444444444,"л/c","=",2.284,"м3/ч"]
[]
[]
[{"$nulls":4},"Скорость в трубопроводе диаметром  Dy =",37,"мм"]
[]
["Скорость =",2.284,null,"[м3/ч]","W=",0.603,"м/с",null,"Скорость = ","V [м3/ч]","[м/с]"]
[null,"3600 *",0.0010752100858315,"м2",{"$nulls":5},"3,6 ρ S [м2]"]
[{"$nulls":5},"(Рекомендуется 0,5-0,7 м/с)"]
[]
[]
[null,"Площадь сечения :"]
["S  =",2.284,null,"[м3/ч]","=",0.0010574074074074073,"м2",null,"S = ","V    [м3/ч] "," [м2]"]
[null,"3600 *",0.6,"[м/с]",{"$nulls":5},"3600 * Скорость [м/с]"]
[]
[{"$nulls":4},"Рекомендуемый диаметр Dy  =",36.69240964874345,"мм"]
["величина удельной потери давления на трение\nR не более 100…200 Па/м., смотри вкладку \"Труба Stabi\""]

{"sheet":"Свойства воды","index":1,"n_rows":23,"n_cols":5,"rows_kept":23,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
[null,"          СВОЙСТВА ВОДЫ"]
[]
["Температура, С","Плотность, кг/куб.м","Теплоемкость, Дж/(кг*К)","Вязкость, кв.м/с","Тепло-проводность, Вт/(м*К)"]
[5,1000,4202,1.522e-06,0.57]
[10,999.59,4192,1.309e-06,0.58]
[15,999.05,4186,1.14e-06,0.59]
[20,998.23,4182,1.005e-06,0.599]
[25,997.08,4179,8.932e-07,0.607]
[30,995.67,4178,8.005e-07,0.615]
[35,994.05,4178.2,7.232e-07,0.623]
[40,992.24,4179,6.581e-07,0.631]
[45,990.24,4180,6.02e-07,0.638]
[50,988.07,4181,5.536e-07,0.644]
[55,985.73,4183,5.117e-07,0.65]
[60,983.24,4185,4.75e-07,0.655]
[65,980.6,4187,4.422e-07,0.659]
[70,977.81,4190,4.132e-07,0.663]
[75,974.84,4193,3.878e-07,0.667]
[80,971.83,4196,3.653e-07,0.67]
[85,968.66,4200,3.449e-07,0.673]
[90,965.34,4205,3.263e-07,0.675]
[95,961.86,4210,3.095e-07,0.677]
[100,958.38,4216,2.942e-07,0.679]

{"sheet":"Труба Stabi","index":2,"n_rows":48,"n_cols":21,"rows_kept":48,"cut":false,"hidden":false,"merged":[[1,9,1,10],[1,11,1,12],[1,13,1,14],[1,15,1,16],[1,17,1,18],[1,19,1,20],[0,1,0,20],[1,1,1,2],[1,3,1,4],[1,5,1,6],[1,7,1,8]],"flags":["formulas_cached_only"]}
["PN 16","      температура воды = 80 °С  STABI"]
["к = 0.01","16 х 2,3 мм",null,"20 х 2,8 мм",null,"25 х 3,5 мм",null,"32 х 4,4 мм",null,"40 х 5,5 мм",null,"50 х 6,9 мм",null,"63 х 8,6 мм",null,"75 х 10,4 мм",null,"90 х 12,5 мм",null,"110 х 15,2 мм"]
["Q","R","V","R","V","R","V","R","V","R","V","R","V","R","V","R","V","R","V","R","V"]
["л/с","кПа/м","м/с","кПа/м","м/с","кПа/м","м/с","кПа/м","м/с","кПа/м","м/с","кПа/м","м/с","кПа/м","м/с","кПа/м","м/с","кПа/м","м/с","кПа/м","м/с"]
[]
[0.01,0.015,0.1,0.004,0.1]
[0.02,0.061,0.2,0.019,0.1,0.007,0.1]
[0.03,0.117,0.3,0.038,0.2,0.014,0.1,0.004,0.1]
[0.04,0.198,0.4,0.067,0.2,0.023,0.2,0.007,0.1,0.002,0.1]
[0.05,0.297,0.5,0.098,0.3,0.034,0.2,0.01,0.1,0.004,0.1]
[0.06,0.414,0.6,0.134,0.4,0.047,0.2,0.013,0.1,0.005,0.1,0.002,0.1]
[0.07,0.55,0.7,0.175,0.4,0.062,0.3,0.019,0.2,0.007,0.1,0.002,0.1]
[0.08,0.686,0.8,0.221,0.5,0.074,0.3,0.023,0.2,0.008,0.1,0.003,0.1]
[0.09,0.855,0.9,0.272,0.6,0.092,0.4,0.03,0.2,0.01,0.1,0.004,0.1,0.001,0.1]
[0.1,1.04,1,0.328,0.6,0.111,0.4,0.034,0.2,0.011,0.2,0.004,0.1,0.001,0.1]
[0.12,1.462,1.2,0.465,0.7,0.155,0.5,0.048,0.3,0.016,0.2,0.006,0.1,0.002,0.1,0.001,0.1]
[0.14,1.926,1.4,0.612,0.9,0.206,0.6,0.064,0.3,0.021,0.2,0.008,0.1,0.003,0.1,0.001,0.1]
[0.16,2.479,1.6,0.777,1,0.263,0.6,0.082,0.4,0.028,0.2,0.01,0.2,0.003,0.1,0.001,0.1]
[0.18,3.067,1.8,0.976,1.1,0.327,0.7,0.097,0.4,0.034,0.3,0.011,0.2,0.004,0.1,0.002,0.1,0.001,0.1]
[0.2,3.496,2,1.18,1.2,0.397,0.8,0.119,0.5,0.041,0.3,0.013,0.2,0.004,0.1,0.002,0.1,0.001,0.1]
[0.3,8.047,2.9,2.492,1.8,0.828,1.2,0.247,0.7,0.083,0.5,0.027,0.3,0.009,0.2,0.004,0.1,0.002,0.1,0.001,0.1]
[0.4,null,null,4.299,2.5,1.406,1.6,0.419,1,0.139,0.6,0.047,0.4,0.015,0.2,0.006,0.2,0.003,0.1,0.001,0.1]
[0.5,null,null,6.539,3.1,2.129,2,0.631,1.2,0.212,0.8,0.07,0.5,0.023,0.3,0.01,0.2,0.004,0.2,0.002,0.1]
[0.6,{"$nulls":4},3.018,2.4,0.885,1.4,0.293,0.9,0.095,0.6,0.032,0.4,0.014,0.3,0.006,0.2,0.002,0.1]
[0.7,{"$nulls":4},4.03,2.8,1.18,1.7,0.388,1.1,0.127,0.7,0.042,0.4,0.018,0.3,0.007,0.2,0.003,0.1]
[0.8,{"$nulls":4},5.183,3.1,1.53,1.9,0.501,1.2,0.164,0.8,0.053,0.5,0.023,0.3,0.01,0.2,0.004,0.2]
[0.9,{"$nulls":4},6.513,3.5,1.907,2.2,0.621,1.4,0.2,0.9,0.065,0.6,0.028,0.4,0.012,0.3,0.004,0.2]
[1,{"$nulls":6},2.323,2.4,0.761,1.5,0.244,1,0.079,0.6,0.034,0.4,0.014,0.3,0.005,0.2]
[1.2,{"$nulls":6},3.277,2.9,1.062,1.8,0.346,1.2,0.109,0.7,0.048,0.5,0.02,0.4,0.007,0.2]
[1.4,{"$nulls":6},4.389,3.4,1.423,2.1,0.457,1.4,0.148,0.9,0.064,0.6,0.026,0.4,0.01,0.3]
[1.6,{"$nulls":8},1.835,2.5,0.583,1.6,0.188,1,0.08,0.7,0.033,0.5,0.012,0.3]
[1.8,{"$nulls":8},2.281,2.8,0.731,1.7,0.233,1.1,0.1,0.8,0.041,0.5,0.015,0.4]
[2,{"$nulls":8},2.792,3.1,0.888,1.9,0.282,1.2,0.122,0.9,0.05,0.6,0.019,0.4]
[2.2,{"$nulls":8},3.354,3.4,1.067,2.1,0.34,1.3,0.144,1,0.059,0.7,0.022,0.4]
[2.4,{"$nulls":10},1.253,2.3,0.399,1.5,0.17,1,0.069,0.7,0.026,0.5]
[2.6,{"$nulls":10},1.465,2.5,0.462,1.6,0.198,1.1,0.08,0.8,0.03,0.5]
[2.8,{"$nulls":10},1.68,2.7,0.529,1.7,0.225,1.2,0.092,0.8,0.034,0.6]
[3,{"$nulls":10},1.91,2.9,0.607,1.8,0.257,1.3,0.104,0.9,0.039,0.6]
[3.2,{"$nulls":10},2.167,3.1,0.684,2,0.291,1.4,0.118,1,0.044,0.6]
[3.4,{"$nulls":10},2.426,3.3,0.765,2.1,0.324,1.5,0.132,1,0.049,0.7]
[3.6,{"$nulls":10},2.715,3.5,0.85,2.2,0.362,1.6,0.146,1.1,0.054,0.7]
[3.8,{"$nulls":12},0.947,2.3,0.402,1.6,0.164,1.1,0.06,0.8]
[4,{"$nulls":12},1.042,2.4,0.439,1.7,0.181,1.2,0.066,0.8]
[4.2,{"$nulls":12},1.14,2.6,0.483,1.8,0.198,1.3,0.072,0.8]
[4.4,{"$nulls":12},1.244,2.7,0.528,1.9,0.216,1.3,0.078,0.9]
[4.6,{"$nulls":12},1.36,2.8,0.571,2,0.234,1.4,0.085,0.9]
[4.8,{"$nulls":12},1.472,2.9,0.621,2.1,0.253,1.4,0.092,1]
[5,{"$nulls":12},1.589,3.1,0.672,2.2,0.273,1.5,0.099,1]