{"text_format":"2","workbook":"xls","n_sheets":2,"sheets":["Расчет","Справочные данные"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Расчет","index":0,"n_rows":19,"n_cols":3,"rows_kept":19,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
[]
["Тепловая мощность системы, кВт",400]
[]
["Расчетная температура теплоносителя в системе",85]
[null,85,95]
[null,10.8,9.5]
[1,10.8]
[null,85,95]
[null,7.6,6.9]
[2,7.6]
[null,85,95]
[null,0.23,0.21]
[2,0.23]
[null,18.63]
["Объем системы, л",7452]
["Минимальное давление в системе, бар",3]
["Максимальное давление в системе, бар",6]
["Объемное расширение, л",267.52680000000004]
["Объем закрытого бака, л",624.2292]

{"sheet":"Справочные данные","index":1,"n_rows":23,"n_cols":9,"rows_kept":23,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
[]
[null,85,95,105,110,115,130,135,150]
["Радиатор чугунный секционный 140 мм",10.8,9.5,8.9,8.5,8.2,7.2,6.8,6.8]
["Радиатор чугунный секционный 90 мм",14.4,12.9,11.9,11.4,11,9.6,9.2,9.2]
["Ребристая труба чугунная",6,5.6,5.2,5,4.8,4.3,3.6,3.6]
["Гладкая труба D=70-100",35.7,31.6,30.4,29.7,28.6,24.9,21.5,21.5]
["Радиатор стальной панельный",8.1,7.1,6.6,6.4,6.1,5.3,5.1,5.1]
[]
[]
[null,85,95,105,110,115,130,135,150]
["Труба при циркуляции естественной",13.8,13.8,13.8,13.8,13.8,13.8,13.8,13.8]
["Труба при циркуляции искусственной",7.6,6.9,6.4,6,5.6,5.2,4.7,4.7]
[]
[]
[null,85,95,105,110,115,130,135,150]
["Котел чугунный секционный",2.6,2.6,2.6,2.6,2.6,2.6,2.6,2.6]
["Теплообменник скоростной",0.23,0.21,0.19,0.18,0.17,0.15,0.15,0.15]
[]
[]
[]
[]
[]
["Справлочные данные взяты из \"Справочника проектировщика\" Внутренние санитарно-технические устройства\". Часть 1. Отопление. Стр. 87 п.10.6.8"]