{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["гидравлика"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"гидравлика","index":0,"n_rows":19,"n_cols":18,"rows_kept":19,"cut":false,"hidden":false,"merged":[[1,0,3,0],[1,1,3,1],[1,3,1,5],[1,6,1,16],[2,13,2,16],[2,7,3,7],[1,2,3,2],[0,15,0,17],[1,17,3,17],[2,9,3,9],[2,10,3,10],[0,6,0,13],[16,1,16,6],[16,9,16,11],[2,5,3,5],[2,6,3,6],[2,8,3,8],[2,11,3,11],[2,12,3,12],[2,3,3,3],[2,4,3,4]],"flags":["formulas_cached_only"]}
[{"$nulls":6},"Гидравлический  расчет ",{"$nulls":8},"Приложение 3"]
["№        стояка        п/п","№     пред.   уч-ка         ","Тепловая нагрузка, Вт","Характеристика участка",null,null,"Расчетные данные участка",{"$nulls":10},"Потери напора от источника ΣН,м"]
[null,null,null,"Диаметр тр-да        D, м","Длина   тр-да      L, м","Сумма коэф-тов местных сопротивлений    Σξ","Расход сетевой воды     G, т/ч","l","Скорость воды    W, м/с","Удельные потери напора при  К=0,5 мм             R, мм/м","Эвивалентная шероховатость Кэкв, мм","Поправочный коэф-т             к удельным потерям         β","Расчетное значение удельных потерь      Rp, мм/м","Потери напора на уч-ке, мм"]
[{"$nulls":13},"Линейные ΔНл, мм","Местные ΔНм, мм","Всего ΔН,мм","Всего  ΔН,м"]
[1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,16,17,18]
["О","Т.П.",110864,0.05,38,10,3.810123150357995,0.03785068661145514,0.5625639136945121,11.710001109166187,0.7,1.14,13.349401264449453,507.2772480490792,154.68677265186346,661.9640207009427,0.6619640207009427,0.6619640207009427]
[1,2,60864,0.05,1.5,5,2.091746062052506,0.03785068661145514,0.3088458836331252,3.529367076420946,0.7,1.14,4.023478467119879,6.0352177006798176,23.31111660305271,29.346334303732526,0.029346334303732527,0.6913103550046753]
[2,3,45864,0.025,3.5,2.5,1.576232935560859,0.04856042729275657,0.9309218984588363,82.27699500209172,0.7,1.14,93.79577430238456,328.28521005834597,105.89511819221114,434.1803282505571,0.43418032825055713,1.1254906832552325]
[3,4,41701,0.02,8,3.5,1.433160859188544,0.05299029978348444,1.3225369464487375,226.5121202197305,0.7,1.14,258.22381705049276,2065.790536403942,299.221715675648,2365.01225207959,2.3650122520795898,3.4905029353348223]
[4,5,35819,0.02,2,1.5,1.2310109785202863,0.05299029978348444,1.1359907648461027,167.11884290496843,0.7,1.14,190.51548091166399,381.03096182332797,94.61288778576863,475.6438496090966,0.4756438496090966,3.966146784943919]
[5,6,26996,0.02,6,1.5,0.9277861575178997,0.05299029978348444,0.8561714924421506,94.92865880034816,0.7,1.14,108.2186710323969,649.3120261943814,53.74303930430001,703.0550654986814,0.7030550654986815,4.6692018504426]
[6,7,18173,0.02,6,1.5,0.624561336515513,0.05299029978348444,0.5763522200381983,43.01815293675513,0.7,1.14,49.040694347900846,294.24416608740506,24.35435529475679,318.59852138216183,0.3185985213821618,4.987800371824762]
[7,8,15232,0.015,6.5,2.5,0.5234863961813842,0.0596558274221208,0.858807340865566,143.37140737473194,0.7,1.14,163.4434044071944,1062.3821286467637,90.124100341601,1152.5062289883647,1.1525062289883647,6.140306600813127]
[8,9,6409,0.015,11,1.5,0.22026157517899758,0.0596558274221208,0.3613508565918732,25.382198111103015,0.7,1.14,28.935705846657434,318.29276431323177,9.573238393941882,327.86600270717366,0.32786600270717364,6.4681726035203]
[9,10,5229,0.015,6,2.5,0.17970787589498807,0.0596558274221208,0.2948203509313318,16.896080499197215,0.7,1.14,19.261531769084822,115.56919061450893,10.620974447920425,126.19016506242934,0.12619016506242933,6.59436276858273]
[10,11,2083,0.015,20,8,0.07158758949880668,0.0596558274221208,0.11744325702619317,2.681187748419437,0.7,1.14,3.056554033198158,61.13108066396316,5.393312668915025,66.52439333287819,0.06652439333287818,6.660887161915609]
[{"$nulls":9},"Потери напора в сети, кПа "]
["Tп",95,0.49000000000000005,4.9,0.102,48.03921568627452,null,null,1.3321774323831217,13.321774323831217,0.102,130.60563062579627,null,null,null,"ИТОГО",null,13.321774323831217]
["Тохл.",70,"атм","м",null,"кПа",null,null,"атм","м",null,"кПа"]