{"text_format":"2","workbook":"xls","n_sheets":4,"sheets":["Свойства воды","Свойства гликоля","Свойства воздуха","Свойства газов"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Свойства воды","index":0,"n_rows":26,"n_cols":6,"rows_kept":26,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
[]
[null,"             ТЕПЛОФИЗИЧЕСКИЕ СВОЙСТВА ВОДЫ"]
[]
["Температура, С","Плотность, кг/куб.м","Теплоемкость, Дж/(кг*К)","Вязкость, кв.м/с","Тепло-проводность, Вт/(м*К)","Критерий Прандтля"]
[5,1000,4202,1.522e-06,0.57,11.220077192982458]
[10,999.59,4192,1.309e-06,0.58,9.45703137158621]
[15,999.05,4186,1.14e-06,0.59,8.08051959661017]
[20,998.23,4182,1.005e-06,0.599,7.004124957095158]
[25,997.08,4179,8.932e-07,0.607,6.131438824092258]
[30,995.67,4178,8.005e-07,0.615,5.414646118097561]
[35,994.05,4178.2,7.232e-07,0.623,4.821340735589085]
[40,992.24,4179,6.581e-07,0.631,4.324656654161648]
[45,990.24,4180,6.02e-07,0.638,3.905643144827586]
[50,988.07,4181,5.536e-07,0.644,3.551224228124224]
[55,985.73,4183,5.117e-07,0.65,3.245995393081538]
[60,983.24,4185,4.75e-07,0.655,2.9840583435114505]
[65,980.6,4187,4.422e-07,0.659,2.755041679575114]
[70,977.81,4190,4.132e-07,0.663,2.5533789977073904]
[75,974.84,4193,3.878e-07,0.667,2.3765128901589208]
[80,971.83,4196,3.653e-07,0.67,2.223313220602985]
[85,968.66,4200,3.449e-07,0.673,2.084965085884101]
[90,965.34,4205,3.263e-07,0.675,1.9622737905333332]
[95,961.86,4210,3.095e-07,0.677,1.8512537233382569]
[100,958.38,4216,2.942e-07,0.679,1.750698011098674]
[]
["Примечание: температура замерзания 0С."]

{"sheet":"Свойства гликоля","index":1,"n_rows":31,"n_cols":6,"rows_kept":31,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
[]
["                ТЕПЛОФИЗИЧЕСКИЕ СВОЙСТВА 50% РАСТВОРА ЭТИЛЕНГЛИКОЛЯ"]
[]
["Температура, С","Плотность, кг/куб.м","Теплоемкость, Дж/(кг*К)","Вязкость, кв.м/с","Тепло-проводность, Вт/(м*К)","Критерий Прандтля"]
[-20,1078,3125,2.159e-05,0.425,171.13250000000005]
[-15,1076,3149,1.613e-05,0.424,128.90015594339621]
[-10,1074,3172,1.236e-05,0.423,99.5441089361702]
[-5,1071,3195,9.69e-06,0.422,78.57269680094787]
[0,1069,3219,7.37e-06,0.421,60.239876650831356]
[5,1067,3242,6.06e-06,0.42,49.911516285714285]
[10,1065,3265,5.05e-06,0.419,41.909275059665866]
[15,1062,3287,4.25e-06,0.418,35.49252272727273]
[20,1060,3310,3.62e-06,0.417,30.458350119904075]
[25,1057,3333,3.11e-06,0.416,26.337670456730766]
[30,1055,3355,2.69e-06,0.416,22.88779387019231]
[35,1052,3377,2.35e-06,0.415,20.117155180722893]
[40,1049,3399,2.07e-06,0.414,17.827755000000003]
[45,1046,3421,1.83e-06,0.413,15.855713753026635]
[50,1043,3443,1.63e-06,0.412,14.207305509708739]
[55,1040,3464,1.46e-06,0.411,12.797415085158152]
[60,1037,3485,1.32e-06,0.41,11.635140000000003]
[65,1034,3507,1.19e-06,0.409,10.550668019559902]
[70,1030,3527,1.09e-06,0.408,9.705301225490196]
[75,1027,3548,9.9e-07,0.407,8.86328756756757]
[80,1023,3569,9.1e-07,0.407,8.163364054054055]
[85,1020,3589,8.4e-07,0.406,7.574027586206896]
[90,1016,3609,7.8e-07,0.405,7.061877333333333]
[95,1012,3629,7.2e-07,0.404,6.5451350495049505]
[100,1009,3648,6.7e-07,0.403,6.119497369727048]
[]
["Примечание: температура замерзания минус 38С."]

{"sheet":"Свойства воздуха","index":2,"n_rows":37,"n_cols":6,"rows_kept":37,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
[]
[null,"           ТЕПЛОФИЗИЧЕСКИЕ СВОЙСТВА ВОЗДУХА"]
[]
["Температура, С","Плотность, кг/куб.м","Теплоемкость, Дж/(кг*К)","Вязкость, кв.м/с","Тепло-проводность, Вт/(м*К)","Критерий Прандтля"]
[-50,1.584,1013,9.23e-06,0.0204,0.7259992235294116]
[-40,1.515,1013,1.004e-05,0.0212,0.7268083867924529]
[-30,1.453,1013,1.08e-05,0.022,0.722563690909091]
[-20,1.395,1009,1.179e-05,0.0228,0.7278540986842106]
[-10,1.342,1009,1.243e-05,0.0236,0.7131859974576271]
[0,1.293,1005,1.328e-05,0.0244,0.7072498032786884]
[10,1.247,1005,1.416e-05,0.0251,0.7070042868525896]
[20,1.205,1005,1.506e-05,0.0259,0.7041712934362934]
[30,1.165,1005,1.6e-05,0.0267,0.70161797752809]
[40,1.128,1005,1.696e-05,0.0276,0.6966135652173913]
[50,1.093,1005,1.795e-05,0.0283,0.6967295671378092]
[60,1.06,1005,1.897e-05,0.029,0.6968531379310345]
[70,1.029,1009,2.002e-05,0.0296,0.7022292304054054]
[80,1,1009,2.109e-05,0.0305,0.6976986885245902]
[90,0.972,1009,2.21e-05,0.0313,0.6924770223642173]
[100,0.946,1009,2.313e-05,0.0321,0.6877853214953272]
[120,0.898,1009,2.545e-05,0.0334,0.6904127814371258]
[140,0.854,1013,2.78e-05,0.0349,0.6891070372492838]
[160,0.815,1017,3.009e-05,0.0364,0.6851716195054945]
[180,0.779,1022,3.249e-05,0.0378,0.6842995666666667]
[200,0.746,1026,3.485e-05,0.0393,0.6787290229007633]
[250,0.674,1038,4.061e-05,0.0427,0.6653686960187354]
[300,0.615,1047,4.833e-05,0.046,0.6765201880434782]
[350,0.566,1059,5.546e-05,0.0491,0.6770344448065172]
[400,0.524,1068,6.309e-05,0.0521,0.677681053358925]
[500,0.456,1093,7.938e-05,0.0574,0.6892617951219514]
[600,0.404,1114,9.689e-05,0.0622,0.7010599009646303]
[700,0.362,1135,0.0001154,0.0671,0.7066229210134128]
[800,0.329,1156,0.0001348,0.0718,0.7140344735376044]
[900,0.301,1172,0.0001551,0.0763,0.7171027155963302]
[1000,0.277,1185,0.0001771,0.0807,0.7203493122676581]
[1100,0.257,1197,0.0001993,0.085,0.7212995258823529]
[1200,0.239,1210,0.0002337,0.0915,0.7386197049180327]

{"sheet":"Свойства газов","index":3,"n_rows":17,"n_cols":6,"rows_kept":17,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
[]
["                                ТЕПЛОФИЗИЧЕСКИЕ СВОЙСТВА ДЫМОВЫХ ГАЗОВ"]
[]
["Температура, С","Плотность, кг/куб.м","Теплоемкость, Дж/(кг*К)","Вязкость, кв.м/с","Тепло-проводность, Вт/(м*К)","Критерий Прандтля"]
[0,1.295,1042,1.22e-05,0.0228,0.7220420175438595]
[100,0.95,1068,2.154e-05,0.0313,0.6982263258785941]
[200,0.748,1097,3.28e-05,0.0401,0.6711779750623441]
[300,0.617,1122,4.581e-05,0.0484,0.655228759090909]
[400,0.5252,1151,6.038e-05,0.057,0.6403512978245613]
[500,0.457,1185,7.63e-05,0.0656,0.6298762728658537]
[600,0.405,1214,9.361e-05,0.0742,0.6202861010781673]
[700,0.363,1239,0.0001121,0.0827,0.6096464292623942]
[800,0.33,1264,0.0001318,0.0915,0.6008351475409837]
[900,0.301,1290,0.0001525,0.1,0.5921422499999999]
[1000,0.275,1306,0.0001743,0.109,0.5743105045871559]
[1100,0.257,1323,0.0001971,0.1175,0.5703503668085106]
[1200,0.24,1340,0.000221,0.1262,0.5631822503961965]