{"text_format":"2","workbook":"xls","n_sheets":3,"sheets":["Лист1","Лист2","Лист3"],"not_rendered":{"charts":0,"images":1,"macros":1,"external_links":1,"defined_names":1,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Лист1","index":0,"n_rows":803,"n_cols":25,"rows_kept":803,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["Tпод",85]
["Tобр",65]
["Гидравлический расчет системы отпления1(трубы Обыкновенные температура 85-65 С)"]
["N участка","Q, Вт","G, кг/ч","l, м","d, мм","dвн, мм","F, м2","v, м/с","R, Па/м","Rl, Па","Сум s.","Рд, Па","Z, Па","Р, Па","Сум Р, Па","Характеристика местный сопротивлений ",null,"Кинематическая вязкость, м2/сек","Re","kэ","d/kэ","Reпр1","Reпр2","Плотность воды, кг/м3","l "]
["1",89085,4414.207494626224,16.6,65,70.4,0.0038924441600000003,0.32475520298959887,19.44262805763094,322.74762575667364,1.5,51.15098180637555,76.72647270956332,399.47409846623697,null,"задвижка-0,5, отводы -2 шт-1.",null,4.79e-07,47730.201023941045,0.2,352,3445.6615708915406,52800,983.25,0.026398632630996788]
["2",83390,4132.0173202770475,5.67,65,70.4,0.0038924441600000003,0.30399434671720993,17.228646131463925,97.68642356540046,1,44.82009297547127,44.82009297547127,142.50651654087173,null,"тройник на проход - 1 шт;",null,4.79e-07,44678.91859893858,0.2,352,159933.48406385997,52800,983.25,0.026696777140619625]
["3",75558,3743.9376985908757,4.6,50,44.4,0.0015482568600000003,0.6924865860249801,156.07507595998112,717.9453494159131,1.5,232.57577083489812,348.8636562523472,1066.8090056682604,null,"тройник на проход - 1 шт; внезапное сужение-0,5",null,4.79e-07,64188.73574010255,0.2,221.99999999999997,95219.52223366837,33299.99999999999,983.25,0.029394077523160436]
["4",66283,3284.356685932649,6.09,50,44.4,0.0015482568600000003,0.6074815159413135,120.10938980432506,731.4661839083396,1,178.9813892220228,178.9813892220228,910.4475731303625,null,"тройник на проход - 1 шт;",null,4.79e-07,56309.3513732658,0.2,221.99999999999997,95219.52223366837,33299.99999999999,983.25,0.029394077523160436]
["5",57774,2862.7313666109385,5.75,40,41,0.0013202153750000003,0.6209570688238755,139.1872629223388,800.326761803448,1.5,187.01002544133453,280.5150381620018,1080.8417999654498,null,"тройник на проход - 1 шт; внезапное сужение-0,5",null,4.79e-07,53150.81382417306,0.2,205,87056.65888015363,30750,983.25,0.0301041411253084]
["6",50023,2478.665336517793,6.56,40,41,0.0013202153750000003,0.5376490368293129,104.34558739732964,684.5070533264824,1,140.1972460996916,140.1972460996916,824.704299426174,null,"тройник на проход - 1 шт;",null,4.79e-07,46020.063695202145,0.2,205,87056.65888015363,30750,983.25,0.0301041411253084]
["7",41455,2054.116536899928,5.9,40,41,0.0013202153750000003,0.44555985890008926,71.66192323733326,422.8053471002662,1,96.28394011358772,96.28394011358772,519.0892872138539,null,"тройник на проход - 1 шт;",null,4.79e-07,38137.69147161516,0.2,205,87056.65888015363,30750,983.25,0.0301041411253084]
["8",33369,1653.4510847862427,4.6,32,35.9,0.00101219915375,0.46779022929297176,93.93611698860947,432.10613814760353,1.5,106.13143383165598,159.197150747484,591.3032888950875,null,"тройник на проход - 1 шт; внезапное сужение-0,5",null,4.79e-07,35059.852258074505,0.2,179.49999999999997,74972.39960709562,26924.999999999996,983.25,0.03134662584008899]
["9",25838,1280.2861676618102,6.6,32,35.9,0.00101219915375,0.3622153479118884,56.320176585953874,371.71316546729554,1,63.631979757521236,63.631979757521236,435.34514522481675,null,"тройник на проход - 1 шт;",null,4.79e-07,27147.246325755314,0.2,179.49999999999997,74972.39960709562,26924.999999999996,983.25,0.03134662584008899]
["10",16640,824.5205445426318,3.47,32,35.9,0.00101219915375,0.23327128219110702,25.383569363795107,88.08098569236903,1,26.391513181115297,26.391513181115297,114.47249887348433,null,"тройник на проход - 1 шт;",null,4.79e-07,17483.171253989025,0.2,179.49999999999997,74972.39960709562,26924.999999999996,983.25,0.034063606520169036]
["11",11444,567.0560764270361,4.75,25,27.1,0.0005767872537500001,0.2815374152365314,50.308947586638254,238.9675010365317,1.5,38.44270834636255,57.664062519543826,296.63156355607555,null,"тройник на противоток - 1 шт; внезапное сужение-0,5",null,4.79e-07,15928.317229457207,0.2,135.5,54639.98971373989,20325,984.25,0.035845350038145145]
["12","5901",292.3975801289706,21.75,25,27.1,0.0005767872537500001,0.1451723424773481,13.376446700909371,290.9377157447788,45.4,10.221379374874816,464.05062361931664,754.9883393640955,7136.613416324769,"отвод-12 шт-12, воздусборник - 1,5, кран трехходовой при проходе -6 шт, 26,4, задвижка-0,5,радиатор-6 шт, 4,5.внезапное сужение-0,5",null,4.79e-07,8213.299543081699,0.2,135.5,54639.98971373989,20325,985.25,0.0401174856179561]
["13","5901",292.3975801289706,5.75,25,27.1,0.0005767872537500001,0.1451723424773481,13.376446700909371,76.91456853022888,0.5,10.221379374874816,5.110689687437408,82.02525821766629,null," отводы -1 шт-0,5.",null,4.79e-07,8213.299543081699,0.2,135.5,54639.98971373989,20325,986.25,0.0401174856179561]
["14",11444,567.0560764270361,4.75,25,27.1,0.0005767872537500001,0.2815374152365314,50.308947586638254,238.9675010365317,2,38.44270834636255,76.8854166927251,315.8529177292568,null,"тройник на проход - 1 шт; внезапное рассширение-1",null,4.79e-07,15928.317229457207,0.2,135.5,54639.98971373989,20325,987.25,0.035845350038145145]
["15",16640,824.5205445426318,3.47,32,35.9,0.00101219915375,0.23327128219110702,24.30183680511558,84.32737371375107,2,26.391513181115297,52.78302636223059,137.11040007598166,null,"тройник на проход - 1 шт; внезапное рассширение-1",null,4.79e-07,17483.171253989025,0.2,179.49999999999997,74972.39960709562,26924.999999999996,988.25,0.034063606520169036]
["16",25838,1280.2861676618102,6.6,32,35.9,0.00101219915375,0.3622153479118884,58.59360837105097,386.7178152489364,1,63.631979757521236,63.631979757521236,450.3497950064576,null,"тройник на проход - 1 шт;",null,4.79e-07,27147.246325755314,0.2,179.49999999999997,74972.39960709562,26924.999999999996,989.25,0.03134662584008899]
["17",33369,1653.4510847862427,4.6,32,35.9,0.00101219915375,0.46779022929297176,97.72796152951888,449.5486230357868,1,106.13143383165598,106.13143383165598,555.6800568674428,null,"тройник на проход - 1 шт;",null,4.79e-07,35059.852258074505,0.2,179.49999999999997,74972.39960709562,26924.999999999996,990.25,0.03134662584008899]
["18",41455,2054.116536899928,5.9,40,41,0.0013202153750000003,0.44555985890008926,75.09601686959455,443.06649953060787,2,96.28394011358772,192.56788022717544,635.6343797577833,null,"тройник на проход - 1 шт; внезапное рассширение-1",null,4.79e-07,38137.69147161516,0.2,205,87056.65888015363,30750,991.25,0.0301041411253084]
["19",50023,2478.665336517793,6.56,40,41,0.0013202153750000003,0.5376490368293129,109.34590696800305,717.3091497101,1,140.1972460996916,140.1972460996916,857.5063958097916,null,"тройник на проход - 1 шт;",null,4.79e-07,46020.063695202145,0.2,205,87056.65888015363,30750,992.25,0.0301041411253084]
["20",57774,2862.7313666109385,5.75,40,41,0.0013202153750000003,0.6209570688238755,145.85722197033252,838.679026329412,1,187.01002544133453,187.01002544133453,1025.6890517707466,null,"тройник на проход - 1 шт;",null,4.79e-07,53150.81382417306,0.2,205,87056.65888015363,30750,993.25,0.0301041411253084]
["21",66283,3284.356685932649,6.09,50,44.4,0.0015482568600000003,0.6074815159413135,126.36361197202626,769.5543969096399,2,178.9813892220228,357.9627784440456,1127.5171753536856,null,"тройник на проход - 1 шт; внезапное рассширение-1",null,4.79e-07,56309.3513732658,0.2,221.99999999999997,95219.52223366837,33299.99999999999,994.25,0.029394077523160436]
["22",75558,3743.9376985908757,4.6,50,44.4,0.0015482568600000003,0.6924865860249801,164.20206920742672,755.3295183541628,1,232.57577083489812,232.57577083489812,987.9052891890609,null,"тройник на проход - 1 шт;",null,4.79e-07,64188.73574010255,0.2,221.99999999999997,95219.52223366837,33299.99999999999,995.25,0.029394077523160436]
["23",83390,4132.0173202770475,5.67,65,70.4,0.0038924441600000003,0.30399434671720993,17.784833282816482,100.84000471356946,2,44.82009297547127,89.64018595094254,190.480190664512,null,"тройник на проход - 1 шт; внезапное рассширение-1",null,4.79e-07,44678.91859893858,0.2,352,159933.48406385997,52800,996.25,0.026696777140619625]
["24",89085,4414.207494626224,2,65,70.4,0.0038924441600000003,0.32475520298959887,21.21955024224435,42.4391004844887,1,51.15098180637555,51.15098180637555,93.59008229086425,6459.340992733249,"задвижка-0,5, отводы -1шт-0,5.",null,4.79e-07,47730.201023941045,0.2,352,159933.48406385997,52800,999.25,0.026398632630996788]
[{"$nulls":13},"Невязка %",9.490109441016966,null,null,4.79e-07,{"$error":"#VALUE!"},0.2,0,0,0,1018.25,{"$error":"#VALUE!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1019.25,{"$error":"#NUM!"}]
["12","5543",274.6584962980655,16.1,20,21.2,0.00035297894000000003,0.2228281263017796,42.83559448480273,689.6530712053241,38.75,24.08140132751349,933.1543014411477,1622.8073726464718,7547.159789356816,"отвод-12 шт-12,  кран трехходовой при проходе -5шт, 22, задвижка-0,5*2=1,радиатор-5 шт, 3,75",null,4.79e-07,9862.121665130955,0.2,105.99999999999999,41452.23964306845,15899.999999999998,985.25,0.04010106681453186]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1021.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1022.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1023.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1024.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1025.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1026.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1027.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1028.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1029.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1030.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1031.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1032.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1033.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1034.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1035.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1036.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1037.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1038.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1039.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1040.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1041.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1042.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1043.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1044.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1045.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1046.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1047.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1048.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1049.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1050.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1051.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1052.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1053.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1054.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1055.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1056.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1057.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1058.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1059.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1060.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1061.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1062.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1063.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1064.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1065.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1066.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1067.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1068.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1069.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1070.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1071.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1072.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1073.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1074.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1075.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1076.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1077.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1078.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1079.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1080.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1081.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1082.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1083.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1084.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1085.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1086.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1087.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1088.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1089.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1090.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1091.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1092.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1093.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1094.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1095.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1096.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1097.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1098.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1099.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1100.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1101.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1102.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1103.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1104.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1105.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1106.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1107.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1108.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1109.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1110.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1111.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1112.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1113.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1114.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1115.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1116.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1117.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1118.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1119.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1120.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1121.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1122.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1123.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1124.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1125.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1126.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1127.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1128.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1129.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1130.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1131.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1132.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1133.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1134.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1135.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1136.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1137.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1138.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1139.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1140.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1141.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1142.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1143.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1144.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1145.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1146.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1147.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1148.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1149.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1150.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1151.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1152.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1153.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1154.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1155.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1156.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1157.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1158.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1159.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1160.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1161.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1162.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1163.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1164.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1165.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1166.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1167.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1168.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1169.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1170.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1171.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1172.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1173.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1174.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1175.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1176.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1177.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1178.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1179.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1180.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1181.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1182.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1183.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1184.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1185.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1186.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1187.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1188.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1189.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1190.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1191.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1192.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1193.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1194.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1195.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1196.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1197.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1198.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1199.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1200.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1201.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1202.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1203.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1204.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1205.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1206.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1207.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1208.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1209.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1210.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1211.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1212.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1213.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1214.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1215.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1216.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1217.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1218.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1219.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1220.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1221.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1222.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1223.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1224.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1225.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1226.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1227.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1228.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1229.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1230.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1231.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1232.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1233.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1234.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1235.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1236.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1237.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1238.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1239.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1240.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1241.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1242.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1243.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1244.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1245.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1246.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1247.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1248.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1249.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1250.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1251.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1252.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1253.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1254.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1255.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1256.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1257.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1258.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1259.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1260.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1261.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1262.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1263.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1264.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1265.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1266.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1267.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1268.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1269.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1270.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1271.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1272.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1273.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1274.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1275.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1276.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1277.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1278.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1279.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1280.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1281.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1282.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1283.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1284.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1285.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1286.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1287.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1288.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1289.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1290.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1291.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1292.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1293.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1294.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1295.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1296.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1297.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1298.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1299.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1300.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1301.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1302.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1303.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1304.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1305.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1306.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1307.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1308.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1309.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1310.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1311.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1312.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1313.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1314.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1315.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1316.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1317.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1318.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1319.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1320.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1321.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1322.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1323.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1324.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1325.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1326.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1327.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1328.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1329.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1330.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1331.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1332.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1333.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1334.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1335.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1336.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1337.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1338.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1339.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1340.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1341.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1342.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1343.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1344.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1345.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1346.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1347.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1348.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1349.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1350.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1351.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1352.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1353.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1354.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1355.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1356.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1357.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1358.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1359.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1360.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1361.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1362.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1363.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1364.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1365.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1366.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1367.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1368.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1369.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1370.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1371.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1372.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1373.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1374.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1375.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1376.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1377.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1378.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1379.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1380.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1381.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1382.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1383.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1384.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1385.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1386.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1387.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1388.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1389.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1390.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1391.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1392.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1393.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1394.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1395.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1396.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1397.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1398.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1399.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1400.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1401.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1402.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1403.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1404.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1405.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1406.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1407.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1408.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1409.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1410.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1411.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1412.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1413.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1414.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1415.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1416.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1417.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1418.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1419.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1420.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1421.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1422.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1423.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1424.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1425.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1426.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1427.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1428.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1429.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1430.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1431.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1432.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1433.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1434.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1435.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1436.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1437.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1438.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1439.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1440.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1441.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1442.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1443.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1444.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1445.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1446.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1447.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1448.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1449.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1450.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1451.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1452.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1453.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1454.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1455.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1456.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1457.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1458.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1459.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1460.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1461.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1462.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1463.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1464.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1465.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1466.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1467.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1468.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1469.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1470.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1471.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1472.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1473.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1474.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1475.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1476.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1477.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1478.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1479.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1480.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1481.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1482.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1483.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1484.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1485.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1486.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1487.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1488.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1489.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1490.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1491.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1492.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1493.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1494.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1495.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1496.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1497.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1498.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1499.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1500.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1501.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1502.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1503.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1504.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1505.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1506.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1507.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1508.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1509.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1510.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1511.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1512.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1513.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1514.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1515.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1516.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1517.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1518.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1519.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1520.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1521.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1522.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1523.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1524.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1525.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1526.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1527.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1528.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1529.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1530.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1531.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1532.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1533.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1534.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1535.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1536.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1537.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1538.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1539.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1540.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1541.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1542.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1543.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1544.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1545.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1546.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1547.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1548.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1549.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1550.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1551.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1552.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1553.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1554.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1555.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1556.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1557.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1558.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1559.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1560.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1561.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1562.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1563.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1564.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1565.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1566.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1567.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1568.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1569.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1570.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1571.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1572.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1573.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1574.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1575.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1576.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1577.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1578.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1579.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1580.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1581.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1582.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1583.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1584.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1585.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1586.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1587.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1588.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1589.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1590.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1591.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1592.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1593.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1594.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1595.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1596.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1597.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1598.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1599.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1600.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1601.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1602.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1603.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1604.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1605.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1606.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1607.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1608.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1609.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1610.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1611.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1612.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1613.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1614.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1615.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1616.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1617.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1618.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1619.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1620.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1621.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1622.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1623.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1624.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1625.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1626.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1627.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1628.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1629.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1630.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1631.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1632.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1633.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1634.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1635.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1636.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1637.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1638.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1639.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1640.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1641.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1642.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1643.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1644.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1645.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1646.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1647.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1648.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1649.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1650.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1651.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1652.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1653.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1654.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1655.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1656.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1657.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1658.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1659.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1660.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1661.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1662.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1663.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1664.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1665.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1666.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1667.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1668.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1669.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1670.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1671.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1672.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1673.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1674.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1675.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1676.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1677.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1678.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1679.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1680.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1681.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1682.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1683.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1684.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1685.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1686.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1687.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1688.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1689.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1690.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1691.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1692.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1693.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1694.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1695.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1696.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1697.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1698.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1699.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1700.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1701.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1702.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1703.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1704.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1705.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1706.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1707.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1708.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1709.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1710.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1711.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1712.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1713.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1714.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1715.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1716.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1717.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1718.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1719.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1720.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1721.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1722.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1723.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1724.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1725.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1726.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1727.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1728.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1729.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1730.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1731.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1732.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1733.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1734.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1735.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1736.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1737.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1738.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1739.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1740.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1741.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1742.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1743.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1744.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1745.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1746.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1747.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1748.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1749.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1750.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1751.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1752.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1753.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1754.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1755.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1756.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1757.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1758.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1759.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1760.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1761.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1762.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1763.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1764.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1765.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1766.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1767.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1768.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1769.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1770.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1771.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1772.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1773.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1774.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1775.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1776.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1777.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1778.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1779.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1780.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1781.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1782.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1783.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1784.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1785.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1786.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1787.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1788.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1789.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1790.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1791.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1792.25,{"$error":"#NUM!"}]

{"sheet":"Лист2","index":1,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}

{"sheet":"Лист3","index":2,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}