{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["емкость"],"not_rendered":{"charts":0,"images":1,"macros":0,"external_links":2,"defined_names":4,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"емкость","index":0,"n_rows":9,"n_cols":11,"rows_kept":9,"cut":false,"hidden":false,"merged":[[1,0,1,6]],"flags":["formulas_cached_only"]}
[]
["Таблица расчета удельных потерь  трубопроводов  и емкостей Вт/м"]
["№п/п","Dтрубы","Толщ.изоляции",null,"Tвнутри","Tокр.среды","Q"]
[null,"м","м","изоляции"," трубы",null,"теплопотери"]
[null,null,null,"Вт/м*С","гр.Цельсия","гр.Цельсия","Вт/м"]
[1,2,3,4,5,6,9,null,null,null,"ln"]
["Емкость",2,0.05,0.032,10,-50,248,null,0.24278545068387763,1.05,0.04879016416943205]
["Труба 110",0.11,0.05,0.032,10,-50,24,null,3.217690908265588,1.9090909090909092,0.6466271649250525]
["Труба 50",0.05,0.05,0.032,10,-50,14.399999999999999,null,5.466820703961534,3.0000000000000004,1.0986122886681098]