{"text_format":"2","workbook":"xls","n_sheets":3,"sheets":["Лист1","Лист2","Лист3"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":0,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Лист1","index":0,"n_rows":78,"n_cols":15,"rows_kept":78,"cut":false,"hidden":false,"merged":[[5,8,7,8],[5,9,5,14],[4,0,4,6],[5,0,7,0],[5,1,5,6]],"flags":["formulas_cached_only"]}
[]
[]
["Гидравлические характеристики металлопластиковых труб VALPEX"]
[]
["Температура воды 20  С."]
["Расход л/с",{"$nulls":7},"Расход л/с"]
[null,"Ф16","Ф20","ф26","ф32","ф40","ф50",null,null,"Ф16","Ф20","ф26","ф32","ф40","ф50"]
[null,"Потери давления на трение, Па/м","Потери давления на трение, Па/м","Потери давления на трение, Па/м","Потери давления на трение, Па/м","Потери давления на трение, Па/м","Потери давления на трение, Па/м",null,null,"Потери давления на трение, Па/м","Потери давления на трение, Па/м","Потери давления на трение, Па/м","Потери давления на трение, Па/м","Потери давления на трение, Па/м","Потери давления на трение, Па/м"]
[0.01,24.16,7.72,3.17,1.12,0.44,0.16,null,0.71,null,null,2806.55,790.4,261.1,81.31]
[0.02,57.33,18.4,7.56,2.66,0.98,0.37,null,0.72,null,null,2886.55,813,268.06,83.54]
[0.03,122.67,31.86,13.11,4.62,1.74,0.68,null,0.73,null,null,2967.68,835.93,264.72,85.81]
[0.04,203.27,51.88,19.72,6.8,2.67,1.02,null,0.74,null,null,2911.3,857.94,272.21,88.1]
[0.05,300.64,77.36,26.5,9.67,3.66,1.4,null,0.75,null,null,2990.89,881.49,279.17,90.76]
[0.06,422.17,105.97,36.41,12.75,4.89,1.87,null,0.76,null,null,3069.01,905.36,286.87,93.12]
[0.07,541.82,139.77,48.4,13.71,6.3,2.44,null,0.77,null,null,3150.71,929.54,294.66,95.51]
[0.08,687.98,177.88,61.66,17.51,5.75,3,null,0.78,null,null,3233.49,954.04,301.9,97.93]
[0.09,843.28,212.86,74,21.64,6.84,3.61,null,0.79,null,null,3317.34,978.86,309.9,96.86]
[0.1,1009.82,263.02,90.85,25.78,8.28,4.31,null,0.8,null,null,3402.26,1004.01,318,99.25]
[0.11,1181.26,308,106.99,30.43,9.82,3.11,null,0.81,null,null,3488.25,983.42,326.21,101.67]
[0.12,1407.24,355.76,123.81,35.3,11.26,3.69,null,0.82,null,null,3572.58,1008.06,333.82,104.11]
[0.13,1595.11,404.79,141.14,41.48,13.28,4.2,null,0.83,null,null,3660.69,1033,342.23,106.59]
[0.14,1848.57,469.77,163.81,46.83,15.05,4.73,null,0.84,null,null,3749.87,1058.25,350.74,109.46]
[0.15,2050.68,520.78,182.45,52.27,16.67,5.41,null,0.85,null,null,3840.12,1083.81,358.63,112]
[0.16,2331.68,592.93,207.7,59.52,19.04,6.08,null,0.86,null,null,3931.45,1109.67,352.04,114.57]
[0.17,2540.14,647.44,226.41,64.87,20.96,6.65,null,0.87,null,null,4023.84,1134.45,360.49,117.16]
[0.18,2846.08,726.23,253.99,72.8,23.57,7.43,null,0.88,null,null,4117.32,1160.91,368.32,119.79]
[0.19,3173.2,807.83,274.02,78.73,25.34,8.03,null,0.89,null,null,4208.89,1187.67,376.96,122.83]
[0.2,3383.97,864.7,303.77,87.3,28.16,8.87,null,0.9,null,null,4099.5,1214.73,385.7,125.52]
[0.21,3733.04,953.78,323.89,93.32,30.2,9.61,null,0.91,null,null,4191.56,1242.1,393.8,128.23]
[0.22,4095.03,1047.24,355.62,102.49,32.96,10.51,null,0.92,null,null,4284.64,1269.77,402.73,130.98]
[0.23,4305.92,1104.16,387.77,111.57,36.11,11.46,null,0.93,null,null,4378.74,1297.75,411.77,128.79]
[0.24,4686.38,1200.69,407.84,117.65,38.21,12.09,null,0.94,null,null,4473.86,1324.54,420.9,131.49]
[0.25,5087.54,1303.36,442.72,127.75,41.26,13.24,null,0.95,null,null,4566.99,1353.11,429.36,134.21]
[0.26,5500.39,1358,479.04,138.27,44.73,14.28,null,0.96,null,null,4664.12,1381.99,438.68,136.96]
[0.27,5696.93,1464.98,516.78,149.2,46.82,14.91,null,0.97,null,null,null,1347.03,448.11,139.75]
[0.28,6124.36,1573.75,536.1,155.19,50.44,16,null,0.98,null,null,null,1375.18,456.84,142.96]
[0.29,6567.25,1688.75,575.25,165.95,53.88,17.13,null,0.99,null,null,null,1403.62,466.46,145.8]
[0.3,7030.9,1738.28,614.5,177.71,57.76,17.91,null,1,null,null,null,1430.83,476.17,148.67]
[0.31,7504.88,1856.65,656.37,189.86,59.79,19.08,null,1.1,null,null,null,1732.3,551.12,172.31]
[0.32,7666.64,1976.45,699.62,195.43,63.46,20.29,null,1.2,null,null,null,1962.62,655.88,205.45]
[0.33,8150.68,2102.54,716.68,207.94,67.6,21.54,null,1.3,null,null,null,2304.45,734.76,230.51]
[0.34,8655.28,2232.54,760.99,220.84,71.87,22.29,null,1.4,null,null,null,2671.68,852.14,267.21]
[0.35,null,2366.44,806.63,234.13,73.37,23.58,null,1.5,null,null,null,2914.81,931.64,306.63]
[0.36,null,2401.38,852.1,238.25,77.74,24.9,null,1.6,null,null,null,3315.38,1060,332.9]
[0.37,null,2537.33,900.35,251.79,82.23,26.26,null,1.7,{"$nulls":4},1196.64,376.31]
[0.38,null,2677.03,913.4,265.7,86.85,27.66,null,1.8,{"$nulls":4},1341.56,421.73]
[0.39,null,2820.47,962.35,279.99,91.2,28.35,null,1.9,{"$nulls":4},1420.03,447.37]
[0.4,null,2964.67,1012.58,294.65,92.75,29.77,null,2,{"$nulls":4},1573.44,495.56]
[0.41,null,3115.52,1064.08,309.69,97.57,31.23,null,2.1,{"$nulls":4},1734.72,546.93]
[0.42,null,3133.86,1116.87,312.27,102.09,32.73,null,2.2,{"$nulls":4},1903.86,600.08]
[0.43,null,3285.6,1169.22,327.45,107.14,34.48,null,2.3,{"$nulls":4},1969.89,622.91]
[0.44,null,3437.78,1175.54,343,112.31,34.85,null,2.4,{"$nulls":4},2144.98,678.08]
[0.45,null,3596.62,1229.85,358.9,117.16,36.4,null,2.5,{"$nulls":4},2327.51,735.59]
[0.46,null,3759.05,1285.39,375.16,118.19,37.98,null,2.6,{"$nulls":4},2517.5,796.3]
[0.47,null,3925.07,1342.16,391.78,123.52,39.6,null,2.7,{"$nulls":5},858.52]
[0.48,null,4094.67,1400.15,408.77,128.52,41.49,null,2.8,{"$nulls":5},923.09]
[0.49,null,4264.36,1459.37,408.84,134.07,43.19,null,2.9,{"$nulls":5},937.9]
[0.5,null,4247.98,1517.91,425.84,139.75,44.91,null,3,{"$nulls":5},1003.5]
[0.51,null,4420.43,1579.55,443.19,145.54,45.06,null,3.1,{"$nulls":5},1072.29]
[0.52,null,4596.32,1573.97,460.89,150.95,47.04,null,3.2,{"$nulls":5},1142.36]
[0.53,null,4772.02,1635.39,478.93,151.15,48.81,null,3.3,{"$nulls":5},1214.65]
[0.54,null,4954.69,1697.98,497.33,157.06,50.61,null,3.4,{"$nulls":5},1289.15]
[0.55,null,5140.81,1761.75,515.07,162.58,52.44,null,3.5,{"$nulls":5},1366.96]
[0.56,null,5330.35,1824.65,534.13,168.7,54.31,null,3.6,{"$nulls":5},1365.61]
[0.57,null,5519.43,1890.73,531.4,174.94,56.48,null,3.7,{"$nulls":5},1442.29]
[0.58,null,5715.76,1957.99,550.37,180.76,56.33,null,3.8,{"$nulls":5},1521.06]
[0.59,null,5915.53,2026.42,569.67,187.21,58.23,null,3.9,{"$nulls":5},1601.93]
[0.6,null,5840.6,2096.03,589.31,193.78,60.15,null,4,{"$nulls":5},1686.06]
[0.61,null,6033.86,2166.82,609.27,200.46,62.4,null,4.1,{"$nulls":5},1771.15]
[0.62,null,null,2141.44,628.5,198.74,64.39,null,4.2,{"$nulls":5},1858.33]
[0.63,null,null,2209.19,649.11,205.37,66.42]
[0.64,null,null,2280.24,670.06,212.11,68.48]
[0.65,null,null,2352.41,691.34,218.39,70.57]
[0.66,null,null,2425.7,712.95,225.34,73]
[0.67,null,null,2500.12,734.89,232.4,75.16]
[0.68,null,null,2575.66,724.49,238.97,74.48]
[0.69,null,null,2649.91,746.14,246.24,76.62]
[0.7,null,null,2727.67,768.11,253.61,79.11]

{"sheet":"Лист2","index":1,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}

{"sheet":"Лист3","index":2,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}