{"text_format":"2","workbook":"xls","n_sheets":4,"sheets":["Лист3","Лист2","Лист1","Лист4"],"not_rendered":{"charts":0,"images":1,"macros":1,"external_links":1,"defined_names":14,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Лист3","index":0,"n_rows":94,"n_cols":18,"rows_kept":94,"cut":false,"hidden":false,"merged":[[20,9,20,11],[31,0,31,8],[48,5,48,6],[44,5,44,6],[45,5,45,6],[46,5,46,6],[47,5,47,6],[54,0,54,1],[88,9,88,10],[92,9,92,10],[91,9,91,10],[90,9,90,10],[89,9,89,10],[55,0,55,1],[89,3,90,3],[85,0,85,6]],"flags":["formulas_cached_only"]}
["   Зависимости давления насыщенного пара над плоской поверхностью воды и льда от температуры,",{"$nulls":8},"Удельная теплота парообразования воды ",null,null,null,"22,6 * 105","дж/кг"]
[" полученные теоретически на основании уравнения Клаузиуса - Клапейрона и сверенные",{"$nulls":8},"Удельная теплоемкость  воды (СРЕДНЯЯ)",null,null,null,"4,19 * 103","дж/кг"]
[" с экспериментальными данными многих исследователей, рекомендованы для метеорологической",{"$nulls":8},"Удельная теплота плавления льда",null,null,null,"3,33 * 105","дж/кг",333000]
[" практики Всемирной метеорологической организацией (ВМО) :",{"$nulls":8},"Удельная теплоемкость льда",null,null,null,"2,1 * 103","дж/кг"]
[{"$nulls":9},"Плотность льда",null,null,null,900,"кг/м.куб"]
["ln psw =-6094,4692T-1 +21,1249952-0,027245552 T+0,000016853396T2 +2,4575506 ln T",{"$nulls":7},-20]
["ln psi =-5504,4088T-1 - 3,5704628-0,017337458T+ 0,0000065204209T2 + 6,1295027 ln T,",{"$nulls":7},-20,{"$nulls":7},"a",5504.4088]
[{"$nulls":8},124.52761642027826,{"$nulls":7},"b",3.5704628]
["где psw и psi - давление насыщенного пара над плоской поверхностью воды и льда соответственно (Па);",{"$nulls":15},"c",0.017337458]
["Т - температура ( К ).",{"$nulls":10},"Гидравлический диаметр воздуховода",{"$nulls":4},"d",6.5204209e-06]
["Тогда для температуры Т = ",null,null,96,null,"Рsw = ",87721.4610049979,"Па",0.894204495463791,"бар",null,null,null,"F - площадь сечения, м2",null,null,"g",6.1295027]
[{"$nulls":5},"Psi  =",95649.83610077543,null,0.9750238134635619,"бар",null,null,null,"П - периметр, м"]
[{"$nulls":8},0.8934240168449241,"бар"]
[" Приведенные формулы справедливы для температур от 0 до 100ºC (для psw) и от -0 до -100ºC (для psi).",{"$nulls":8},"Кол-во тепла на воздухоохладителе:",null,null,null,"Q = 1,2*V*(Iвх-Iвых)/3600",null,null,"кВт"]
[" В то же время ВМО рекомендует первую формулу и для отрицательных температур для переохлажденной"]
[" воды (до -50ºC). "]
[]
["Другая формула для расчета давления насыщенного пара:"]
[{"$nulls":11},"1 кГс/м2",9.81,"1 Па",0.000981,"кГ/см2",0.000981]
[null,"Pн=133,32*10(156+8.12*t)/(236+t)",null,null,"Па",null,"(1 мм рт ст = 133,32 Па)"]
[{"$nulls":6},"1 кДж =",0.000278,"кВт*час"]
["Основные формулы:"]
["Относительная влажность",null,null,"j=100000*Рб*d/(Pн(622+d)",{"$nulls":8},"ПРО ТОЧКУ РОСЫ:"]
["Абсолютная влажность",null,null,"d=622*jPн/(Pб-jPн)",null,null,"г/кг сух возд, где",null,null,null,"Точка росы",null,"Тр=вδ(T,RH)/(а-δ(T,RH))",null,null,null,"где:"]
["Энтальпия                                       ",null,null,"I  = ct+(2500+1,8068t)*(d/1000)",null,null,"j - относит влажность воздуха"]
["Теплоемкость                         ",null,null,"с = 1,005+1,8068*(d/1000) ",null,null,"Рб - барометрическое давление",{"$nulls":5},"а=17,27","Т-температура, С"]
["Давление насыщения можно считать и по такой формуле:",{"$nulls":11},"в=237,7","RH - относ. влажность = 0-1"]
[null,null,null,"Pн = Pб*d/(j*(622+d))",null,null,"Рб-в Па,    j-%/100,     d-г/кг",{"$nulls":6},"δ(T,RH)=аТ/(в+Т)+ln(RH)"]
["или по такой:",null,null,"Pн =10(156+8*t)/(236+t)",{"$nulls":6},"Человек при высоких значениях точки росы чувствует себя некомфортно. "]
["Плотность воздуха",null,null,"р=353/(273,16+t)",{"$nulls":6},"В континентальном климате условия с точкой росы между 15 и 20 °C доставляют "]
[{"$nulls":10},"некоторый дискомфорт, а воздух с точкой росы выше 21 °C воспринимается как душный."]
["КОНДИЦИОНИРОВАНИЕ",{"$nulls":9},"Т",-28.5,"Тр=",-31.445621907226478]
["Город","122. Москва","Период","Холодный","Температура",-26,"Энтальпия",-25.3,null,null,"j",0.7556006491302424]
[null,null,-2.6852275968623367,{"$nulls":7},"δ(T,RH)",-2.632990850228302]
[{"$nulls":13},408]
[]
["Содержимое \"желтых\" ячеек - в вашем распоряжении - меняйте-экспериментируйте"]
[]
["Дано: ",null,null,null,"На входе",null,null,"На выходе",null,-5.248831340676219e-06]
[]
[null,"Температура воздуха, С",null,null,-28.5,null,null,22]
[null,"Влажность",null,"%",75.56006491302423,0.7556006491302424,null,1.6792027489460297,0.016792027489460296]
[null,"Давление",null,"мм.рт.ст",756,100.78992,"кПа",756,100.78992]
[null,"Температура по влажному термометру",null,null,{"$error":"#N/A"},null,null,{"$error":"#N/A"}]
["Тогда","Давление насыщения",null,null,58.80176546586117,"Па",null,2645.9879629376287,"конденсат"]
[null,"Абсолютная влажность",null,null,0.27420484063314016,"г/кг воздуха",null,0.27421008946448083,-5.248831340676219e-06]
[null,"Плотность воздуха",null,null,1.4428186054115915,"кг/куб.м",null,1.1959615124000542,"гр/кг возд"]
[null,"Теплоемкость                         ",null,null,1.005495433306056,null,null,1.0054954427896443]
[null,"Энтальпия",null,null,-27.985227596862337,"кДж/кГ",null,22.817324706405554]
[null,"Точка росы",null,null,-31.445621907226478,"  (+/- 0,4 град.С)",null,-31.350906819534874]
["Объем перекачиваемого воздуха в час",null,null,null,100,"м/куб","его вес",144.28186054115915,"кГ"]
["(вес на выходе установки не изменился, изменился объем!)",{"$nulls":7},"Конденсат"]
["Кол-во тепла в час",null,null,null,7329.886766555041,"кДж",2.037708521102301,"кВт*час",-7.573111514995116e-07,null,null,null,100,null,0.0816326530612245]
["Потребная  мощность установки",null,null,null,2.037708521102301,"кВт",null,null,"кГ/час"]
["Скорость воздуха",null,2.6,"м/сек",null,null,null,"для 2 х",82.49207907839148,null,null,null,2.037708521102301]
["Сечение в/в",null,0.010683760683760684,"кв.м","эквив. диаметр, мм:",null,116.66141702101508,"для 3 х",67.35450052112625]
[]
[null,null,9.360000000000001]
[null,null,1.38]
{"$rows_empty":12}
[null,"Для бассейнов:"]
[]
[" Интенсивность испарения рассчитывается следующим образом:"]
["W = e х F х (PB - PL )   [кг/час]"]
["F = Площадь водной поверхности бассейна (м2),"]
["PB = Давление водяных паров насыщенного воздуха у поверхности при Тводы в бассейне [bar],"]
["PL = Парциальное давление водяных паров при заданных температуре и влажности воздуха [bar],"]
["e = Эмпирический коэффициент [кг/(м2 х час х bar)]:"]
["0,5 - закрытая поверхность бассейна,"]
["5 - неподвижная поверхность бассейна,"]
["15 - небольшие частные бассейны с ограниченным количеством купающихся,"]
["20 - общественные бассейны с нормальной активностью купающихся, "]
["28 - бассейны для отдыха и развлечений,"]
["35 - бассейны с водяными горками и значительным волнообразованием"]
["                           Исходные данные:                              Результат:"]
["Тводы",19,"град С",0.02198903574324462,"PBоды [bar],"]
["Твоздуха",21,"град С",0.02488859488703302,"PBоздуха [bar],"]
["Относ. влажность",85,"%",0.021155305653978065,"PL  [bar],",{"$nulls":4},"Единицы энергии",null,"Джоуль"]
["e ",15,null,25.011902677996613,"[кг/(м2 х час х bar)]",{"$nulls":4},"Джоуль",null,1]
["F",2000,"кв.м",null,"кг/час",{"$nulls":4},"Квт-час (кВт×ч)",null,"3,6×106"]
["Относительная влажность воздуха j, выраженная в процентах, - отношение парциального давления ",{"$nulls":8},"Килокалория (ккал)",null,4186.8]
["водяного пара, содержащегося в воздухе, к парциальному давлению насыщенного водяного пара:",{"$nulls":8},"Килограммо-метр (кгс×м)",null,9.8]
["J = (рп / рнп)*100%"]

{"sheet":"Лист2","index":1,"n_rows":2833,"n_cols":20,"rows_kept":2833,"cut":false,"hidden":false,"merged":[[2830,13,2830,14],[2831,13,2831,14],[2832,13,2832,14],[2826,13,2826,14],[2827,13,2827,14],[2828,13,2828,14],[2829,13,2829,14],[2822,13,2822,14],[2823,13,2823,14],[2824,13,2824,14],[2825,13,2825,14],[2818,13,2818,14],[2819,13,2819,14],[2820,13,2820,14],[2821,13,2821,14],[2814,13,2814,14],[2815,13,2815,14],[2816,13,2816,14],[2817,13,2817,14],[2810,13,2810,14],[2811,13,2811,14],[2812,13,2812,14],[2813,13,2813,14],[2806,13,2806,14],[2807,13,2807,14],[2808,13,2808,14],[2809,13,2809,14],[2802,13,2802,14],[2803,13,2803,14],[2804,13,2804,14],[2805,13,2805,14],[2798,13,2798,14],[2799,13,2799,14],[2800,13,2800,14],[2801,13,2801,14],[2794,13,2794,14],[2795,13,2795,14],[2796,13,2796,14],[2797,13,2797,14],[2790,13,2790,14],[2791,13,2791,14],[2792,13,2792,14],[2793,13,2793,14],[2786,13,2786,14],[2787,13,2787,14],[2788,13,2788,14],[2789,13,2789,14],[2782,13,2782,14],[2783,13,2783,14],[2784,13,2784,14],[2785,13,2785,14],[2778,13,2778,14],[2779,13,2779,14],[2780,13,2780,14],[2781,13,2781,14],[2774,13,2774,14],[2775,13,2775,14],[2776,13,2776,14],[2777,13,2777,14],[2770,13,2770,14],[2771,13,2771,14],[2772,13,2772,14],[2773,13,2773,14],[2766,13,2766,14],[2767,13,2767,14],[2768,13,2768,14],[2769,13,2769,14],[2762,13,2762,14],[2763,13,2763,14],[2764,13,2764,14],[2765,13,2765,14],[2758,13,2758,14],[2759,0,2759,14],[2760,0,2760,14],[2761,13,2761,14],[2754,13,2754,14],[2755,13,2755,14],[2756,13,2756,14],[2757,13,2757,14],[2750,13,2750,14],[2751,13,2751,14],[2752,13,2752,14],[2753,13,2753,14],[2746,13,2746,14],[2747,13,2747,14],[2748,13,2748,14],[2749,13,2749,14],[2742,13,2742,14],[2743,13,2743,14],[2744,13,2744,14],[2745,13,2745,14],[2738,13,2738,14],[2739,13,2739,14],[2740,13,2740,14],[2741,13,2741,14],[2734,13,2734,14],[2735,13,2735,14],[2736,13,2736,14],[2737,13,2737,14],[2730,13,2730,14],[2731,13,2731,14],[2732,13,2732,14],[2733,13,2733,14],[2726,13,2726,14],[2727,13,2727,14],[2728,13,2728,14],[2729,13,2729,14],[2722,13,2722,14],[2723,13,2723,14],[2724,13,2724,14],[2725,13,2725,14],[2718,13,2718,14],[2719,0,2719,14],[2720,0,2720,14],[2721,13,2721,14],[2714,13,2714,14],[2715,13,2715,14],[2716,13,2716,14],[2717,13,2717,14],[2710,13,2710,14],[2711,13,2711,14],[2712,13,2712,14],[2713,13,2713,14],[2706,13,2706,14],[2707,13,2707,14],[2708,13,2708,14],[2709,13,2709,14],[2702,0,2702,14],[2703,0,2703,14],[2704,13,2704,14],[2705,13,2705,14],[2698,13,2698,14],[2699,0,2699,14],[2700,0,2700,14],[2701,13,2701,14],[2694,13,2694,14],[2695,13,2695,14],[2696,13,2696,14],[2697,13,2697,14],[2690,13,2690,14],[2691,13,2691,14],[2692,13,2692,14],[2693,13,2693,14],[2686,13,2686,14],[2687,13,2687,14],[2688,13,2688,14],[2689,13,2689,14],[2682,0,2682,14],[2683,0,2683,14],[2684,13,2684,14],[2685,13,2685,14],[2678,13,2678,14],[2679,13,2679,14],[2680,13,2680,14],[2681,13,2681,14],[2674,13,2674,14],[2675,13,2675,14],[2676,13,2676,14],[2677,13,2677,14],[2670,13,2670,14],[2671,13,2671,14],[2672,13,2672,14],[2673,13,2673,14],[2666,13,2666,14],[2667,13,2667,14],[2668,13,2668,14],[2669,13,2669,14],[2662,13,2662,14],[2663,13,2663,14],[2664,13,2664,14],[2665,13,2665,14],[2658,13,2658,14],[2659,13,2659,14],[2660,13,2660,14],[2661,13,2661,14],[2654,13,2654,14],[2655,13,2655,14],[2656,13,2656,14],[2657,13,2657,14],[2650,13,2650,14],[2651,13,2651,14],[2652,13,2652,14],[2653,13,2653,14],[2646,13,2646,14],[2647,13,2647,14],[2648,13,2648,14],[2649,13,2649,14],[2642,13,2642,14],[2643,13,2643,14],[2644,13,2644,14],[2645,13,2645,14],[2638,13,2638,14],[2639,13,2639,14],[2640,13,2640,14],[2641,13,2641,14],[2634,13,2634,14],[2635,13,2635,14],[2636,13,2636,14],[2637,13,2637,14],[2630,13,2630,14],[2631,13,2631,14],[2632,13,2632,14],[2633,13,2633,14],[2626,13,2626,14],[2627,13,2627,14],[2628,13,2628,14],[2629,13,2629,14],[2622,13,2622,14],[2623,13,2623,14],[2624,13,2624,14],[2625,13,2625,14],[2618,0,2618,14],[2619,0,2619,14],[2620,13,2620,14],[2621,13,2621,14],[2614,13,2614,14],[2615,13,2615,14],[2616,13,2616,14],[2617,13,2617,14],[2610,13,2610,14],[2611,13,2611,14],[2612,13,2612,14],[2613,13,2613,14],[2606,13,2606,14],[2607,13,2607,14],[2608,13,2608,14],[2609,13,2609,14],[2602,13,2602,14],[2603,13,2603,14],[2604,13,2604,14],[2605,13,2605,14],[2598,13,2598,14],[2599,13,2599,14],[2600,13,2600,14],[2601,13,2601,14],[2594,13,2594,14],[2595,13,2595,14],[2596,0,2596,14],[2597,0,2597,14],[2590,13,2590,14],[2591,13,2591,14],[2592,13,2592,14],[2593,13,2593,14],[2586,13,2586,14],[2587,13,2587,14],[2588,13,2588,14],[2589,13,2589,14],[2582,13,2582,14],[2583,13,2583,14],[2584,13,2584,14],[2585,13,2585,14],[2578,13,2578,14],[2579,0,2579,14],[2580,0,2580,14],[2581,13,2581,14],[2574,13,2574,14],[2575,13,2575,14],[2576,13,2576,14],[2577,13,2577,14],[2570,13,2570,14],[2571,13,2571,14],[2572,13,2572,14],[2573,13,2573,14],[2566,12,2566,13],[2567,0,2567,14],[2568,0,2568,14],[2569,13,2569,14],[2562,13,2562,14],[2563,13,2563,14],[2564,0,2564,14],[2565,0,2565,14],[2558,13,2558,14],[2559,13,2559,14],[2560,13,2560,14],[2561,13,2561,14],[2554,13,2554,14],[2555,13,2555,14],[2556,13,2556,14],[2557,13,2557,14],[2550,13,2550,14],[2551,13,2551,14],[2552,13,2552,14],[2553,13,2553,14],[2546,13,2546,14],[2547,13,2547,14],[2548,13,2548,14],[2549,13,2549,14],[2542,13,2542,14],[2543,13,2543,14],[2544,13,2544,14],[2545,13,2545,14],[2538,13,2538,14],[2539,13,2539,14],[2540,13,2540,14],[2541,13,2541,14],[2534,13,2534,14],[2535,13,2535,14],[2536,13,2536,14],[2537,13,2537,14],[2530,13,2530,14],[2531,13,2531,14],[2532,13,2532,14],[2533,13,2533,14],[2526,13,2526,14],[2527,13,2527,14],[2528,13,2528,14],[2529,13,2529,14],[2522,13,2522,14],[2523,13,2523,14],[2524,13,2524,14],[2525,13,2525,14],[2518,13,2518,14],[2519,13,2519,14],[2520,13,2520,14],[2521,13,2521,14],[2514,13,2514,14],[2515,13,2515,14],[2516,13,2516,14],[2517,13,2517,14],[2510,13,2510,14],[2511,13,2511,14],[2512,13,2512,14],[2513,13,2513,14],[2506,13,2506,14],[2507,13,2507,14],[2508,13,2508,14],[2509,13,2509,14],[2502,13,2502,14],[2503,13,2503,14],[2504,13,2504,14],[2505,13,2505,14],[2498,13,2498,14],[2499,13,2499,14],[2500,13,2500,14],[2501,13,2501,14],[2494,13,2494,14],[2495,13,2495,14],[2496,13,2496,14],[2497,13,2497,14],[2490,13,2490,14],[2491,13,2491,14],[2492,13,2492,14],[2493,13,2493,14],[2486,13,2486,14],[2487,13,2487,14],[2488,13,2488,14],[2489,13,2489,14],[2482,13,2482,14],[2483,13,2483,14],[2484,13,2484,14],[2485,13,2485,14],[2478,13,2478,14],[2479,13,2479,14],[2480,13,2480,14],[2481,13,2481,14],[2474,13,2474,14],[2475,13,2475,14],[2476,13,2476,14],[2477,13,2477,14],[2470,13,2470,14],[2471,13,2471,14],[2472,13,2472,14],[2473,13,2473,14],[2466,13,2466,14],[2467,13,2467,14],[2468,13,2468,14],[2469,13,2469,14],[2462,13,2462,14],[2463,13,2463,14],[2464,13,2464,14],[2465,13,2465,14],[2458,13,2458,14],[2459,13,2459,14],[2460,13,2460,14],[2461,13,2461,14],[2454,13,2454,14],[2455,13,2455,14],[2456,13,2456,14],[2457,13,2457,14],[2450,13,2450,14],[2451,13,2451,14],[2452,13,2452,14],[2453,13,2453,14],[2446,13,2446,14],[2447,13,2447,14],[2448,13,2448,14],[2449,13,2449,14],[2442,13,2442,14],[2443,13,2443,14],[2444,13,2444,14],[2445,13,2445,14],[2438,13,2438,14],[2439,13,2439,14],[2440,13,2440,14],[2441,13,2441,14],[2434,13,2434,14],[2435,13,2435,14],[2436,13,2436,14],[2437,13,2437,14],[2430,13,2430,14],[2431,13,2431,14],[2432,13,2432,14],[2433,13,2433,14],[2426,13,2426,14],[2427,13,2427,14],[2428,13,2428,14],[2429,13,2429,14],[2422,13,2422,14],[2423,13,2423,14],[2424,13,2424,14],[2425,13,2425,14],[2418,13,2418,14],[2419,13,2419,14],[2420,13,2420,14],[2421,13,2421,14],[2414,13,2414,14],[2415,13,2415,14],[2416,13,2416,14],[2417,13,2417,14],[2410,13,2410,14],[2411,13,2411,14],[2412,13,2412,14],[2413,13,2413,14],[2406,13,2406,14],[2407,13,2407,14],[2408,13,2408,14],[2409,13,2409,14],[2402,13,2402,14],[2403,13,2403,14],[2404,13,2404,14],[2405,13,2405,14],[2398,13,2398,14],[2399,13,2399,14],[2400,13,2400,14],[2401,13,2401,14],[2394,13,2394,14],[2395,13,2395,14],[2396,13,2396,14],[2397,13,2397,14],[2390,13,2390,14],[2391,13,2391,14],[2392,13,2392,14],[2393,13,2393,14],[2386,13,2386,14],[2387,13,2387,14],[2388,13,2388,14],[2389,13,2389,14],[2382,13,2382,14],[2383,13,2383,14],[2384,13,2384,14],[2385,13,2385,14],[2378,13,2378,14],[2379,13,2379,14],[2380,13,2380,14],[2381,13,2381,14],[2374,13,2374,14],[2375,13,2375,14],[2376,13,2376,14],[2377,13,2377,14],[2370,13,2370,14],[2371,13,2371,14],[2372,13,2372,14],[2373,13,2373,14],[2366,13,2366,14],[2367,13,2367,14],[2368,13,2368,14],[2369,13,2369,14],[2362,13,2362,14],[2363,13,2363,14],[2364,13,2364,14],[2365,13,2365,14],[2358,13,2358,14],[2359,13,2359,14],[2360,13,2360,14],[2361,13,2361,14],[2354,13,2354,14],[2355,13,2355,14],[2356,13,2356,14],[2357,13,2357,14],[2350,13,2350,14],[2351,13,2351,14],[2352,13,2352,14],[2353,13,2353,14],[2346,13,2346,14],[2347,13,2347,14],[2348,13,2348,14],[2349,13,2349,14],[2342,13,2342,14],[2343,13,2343,14],[2344,13,2344,14],[2345,13,2345,14],[2338,13,2338,14],[2339,13,2339,14],[2340,13,2340,14],[2341,13,2341,14],[2334,13,2334,14],[2335,13,2335,14],[2336,13,2336,14],[2337,13,2337,14],[2330,13,2330,14],[2331,13,2331,14],[2332,13,2332,14],[2333,13,2333,14],[2326,13,2326,14],[2327,13,2327,14],[2328,13,2328,14],[2329,13,2329,14],[2322,13,2322,14],[2323,13,2323,14],[2324,13,2324,14],[2325,13,2325,14],[2318,13,2318,14],[2319,13,2319,14],[2320,13,2320,14],[2321,13,2321,14],[2314,13,2314,14],[2315,13,2315,14],[2316,13,2316,14],[2317,13,2317,14],[2310,13,2310,14],[2311,13,2311,14],[2312,13,2312,14],[2313,13,2313,14],[2306,13,2306,14],[2307,13,2307,14],[2308,13,2308,14],[2309,13,2309,14],[2302,13,2302,14],[2303,13,2303,14],[2304,13,2304,14],[2305,13,2305,14],[2298,13,2298,14],[2299,13,2299,14],[2300,13,2300,14],[2301,13,2301,14],[2294,13,2294,14],[2295,13,2295,14],[2296,13,2296,14],[2297,13,2297,14],[2290,13,2290,14],[2291,13,2291,14],[2292,13,2292,14],[2293,13,2293,14],[2286,13,2286,14],[2287,13,2287,14],[2288,13,2288,14],[2289,13,2289,14],[2282,13,2282,14],[2283,13,2283,14],[2284,13,2284,14],[2285,13,2285,14],[2278,13,2278,14],[2279,13,2279,14],[2280,13,2280,14],[2281,13,2281,14],[2274,13,2274,14],[2275,13,2275,14],[2276,13,2276,14],[2277,13,2277,14],[2270,13,2270,14],[2271,13,2271,14],[2272,13,2272,14],[2273,13,2273,14],[2266,13,2266,14],[2267,13,2267,14],[2268,13,2268,14],[2269,13,2269,14],[2262,13,2262,14],[2263,13,2263,14],[2264,13,2264,14],[2265,13,2265,14],[2258,13,2258,14],[2259,13,2259,14],[2260,13,2260,14],[2261,13,2261,14],[2254,13,2254,14],[2255,13,2255,14],[2256,13,2256,14],[2257,13,2257,14],[2250,13,2250,14],[2251,13,2251,14],[2252,13,2252,14],[2253,13,2253,14],[2246,13,2246,14],[2247,13,2247,14],[2248,13,2248,14],[2249,13,2249,14],[2242,13,2242,14],[2243,13,2243,14],[2244,13,2244,14],[2245,13,2245,14],[2238,13,2238,14],[2239,13,2239,14],[2240,13,2240,14],[2241,13,2241,14],[2234,13,2234,14],[2235,13,2235,14],[2236,13,2236,14],[2237,13,2237,14],[2230,13,2230,14],[2231,13,2231,14],[2232,13,2232,14],[2233,13,2233,14],[2226,13,2226,14],[2227,13,2227,14],[2228,13,2228,14],[2229,13,2229,14],[2222,13,2222,14],[2223,13,2223,14],[2224,13,2224,14],[2225,13,2225,14],[2218,13,2218,14],[2219,13,2219,14],[2220,13,2220,14],[2221,13,2221,14],[2214,13,2214,14],[2215,13,2215,14],[2216,13,2216,14],[2217,13,2217,14],[2210,13,2210,14],[2211,13,2211,14],[2212,13,2212,14],[2213,13,2213,14],[2206,13,2206,14],[2207,13,2207,14],[2208,13,2208,14],[2209,13,2209,14],[2202,13,2202,14],[2203,13,2203,14],[2204,13,2204,14],[2205,13,2205,14],[2198,13,2198,14],[2199,13,2199,14],[2200,13,2200,14],[2201,13,2201,14],[2194,13,2194,14],[2195,13,2195,14],[2196,13,2196,14],[2197,13,2197,14],[2190,13,2190,14],[2191,13,2191,14],[2192,13,2192,14],[2193,13,2193,14],[2186,13,2186,14],[2187,13,2187,14],[2188,13,2188,14],[2189,13,2189,14],[2182,13,2182,14],[2183,13,2183,14],[2184,13,2184,14],[2185,13,2185,14],[2178,13,2178,14],[2179,13,2179,14],[2180,13,2180,14],[2181,13,2181,14],[2174,13,2174,14],[2175,13,2175,14],[2176,13,2176,14],[2177,13,2177,14],[2170,13,2170,14],[2171,13,2171,14],[2172,13,2172,14],[2173,13,2173,14],[2166,13,2166,14],[2167,13,2167,14],[2168,13,2168,14],[2169,13,2169,14],[2162,13,2162,14],[2163,13,2163,14],[2164,13,2164,14],[2165,13,2165,14],[2158,13,2158,14],[2159,13,2159,14],[2160,13,2160,14],[2161,13,2161,14],[2154,13,2154,14],[2155,13,2155,14],[2156,13,2156,14],[2157,13,2157,14],[2150,13,2150,14],[2151,13,2151,14],[2152,13,2152,14],[2153,13,2153,14],[2146,13,2146,14],[2147,13,2147,14],[2148,13,2148,14],[2149,13,2149,14],[2142,13,2142,14],[2143,13,2143,14],[2144,13,2144,14],[2145,13,2145,14],[2138,13,2138,14],[2139,13,2139,14],[2140,13,2140,14],[2141,13,2141,14],[2134,13,2134,14],[2135,13,2135,14],[2136,13,2136,14],[2137,13,2137,14],[2130,13,2130,14],[2131,13,2131,14],[2132,13,2132,14],[2133,13,2133,14],[2126,13,2126,14],[2127,13,2127,14],[2128,13,2128,14],[2129,13,2129,14],[2122,13,2122,14],[2123,13,2123,14],[2124,13,2124,14],[2125,13,2125,14],[2118,13,2118,14],[2119,13,2119,14],[2120,13,2120,14],[2121,13,2121,14],[2114,13,2114,14],[2115,13,2115,14],[2116,13,2116,14],[2117,13,2117,14],[2110,13,2110,14],[2111,13,2111,14],[2112,13,2112,14],[2113,13,2113,14],[2106,13,2106,14],[2107,13,2107,14],[2108,13,2108,14],[2109,13,2109,14],[2102,13,2102,14],[2103,13,2103,14],[2104,13,2104,14],[2105,13,2105,14],[2098,13,2098,14],[2099,13,2099,14],[2100,13,2100,14],[2101,13,2101,14],[2094,13,2094,14],[2095,13,2095,14],[2096,13,2096,14],[2097,13,2097,14],[2090,13,2090,14],[2091,13,2091,14],[2092,13,2092,14],[2093,13,2093,14],[2086,13,2086,14],[2087,13,2087,14],[2088,13,2088,14],[2089,13,2089,14],[2082,13,2082,14],[2083,13,2083,14],[2084,13,2084,14],[2085,13,2085,14],[2078,13,2078,14],[2079,13,2079,14],[2080,13,2080,14],[2081,13,2081,14],[2074,13,2074,14],[2075,13,2075,14],[2076,13,2076,14],[2077,13,2077,14],[2070,13,2070,14],[2071,13,2071,14],[2072,13,2072,14],[2073,13,2073,14],[2066,13,2066,14],[2067,13,2067,14],[2068,13,2068,14],[2069,13,2069,14],[2062,13,2062,14],[2063,13,2063,14],[2064,13,2064,14],[2065,13,2065,14],[2058,13,2058,14],[2059,13,2059,14],[2060,0,2060,14],[2061,0,2061,14],[1938,0,1938,12],[1939,0,1939,12],[1978,0,1978,12],[1979,0,1979,12],[1907,0,1907,12],[1908,0,1908,12],[1910,0,1910,12],[1911,0,1911,12],[1887,0,1887,12],[1888,0,1888,12],[1904,0,1904,12],[1905,0,1905,12],[1836,8,1837,8],[1836,9,1837,9],[1836,10,1837,10],[1836,12,1837,12],[1822,0,1822,12],[1823,0,1823,12],[1836,0,1837,0],[1836,1,1837,1],[1836,2,1837,2],[1836,3,1837,3],[1836,4,1837,4],[1836,5,1837,5],[1836,6,1837,6],[1836,7,1837,7],[1783,0,1783,12],[1784,0,1784,12],[1800,0,1800,12],[1801,0,1801,12],[1768,0,1768,12],[1769,0,1769,12],[1771,0,1771,12],[1772,0,1772,12],[1256,19,1256,20],[1262,0,1262,12],[1263,0,1263,12],[1302,0,1302,12],[1252,19,1252,20],[1253,19,1253,20],[1254,19,1254,20],[1255,19,1255,20],[1248,19,1248,20],[1249,19,1249,20],[1250,19,1250,20],[1251,19,1251,20],[1244,19,1244,20],[1245,19,1245,20],[1246,19,1246,20],[1247,19,1247,20],[1240,19,1240,20],[1241,19,1241,20],[1242,19,1242,20],[1243,19,1243,20],[1236,19,1236,20],[1237,19,1237,20],[1238,19,1238,20],[1239,19,1239,20],[1232,19,1232,20],[1233,19,1233,20],[1234,19,1234,20],[1235,19,1235,20],[1228,19,1228,20],[1229,19,1229,20],[1230,19,1230,20],[1231,19,1231,20],[1224,19,1224,20],[1225,19,1225,20],[1226,19,1226,20],[1227,19,1227,20],[1221,19,1221,20],[1222,19,1222,20],[1223,19,1223,20],[471,19,471,20],[472,0,472,19],[473,0,473,19],[472,20,473,20],[474,19,474,20],[475,19,475,20],[476,19,476,20],[1217,19,1217,20],[1218,19,1218,20],[1219,19,1219,20],[1220,19,1220,20],[1213,19,1213,20],[1214,19,1214,20],[1215,19,1215,20],[1216,19,1216,20],[1209,19,1209,20],[1210,19,1210,20],[1211,19,1211,20],[1212,19,1212,20],[1205,19,1205,20],[1206,19,1206,20],[1207,19,1207,20],[1208,19,1208,20],[1201,19,1201,20],[1202,19,1202,20],[1203,19,1203,20],[1204,19,1204,20],[1197,19,1197,20],[1198,19,1198,20],[1199,19,1199,20],[1200,19,1200,20],[1193,19,1193,20],[1194,19,1194,20],[1195,19,1195,20],[1196,19,1196,20],[1189,19,1189,20],[1190,19,1190,20],[1191,19,1191,20],[1192,19,1192,20],[1185,19,1185,20],[1186,19,1186,20],[1187,19,1187,20],[1188,19,1188,20],[1181,19,1181,20],[1182,19,1182,20],[1183,0,1183,19],[1184,0,1184,19],[1183,20,1184,20],[1177,19,1177,20],[1178,19,1178,20],[1179,19,1179,20],[1180,19,1180,20],[1173,19,1173,20],[1174,19,1174,20],[1175,19,1175,20],[1176,19,1176,20],[1169,19,1169,20],[1170,19,1170,20],[1171,19,1171,20],[1172,19,1172,20],[1165,19,1165,20],[1166,19,1166,20],[1167,19,1167,20],[1168,19,1168,20],[1161,19,1161,20],[1162,19,1162,20],[1163,19,1163,20],[1164,19,1164,20],[1157,19,1157,20],[1158,19,1158,20],[1159,19,1159,20],[1160,19,1160,20],[1153,19,1153,20],[1154,19,1154,20],[1155,19,1155,20],[1156,19,1156,20],[1149,19,1149,20],[1150,19,1150,20],[1151,19,1151,20],[1152,19,1152,20],[1145,19,1145,20],[1146,19,1146,20],[1147,19,1147,20],[1148,19,1148,20],[1141,19,1141,20],[1142,19,1142,20],[1143,0,1143,19],[1144,0,1144,19],[1143,20,1144,20],[1137,19,1137,20],[1138,19,1138,20],[1139,19,1139,20],[1140,19,1140,20],[1133,19,1133,20],[1134,19,1134,20],[1135,19,1135,20],[1136,19,1136,20],[1129,19,1129,20],[1130,19,1130,20],[1131,19,1131,20],[1132,19,1132,20],[1125,19,1125,20],[1126,19,1126,20],[1127,19,1127,20],[1128,19,1128,20],[1121,19,1121,20],[1122,19,1122,20],[1123,19,1123,20],[1124,19,1124,20],[1117,19,1117,20],[1118,19,1118,20],[1119,19,1119,20],[1120,19,1120,20],[1114,19,1114,20],[1115,0,1115,19],[1116,0,1116,19],[1115,20,1116,20],[1111,19,1111,20],[1112,0,1112,19],[1113,0,1113,19],[1112,20,1113,20],[1107,19,1107,20],[1108,19,1108,20],[1109,19,1109,20],[1110,19,1110,20],[1103,19,1103,20],[1104,19,1104,20],[1105,19,1105,20],[1106,19,1106,20],[1099,19,1099,20],[1100,19,1100,20],[1101,19,1101,20],[1102,19,1102,20],[1094,19,1094,20],[1095,0,1095,19],[1095,20,1096,20],[1096,0,1096,19],[1090,19,1090,20],[1091,19,1091,20],[1092,19,1092,20],[1093,19,1093,20],[1086,19,1086,20],[1087,19,1087,20],[1088,19,1088,20],[1089,19,1089,20],[1082,19,1082,20],[1083,19,1083,20],[1084,19,1084,20],[1085,19,1085,20],[1078,19,1078,20],[1079,19,1079,20],[1080,19,1080,20]],"merged_total":2323,"flags":["formulas_cached_only","merged_cut"]}
["РАСЧЕТНЫЕ ПАРАМЕТРЫ НАРУЖНОГО ВОЗДУХА"]
["Наименование пункта1","Расчетная географическая широта, °с.ш.","Барометрическое давление, ГПа","Период года","Параметры А",null,null,"Параметры Б",null,null,"Средняя суточная амплитуда температуры воздуха, °С"]
[{"$nulls":4},"температура воздуха, °С","удельная энтальпия, кДж/кг","скорость ветра, м/с","температура воздуха, °С","удельная энтальпия, кДж/кг","скорость ветра, м/с"]
["1. Абакан",52,900,"Теплый",23.8,51.1,1,28,54.4,1,12.7]
[null,null,null,"Холодный",-27,-26.8,1,-40,-42.3,1,"-"]
["2. Алдан",60,930,"Теплый",20.1,49.4,1,24.8,51.1,1,11.4]
[null,null,null,"Холодный",-32,-31.8,2,-42,-42.2,2,"-"]
["3. Актюбинск",52,990,"Теплый",27.1,51.1,1,32.5,56.9,1,14.2]
[null,null,null,"Холодный",-21,-19.7,5,-31,-30.6,5,"-",null,24.8]
["4. Александровск-Сахалинский",52,1010,"Теплый",19,46.9,3.7,22.1,49.8,3.7,8.1]
[null,null,null,"Холодный",-19,-17.6,6,-27,-26.5,6.9,"-"]
["5. Алма-Ата",44,930,"Теплый",27.6,51.5,1,31.2,54.4,1,11.9]
[null,null,null,"Холодный",-10,-6.7,1.7,-25,-24.3,1.3,"-"]
["6. Архангельск",64,1010,"Теплый",18.6,48.6,4,24.5,55.3,4,9.8]
[null,null,null,"Холодный",-19,-17.6,5.8,-31,-30.8,6.2,"-"]
["7. Астрахань",48,1010,"Теплый",29.5,61.1,3.6,33,64.5,3.6,10.7]
[null,null,null,"Холодный",-8,-4.2,9,-23,-21.9,8,"-"]
["8. Ашхабад",36,970,"Теплый",36,58.2,2.4,39,62.8,2.4,14.5]
[null,null,null,"Холодный",-2,4.2,3.2,-11,-8,2,"-"]
["9. Ачинск",56,970,"Теплый","22,6-23",49,3.2,28,52.3,3.2,12.5]
[null,null,null,"Холодный",null,-20.9,2,-41,-41,1,"-"]
["10. Байкит",60,990,"Теплый",-22.3,46.9,1,26,51.1,1,15.4]
[null,null,null,"Холодный",-38,-38.1,2,-50,-50.2,1,"-"]
["11. Баку",40,1010,"Теплый",28.3,65.3,4,31.7,68.7,4,7.4]
[null,null,null,"Холодный",1,8.4,8,-4,0.8,8,"-"]
["12. Балашов",52,990,"Теплый",25.2,50.7,3.7,27.8,54,3.7,12.4]
[null,null,null,"Холодный",-15,-13,5,-27,-26.8,4,"-"]
["13. Барнаул",52,990,"Теплый",23.9,-51.9,1,28.3,55.7,1,11.8]
[null,null,null,"Холодный",-23,-22.2,2.9,-39,-38.9,2,"-"]
["14. Батуми",40,1010,"Теплый",25.9,69.1,"-",29.6,71.6,"-",6.7]
[null,null,null,"Холодный",4,13,4,-1,5,3.1,"-"]
["15. Березники",60,1010,"Теплый",20.6,47.7,"-",26,51.9,"-",11.3]
[null,null,null,"Холодный",-21,-19.7,4.8,-36,-35.2,4.2,"-"]
["16. Березово",64,1010,"Теплый",18.2,45.2,4.2,21,51.5,4.2,8.6]
[null,null,null,"Холодный",-27,-26.8,4.6,-43,-43,4.7,"-"]
["17. Бишкек",44,930,"Теплый",28.9,52.8,1,34.4,57.8]
[null,null,null,"Холодный",-9,-6.3,2.4,-23,-22.2,1,14.2]
["18. Бикин",48,1010,"Теплый",24.9,60.7,1,28.2,65.7,2.2,"-"]
[null,null,null,"Холодный",-23,-22.2,8.2,-32,-31.8,1,10.6]
["19. Бийск",52,970,"Теплый",24.2,51.1,3.1,28.6,55.3,7,"-"]
[null,null,null,"Холодный",-24,-23,2.5,-38,-38.1,3.1,13]
["20. Бисер",60,950,"Теплый",18.7,46.5,1,26.2,49.8,2,"-"]
[null,null,null,"Холодный",-22,-20.9,6,-35,-34.9,1,10.7]
["21. Благовещенск",52,990,"Теплый",25.1,57.8,1,28.5,63.6,4.2,"-"]
[null,null,null,"Холодный",-25,-24.3,2.5,-34,-33.9,1,10.1]
["22. Бодайбо",56,950,"Теплый",23.1,48.6,1,27.6,52.8,2,"-"]
[null,null,null,"Холодный",-36,-36,1,-47,-47.3,1,14.6]
["23. Боровичи",60,990,"Теплый",21.1,48.6,1,25.8,"52,8-28,6",1,"-"]
[null,null,null,"Холодный",-13,-10.5,4.7,-29,null,1,11.4]
["24. Братск",56,970,"Теплый",22.5,49,1,27.7,53.2,1,14.1]
[null,null,null,"Холодный",-30,-29.7,2,-43,-43.1,2,"-"]
["25. Брест",52,990,"Теплый",22.4,49,3.3,27,56.5,3.3,10.8]
[null,null,null,"Холодный",-8,-4.2,7.1,-20,-18.8,4.2,"-"]
["26. Брянск",52,990,"Теплый",22.5,49.8,1,27.3,53.2,1,12.6]
[null,null,null,"Холодный",-13,-10.5,5.2,-26,-25,6,"-"]
["27. Василевичи",52,990,"Теплый",22.8,50.2,1,27,56.1,1,12.2]
[null,null,null,"Холодный",-8,-4.2,4.2,-24,-23,3.6,"-"]
["28. Великие Луки",56,990,"Теплый",21.7,49,1,25.7,53.2,1,11.7]
[null,null,null,"Холодный",-12,-9.2,4.7,-27,-26.8,3.2,"-"]
["29. Вентспилс",56,990,"Теплый",18.4,47.3,1,22.6,51.5,1,6.9]
[null,null,null,"Холодный",-7,-2.5,9.7,-18,-16.3,9.1,"-"]
["30. Верхотурье",60,990,"Теплый",21.3,47.3,1,26.1,52.8,1,12.5]
[null,null,null,"Холодный",-22,-20.9,4.2,-37,-37.2,3.9,"-"]
["31. Верхоянск",68,990,"Теплый",19.2,46.1,1,26.1,48.1,1,13.5]
[null,null,null,"Холодный",-51,-51.1,1.5,-59,-59.3,1,"-"]
["32. Вилюйск",64,990,"Теплый",21.6,46.9,1,26.5,51.5,1,12.1]
[null,null,null,"Холодный",-42,-42.3,2.6,-52,-52.3,2.8,"-"]
["33. Вильнюс",56,990,"Теплый",21.6,48.1,1,26.1,53.2,1,10.3]
[null,null,null,"Холодный",-9,-5,4.2,-23,-22.2,4.1,"-"]
["34. Винница",48,970,"Теплый",23,53.6,2.8,27.3,56.9,2.8,11.9]
[null,null,null,"Холодный",-10,-6.7,7.1,-21,-19.7,5.2,"-"]
["35. Витебск",56,990,"Теплый",21.6,49.4,3.3,25.7,53.2,3.3,10.5]
[null,null,null,"Холодный",-12,-9.2,4.5,-26,-25.5,3.2,"-"]
["36. Владивосток",44,990,"Теплый",23.6,57.8,4.7,23.4,61.5,4.7,5.5]
[null,null,null,"Холодный",-16,-14.2,14.8,-24,-25.3,13.5,"-"]
["37. Владикавказ",44,930,"Теплый",23.8,60.7,1,31.1,64.9,1,10.3]
[null,null,null,"Холодный",-5,0,6.3,-18,-16.5,4,"-"]
["38. Владимир",56,990,"Теплый",21.4,49.4,3.3,27.6,52.8,3.3,10.3]
[null,null,null,"Холодный",-16,-14.2,4.4,-28,-27.8,3.5,"-"]
["39. Вологда",60,990,"Теплый",21.1,50.2,1,27.2,55.3,1,11.1]
[null,null,null,"Холодный",-16,-14.2,5.8,-31,-30.6,5.2,"-"]
["40. Волгоград",48,990,"Теплый",28.6,55.3,5.2,33,57.8,5.2,12.7]
[null,null,null,"Холодный",-13,-10.5,9.1,-25,-23.9,8,"-"]
["41. Воркута",68,990,"Теплый",15.2,35.6,4.8,18.2,41.4,4.8,10.3]
[null,null,null,"Холодный",-26,-25.5,5,-42,-41,6.2,"-"]
["42. Воронеж",52,990,"Теплый",24.2,52.3,3.3,28.9,54.8,3.3,11.3]
[null,null,null,"Холодный",-14,-11.7,6,-26,-25.3,5.7,"-"]
["43. Вышний Волочек",56,990,"Теплый",21,48.6,3.3,25.6,52.8,3.3,10.6]
[null,null,null,"Холодный",-14,-11.7,4.6,-29,-28.5,3.2,"-"]
["44. Гарм",40,870,"Теплый",30.5,49.4,1,33.4,52.3,1,16.9]
[null,null,null,"Холодный",-5,-0.8,7.5,-17,-15.6,2.7,"-"]
["45. Горки",56,990,"Теплый",21.4,49.8,3.8,23.1,53.2,3.8,11.4]
[null,null,null,"Холодный",-12,-9.2,4.2,-25,-26.8,3.2,"-"]
["46. Грозный",44,990,"Теплый",28.8,63.2,1,34.9,66.6,1,12.9]
[null,null,null,"Холодный",-5,0,6.3,-18,-16.2,5.3,"-"]
["47. Гурьев",48,1010,"Теплый",30.1,59.9,5.2,36.2,63.6,5.2,13.3]
[null,null,null,"Холодный",-12,-9.2,9,-26,-25,8,"-"]
["48. Гюрми",40,950,"Теплый",34.4,58.6,1,37.6,60.7,1,15.1]
[null,null,null,"Холодный",-5,0.8,3.3,-13,-10.5,3.6,"-"]
["49. Даугавпилс",56,1010,"Теплый",21.2,48.6,1,24.1,52.8,1,11.1]
[null,null,null,"Холодный",-10,-6.7,4.2,-27,-26.8,3.2,"-"]
["50. Джамбул",44,1010,"Теплый",29.4,54.4,1,33.5,56.6,1,17.6]
[null,null,null,"Холодный",-9,-6.3,3,-26,-25,3,"-"]
["51. Дербент",44,1010,"Теплый",26.4,64.1,1,30.8,67,1,7.4]
[null,null,null,"Холодный",0,7.5,8,-9,-5.9,6.3,"-"]
["52. Днепропетровск",48,1010,"Теплый",26.5,54,1,31,57.4,1,11.3]
[null,null,null,"Холодный",-9,-5.4,7,-23,-22,5.7,"-"]
["53. Дудинка",68,1010,"Теплый",17.2,47.3,4,22.4,49.9,4,8.6]
[null,null,null,"Холодный",-35,-35.2,4.2,-46,-46.1,4.5,"-"]
["54. Душанбе",40,910,"Теплый",34.3,57.8,1,36.8,61.6,1,17.9]
[null,null,null,"Холодный",-2,3.8,3.3,-13,-10.7,2.6,"-"]
["55. Ейск",48,1010,"Теплый",26.3,57.4,5.7,30.8,61.1,5.7,7.5]
[null,null,null,"Холодный",-7,-2.9,12,-22,-19.7,8,"-"]
["56. Екатеринбург",56,970,"Теплый",20.7,48.1,4,28.7,51.1,4,10.6]
[null,null,null,"Холодный",-20,-18.8,4.7,-35,-34.6,5.2,"-"]
["57. Елабуга",56,990,"Теплый",23.9,51.1,3.7,28.3,544,3.7,11.5]
[null,null,null,"Холодный",-19,-17.3,3.4,-33,-28.7,3.2,"-"]
["58. Енисейск",60,990,"Теплый",22.3,48.1,1,27.7,52.8,1,12.3]
[null,null,null,"Холодный",-28,-27.6,2.8,-46,-46.3,2,"-"]
["59. Ербогачен",60,990,"Теплый",21.6,47.7,1,28,51.1,1,15]
[null,null,null,"Холодный",-38,-38.1,1.5,-51,-49.2,1,"-"]
["60. Ереван",40,910,"Теплый",29.7,61.1,1,34.8,62.8,1,15.1]
[null,null,null,"Холодный",-8,1.3,1,-19,-17.6,1,"-"]
["61. Жиганск",68,1010,"Теплый",18.6,47.7,4.2,23.5,49.4,4.2,11.1]
[null,null,null,"Холодный",43,-43.1,3.3,51,-51.1,3.9,"-"]
["62. Запорожье",48,1010,"Теплый",27.1,55.7,1,31.2,58.6,1,12.5]
[null,null,null,"Холодный",-8,-5.4,7.8,-22,-21.2,7.1,"-"]
["63. Земетчино",52,990,"Теплый",23.6,51.1,1,28.6,54.4,1,13]
[null,null,null,"Холодный",-15,-13,4.4,-29,-28.5,3.8,"-"]
["64. Златоуст",56,950,"Теплый",20,47.7,3.6,25.4,51.9,3.6,10.9]
[null,null,null,"Холодный",-20,-18.8,3.5,-34,-29.7,3,"-"]
["65. Иваново",56,990,"Теплый",22.2,49.8,2.8,27,52.8,2.8,11.6]
[null,null,null,"Холодный",-16,-14.2,4.2,-29,-28.6,3.6,"-"]
["66. Измаил",44,1010,"Теплый",27.2,58.6,1,31.8,61.5,1,11.8]
[null,null,null,"Холодный",-5,0,9,-14,-11.7,7,"-"]
["67. Илимск",56,990,"Теплый",23.1,49.4,1,29.2,52.8,1,15.3]
[null,null,null,"Холодный",-29,-28.5,1,-45,-45.2,1,"-"]
["58. Ирбит",56,990,"Теплый",22.5,48.1,3.5,28,52.3,3.5,12.9]
[null,null,null,"Холодный",-21,-19.7,4.8,-36,-33.1,4.6,"-"]
["59. Иргиз",48,990,"Теплый",30,52.3,5.5,33.8,56.9,5,14.5]
[null,null,null,"Холодный",-20,-18.8,6,-30,-29.7,7,"-"]
["70. Иркутск",52,950,"Теплый",22.7,50.2,2.2,26.9,53.6,2.2,13.4]
[null,null,null,"Холодный",-25,-24.3,2,-37,-37.1,2.8,"-"]
["71. Казалинск",44,990,"Теплый",31.4,56.5,3.4,37.1,59.9,3.4,13.7]
[null,null,null,"Холодный",-14,-11.7,4.5,-26,-25,4.4,"-"]
["72. Казань",56,990,"Теплый",22.8,51.1,3.8,27.3,54.8,3.8,11.1]
[null,null,null,"Холодный",-18,-16.3,4,-32,-31.7,4,"-"]
["73. Калининград",56,1010,"Теплый",20.6,48.6,4.3,24.1,52.8,4.3,9]
[null,null,null,"Холодный",-7,-2.9,7.8,-18,-16.3,7,"-"]
["74. Калуга",56,990,"Теплый",22.4,50.2,1,26.3,53.6,1,11.6]
[null,null,null,"Холодный",-14,-11.7,4.8,-27,-26.5,3.2,"-"]
["75. Камышин",52,1010,"Теплый",26.6,54,4.6,31,57.4,4.6,12.5]
[null,null,null,"Холодный",-15,-13,9.1,-26,-25.5,8,"-"]
["76. Караганда",48,950,"Теплый",25.1,46.5,1,31,51.9,1,13.3]
[null,null,null,"Холодный",-20,-18.8,6.5,-32,-31.8,5.8,"-"]
["77. Каргополь",60,990,"Теплый",20,47.3,3.2,24.7,54,3.2,11.1]
[null,null,null,"Холодный",-18,-16.3,5.3,-33,-31.8,3.8,"-"]
["78. Карпинск",60,990,"Теплый",20.9,46.1,"-",25.8,51.5,"-",10.5]
[null,null,null,"Холодный",-23,-22.2,4,-39,-33.9,3.2,"-"]
["79. Каунас",56,990,"Теплый",21.2,48.6,1,24.2,52.8,1,10.2]
[null,null,null,"Холодный",-8,-4.2,5.6,-22,-20.8,3.5,"-"]
["80. Кежма",60,990,"Теплый",23.3,48.1,1,28,51.9,1,13.7]
[null,null,null,"Холодный",-33,-33.1,1.5,-48,-48.2,1,"-"]
["81. Кемерово",56,990,"Теплый",21.8,50.2,1,27.3,53.2,1,12.4]
[null,null,null,"Холодный",-24,-24.3,3.7,-39,-38.9,3.2,"-"]
["82. Кемь",64,1010,"Теплый",18.6,42.7,4.1,21.3,47.7,4.1,7.5]
[null,null,null,"Холодный",-15,-13,5.1,-27,-26.8,3.6,"-"]
["83. Кзыл-Орда",44,990,"Теплый",31.7,53.6,2.6,37.4,58.2,2.6,15.9]
[null,null,null,"Холодный",-12,-9.2,5,-24,-23,5.4,"-"]
["84. Керчь",44,1010,"Теплый",26,60.7,4.1,30.3,62.8,4.1,11]
[null,null,null,"Холодный",-4,1.3,10.2,-15,-13,9,"-"]
["85. Киев",52,990,"Теплый",23.7,53.6,1,28.7,56.1,1,10.8]
[null,null,null,"Холодный",-10,-6.7,5.3,-22,-20.7,4.2,"-"]
["86. Киренск",56,970,"Теплый",23.5,49,1,28,53.2,1,13.2]
[null,null,null,"Холодный",-34,-33.9,2,-49,-49.1,2,"-"]
["87. Киров",60,990,"Теплый",20.9,50.7,4,28.1,56.9,4,9.8]
[null,null,null,"Холодный",-19,-17.6,8.4,-33,-32.6,5.4,"-"]
["88. Кировоград",48,990,"Теплый",25.8,55.3,1,29.7,57.4,1,12.9]
[null,null,null,"Холодный",-9,-5.4,6.7,-22,-20.7,5.7,"-"]
["89. Кишинев",48,990,"Теплый",26,56.9,3.6,30.2,59.5,3.6,12.2]
[null,null,null,"Холодный",-7,-2.9,5.7,-16,-14,4.4,"-"]
["90. Ключи",56,1010,"Теплый",17.7,41.9,1,21.8,46.1,1,12.4]
[null,null,null,"Холодный",-23,-22.2,3,-39,-38.9,3,"-"]
["91. Кокчетав",52,970,"Теплый",24,49.8,1,31.5,54,1,12.8]
[null,null,null,"Холодный",-21,-19.7,6.3,-36,-36.2,5,"-"]
["92. Комсомольск-на-Амуре",52,1010,"Теплый",22.8,52.3,1,27,59.5,1,9.7]
[null,null,null,"Холодный",-27,-26.8,8.2,-35,-34.9,5,"-"]
["93. Конотоп",52,990,"Теплый",24,52.3,1,28,55.7,1,11.6]
[null,null,null,"Холодный",-11,-8,5,-24,-22.2,4.3,"-"]
["94. Корсаков",48,1010,"Теплый",19.6,49.4,1,22,54,1,7]
[null,null,null,"Холодный",-12,-9.2,8,-20,-19.7,10,"-"]
["95. Кострома",56,990,"Теплый",21.1,49.8,4.2,25.8,53.6,4.2,10]
[null,null,null,"Холодный",-16,-14.2,4.8,-31,-30.7,4,"-"]
["96. Котлас",60,990,"Теплый",20.8,46.9,4,23.1,51.1,4,11]
[null,null,null,"Холодный",-19,-17.6,5.4,-34,-34.1,4.2,"-"]
["97. Красноводск",40,1010,"Теплый",31.6,64.5,5.3,35.7,68.2,5.3,9.5]
[null,null,null,"Холодный",0,6.7,7,-8,-4.2,7,"-"]
["98. Краснодар",44,970,"Теплый",28.6,59.5,1,30.8,636,1,18]
[null,null,null,"Холодный",-5,0,4.4,-19,-17.6,3.1,"-"]
["99. Красноуфимск",56,970,"Теплый",21.6,51.9,1,26.6,54.8,1,12]
[null,null,null,"Холодный",-21,-19.7,3.7,-35,-36,3.2,"-"]
["100. Красноярск",56,970,"Теплый",22.5,49.4,1,25.9,51.9,1,10.9]
[null,null,null,"Холодный",-22,-20.9,1.8,-40,-40.2,1,"-"]
["101. Купино",56,990,"Теплый",23.2,50.2,4,27.7,53.6,4,12.1]
[null,null,null,"Холодный",-25,-24.3,5.5,-38,-38.1,4.5,"-"]
["102. Курган",56,990,"Теплый",23.6,51.1,3.2,28,53.6,3.2,12]
[null,null,null,"Холодный",-24,-23,6.1,-37,-36.9,5.2,"-"]
["103. Курск",52,970,"Теплый",22.9,51,3.5,27.8,53.6,3.5,10.4]
[null,null,null,"Холодный",-14,-11.7,6.7,-26,-25,6.3,"-"]
["104. Кустанай",52,990,"Теплый",25,50.2,5.1,28.4,53.6,5.1,13.4]
[null,null,null,"Холодный",-22,-20.9,6.1,-35,-35.2,5.5,"-"]
["105. Кутаиси",44,990,"Теплый",27.4,67,1,31.7,69.1,1,9.2]
[null,null,null,"Холодный",3,10,2,-3,1.7,0.5,"-"]
["106. Кушка",36,950,"Теплый",33.8,56.1,1,38.7,59.5,1,18.8]
[null,null,null,"Холодный",-4,0.8,2,-13,-10.2,2,"-"]
["107. Кызыл",52,950,"Теплый",24,48.6,1,29,49.4,1,13.7]
[null,null,null,"Холодный",-37,-36.8,0.8,-48,-48.1,1,"-"]
["108. Ленинакан",40,830,"Теплый",24.8,61.1,1,30,64.5,1,13.4]
[null,null,null,"Холодный",-11,-8,1.5,-23,-22.2,1,"-"]
["109. Лиепая",56,1010,"Теплый",18.3,47.3,5.6,22.8,52.3,5.6,6.7]
[null,null,null,"Холодный",-6,-1.7,7.5,-18,-16.3,7.1,"-"]
["110. Липецк",52,990,"Теплый",24.4,50.2,4.1,28.7,54.8,4.1,11.6]
[null,null,null,"Холодный",-15,-13,6.5,-27,-26.5,5.4,"-"]
["111. Львов",48,970,"Теплый",22.1,53.2,1,26.4,57.4,1,10.6]
[null,null,null,"Холодный",-9,-2.5,7.1,-19,-17.6,5.1,"-"]
["112. Луганск",48,1010,"Теплый",27.4,55.3,1,31.8,58.6,1,13.9]
[null,null,null,"Холодный",-10,-6.7,6.7,-25,-24.3,5.2,"-"]
["113. Магнитогорск",52,970,"Теплый",22.8,49.4,1,27.4,52.3,1,12.6]
[null,null,null,"Холодный",-22,-20.9,4.1,-34,-33.9,4,"-"]
["114. Малый Узень",52,1010,"Теплый",28.4,54,3.8,33,57.4,3.8,14.7]
[null,null,null,"Холодный",-17,-15.5,7.3,-29,-28.5,7,"-"]
["115. Мариинск",56,990,"Теплый",23.2,50.2,1,28.4,54.4,1,12.9]
[null,null,null,"Холодный",-24,-23,3.5,-40,-39.9,2.2,"-"]
["116. Мариуполь",48,1010,"Теплый",26.6,57.8,3.6,31.8,60.7,3.6,11.4]
[null,null,null,"Холодный",-9,-5.4,12,-23,-22.2,8,"-"]
["117. Махачкала",44,1010,"Теплый",26.9,63.6,4.9,31.6,67,4.9,7.6]
[null,null,null,"Холодный",-2,-4.2,9,-14,-11.7,7.2,"-"]
["118. Мезень",68,1010,"Теплый",18.6,44.8,3.8,21.5,48.1,3.8,10.7]
[null,null,null,"Холодный",-21,-19.7,5.8,-35,-35,4.5,"-"]
["119. Минск",52,990,"Теплый",21.2,49.8,4.2,25.9,53.6,4.2,10.4]
[null,null,null,"Холодный",-10,-6.7,6.3,-25,-24.3,4.5,"-"]
["120. Минусинск",52,970,"Теплый",24,51.1,1,28.2,54.4,1,13.5]
[null,null,null,"Холодный",-27,-26.8,1,-40,-40.3,1,"-"]
["121. Мичуринск",52,990,"Теплый",24.4,51.5,1,29,54.4,1,11.7]
[null,null,null,"Холодный",-15,-13,4.8,-28,-25.5,3.2,"-"]
["122. Москва",56,990,"Теплый",22.3,49.4,1,28.5,54,1,10.4]
[null,null,null,"Холодный",-15,-11.7,4.7,-26,-25.3,4,"-"]
["123. Мурманск",68,1010,"Теплый",16.6,41.4,3.8,22,42.7,3.8,8.9]
[null,null,null,"Холодный",-18,-16.3,8.7,-27,-26.6,8.4,"-"]
["124. Наманган",40,950,"Теплый",34.2,62.4,1,37,65.7,1,14.9]
[null,null,null,"Холодный",-7,-3.8,2.2,-14,-12,1,"-"]
["125. Нарьян-Map",68,1010,"Теплый",17.7,44.8,5.2,23,46.5,5.2,9]
[null,null,null,"Холодный",-25,-24.3,7,-37,-36.8,7,"-"]
["126. Нарым",60,990,"Теплый",22.8,38.5,3.3,27.5,41.4,3.3,"-"]
[null,null,null,"Холодный",-28,-27.6,4.7,-42,-42.3,4.6,"-"]
["127. Нерчинский Завод",52,950,"Теплый",23.5,51.5,1,27.2,55.3,1,13.2]
[null,null,null,"Холодный",-31,-30.6,2,-41,-41,2,"-"]
["128. Нижнеудинск",56,950,"Теплый",23,49.4,1,27.7,53.2,1,13.7]
[null,null,null,"Холодный",-24,-23,2,-40,-38.9,2,"-"]
["129. Нижний Новгород",56,990,"Теплый",21.2,51.1,1,26.8,54.9,1,9.5]
[null,null,null,"Холодный",-16,-14.2,4.1,-30,-29.7,4,"-"]
["130. Нижний Тагил",56,970,"Теплый",21.5,46.5,1,26.3,50.2,1,12.6]
[null,null,null,"Холодный",-21,-19.7,3.7,-36,-31.9,3,"-"]
["131. Николаев",48,1010,"Теплый",27.9,58.2,3.2,31,62,3.2,12.5]
[null,null,null,"Холодный",-7,-2.9,11,-20,-18.6,10,"-"]
["132. Николаевск-на-Амуре",52,1010,"Теплый",19.6,46.1,3.4,23.9,52.3,3.4,9.5]
[null,null,null,"Холодный",-25,-24.3,8,-35,-35.2,6,"-"]
["133. Новгород",60,1010,"Теплый",20.8,48.6,4,24.5,52.8,4,11.2]
[null,null,null,"Холодный",-12,-9.2,5,-27,-26.8,5,"-"]
["134. Новокузнецк",52,990,"Теплый",24.1,51.5,1,27.5,54.4,1,11.6]
[null,null,null,"Холодный",-23,-22.2,2.5,-39,-38.1,2,"-"]
["135. Новороссийск",44,1010,"Теплый",26.7,60.3,1,30.1,65.7,1,8.6]
[null,null,null,"Холодный",-2,3.8,15.4,-13,-10.5,17.5,"-"]
["136. Новосибирск",56,990,"Теплый",22.7,50.2,1,28.4,54.8,1,11.4]
[null,null,null,"Холодный",-24,-23,3.7,-39,-38.9,2.7,"-"]
["137. Нукус",44,1010,"Теплый",32.5,60.3,1,34.5,63.7,1,16.3]
[null,null,null,"Холодный",-10,-6.7,4.4,-19,-17.6,3.2,"-"]
["138. Одесса",48,1010,"Теплый",25,59,3.3,28.6,62,3.3,8.8]
[null,null,null,"Холодный",-6,-1.3,12,-18,-16.3,11,"-"]
["139. Олекминск",60,990,"Теплый",22.6,51.5,1,26.2,55.3,1,13.1]
[null,null,null,"Холодный",-38,-38.1,2.3,-51,-51.3,2,"-"]
["140. Оленек",68,990,"Теплый",18.1,45.2,1,27.6,46.9,1,13.2]
[null,null,null,"Холодный",-50,-50.2,1.2,-57,-57.4,2,"-"]
["141. Омск",56,990,"Теплый",22.4,49.4,3.7,27.7,53.6,3.7,12.1]
[null,null,null,"Холодный",-23,-22.2,6,-37,-36.8,5,"-"]
["142. Онега",64,990,"Теплый",18.4,46.1,2.7,24.5,51.5,2.7,10.2]
[null,null,null,"Холодный",-20,-18.8,5.2,-31,-30.6,3.7,"-"]
["143. Орел",52,990,"Теплый",23.1,49.8,3.9,27.7,53.6,3.9,11.5]
[null,null,null,"Холодный",-13,-10.5,5.2,-26,-25.3,5,"-"]
["144. Оренбург",52,990,"Теплый",26.9,51.9,3.9,31.4,54.4,3.9,13.5]
[null,null,null,"Холодный",-20,-18.8,4.6,-31,-30.5,4.9,"-"]
["145. Орск",52,990,"Теплый",26.3,49.4,1,31.1,52.8,1,14]
[null,null,null,"Холодный",-21,-19.7,4.6,-31,-28.5,3.9,"-"]
["146. Охотск",60,1010,"Теплый",17.2,40.2,1,18.4,41.4,1,5.4]
[null,null,null,"Холодный",-26,-25.5,7.7,-33,-32.6,6.3,"-"]
["147. Павлодар",52,990,"Теплый",23.6,51.5,1,31.6,54,1,12]
[null,null,null,"Холодный",-23,-22.2,5.5,-37,-36.8,4,"-"]
["148. Пенза",52,990,"Теплый",23.8,51.1,1,28.4,54,1,10.9]
[null,null,null,"Холодный",-17,-15.5,4.4,-29,-28.8,3.8,"-"]
["149. Пермь",56,990,"Теплый",21.8,50.2,1,26.3,53.2,1,11.1]
[null,null,null,"Холодный",-20,-18.9,1.9,-35,-34.9,4.2,"-"]
["150. Петрозаводск",60,1010,"Теплый",18.6,46.1,3.2,23.1,50.2,3.2,9.5]
[null,null,null,"Холодный",-15,-11.7,5,-29,-28.5,3.7,"-"]
["151. Петропавловск",56,990,"Теплый",23,49,4.5,28.8,51.9,4.5,12.1]
[null,null,null,"Холодный",-24,-23,5,-36,-36.2,6,"-"]
["152. Петропавловск-Камчатский",52,990,"Теплый",15.7,37.7,1,18,39.8,1,5.8]
[null,null,null,"Холодный",-10,-6.7,8.5,-20,-19.2,8.7,"-"]
["153. Полоцк",56,990,"Теплый",21.4,49.4,3.8,25.8,52.8,3.8,11]
[null,null,null,"Холодный",-11,-8,4.7,-26,-25.5,3.3,"-"]
["154. Полтава",48,990,"Теплый",24.5,53.6,4.4,29.4,56.5,4.4,11.5]
[null,null,null,"Холодный",-11,-8,6.8,-23,-21.9,6.2,"-"]
["155. Порецкое",56,990,"Теплый",23.8,51.1,1,28,54,1,12.3]
[null,null,null,"Холодный",-17,-15.5,5.2,-31,-30.6,4,"-"]
["156. Поти",44,1010,"Теплый",26,69.1,1,29.6,71.6,1,7.6]
[null,null,null,"Холодный",3,10.5,5.2,-3,1.7,4,"-"]
["157. Псков",56,1010,"Теплый",20.6,48.1,3.5,25.6,51.9,3.5,10.6]
[null,null,null,"Холодный",-11,-8,4.1,-26,-25.5,3.9,"-"]
["158. Пярну",60,1010,"Теплый",20,47.3,2.5,24.3,51.1,2.5,8.2]
[null,null,null,"Холодный",-9,-5.4,5.6,-22,-20.9,4.8,"-"]
["159. Пятигорск",44,990,"Теплый",26.3,61.5,1,30.6,63.6,1,11.5]
[null,null,null,"Холодный",-8,-4.2,6.3,-18,-16.3,5.3,"-"]
["160. Рига",56,1010,"Теплый",20.3,47.3,1,24.3,51.1,1,9.8]
[null,null,null,"Холодный",-8,-5.4,5.6,-20,-18.8,5.9,"-"]
["161. Репетек",40,990,"Теплый",37.8,57.8,1,43.2,61.1,1,19.1]
[null,null,null,"Холодный",-2,3.3,3,-12,0.5,1.2,"-"]
["162. Ровно",52,970,"Теплый",22.6,51.5,1,25.1,55.3,1,10.7]
[null,null,null,"Холодный",-9,-5.4,6.8,-21,-19.7,5.1,"-"]
["163. Ростов-на-Дону",48,990,"Теплый",27.3,57.4,3.6,31.9,60.7,3.6,12.5]
[null,null,null,"Холодный",-8,-4.2,12,-22,-20.9,8,"-"]
["164. Рязань",56,990,"Теплый",22.8,49.8,4.1,27.3,53.6,4.1,11.1]
[null,null,null,"Холодный",-16,-14.2,4.8,-27,-26.8,3,"-"]
["165. Салехард",68,1010,"Теплый",17.4,39.8,5.3,22,44.8,5.3,9]
[null,null,null,"Холодный",-29,-28.5,4,-42,-42,6.7,"-"]
["166. Самара",52,990,"Теплый",24.3,52.8,3.2,29.7,55.3,3.2,10.7]
[null,null,null,"Холодный",-18,-16.3,4.6,-30,-29.8,5,"-"]
["167. Самарканд",40,910,"Теплый",32.3,59.5,1,35,62.8,1,16.8]
[null,null,null,"Холодный",-3,2.1,2.2,-13,-10.9,1,"-"]
["168. Санкт-Петербург",60,1010,"Теплый",20.6,48.1,1,24.8,51.5,1,8.7]
[null,null,null,"Холодный",-11,-8,3.5,-26,-25.3,3,"-"]
["169. Саранск",56,990,"Теплый",23.5,51.1,1,27.7,54.4,1,11.6]
[null,null,null,"Холодный",-17,-15.5,3.4,-30,-29.6,3.8,"-"]
["170. Саратов",52,990,"Теплый",25.4,53.6,4.3,30.5,56.5,4.3,11.9]
[null,null,null,"Холодный",-16,-14.2,5.3,-27,-26.3,5,"-"]
["171. Севастополь",44,1010,"Теплый",25,60.7,2.3,29.4,64.5,2.3,8.5]
[null,null,null,"Холодный",0,7.1,10.2,-11,-8.4,9,"-"]
["172. Семипалатинск",52,970,"Теплый",27,51.5,1,32,54,1,14.1]
[null,null,null,"Холодный",-22,-19.7,3.5,-38,-38.1,2.7,"-"]
["173. Серафимович",48,1010,"Теплый",26.5,54.4,3.6,31.9,57.4,3.6,11.8]
[null,null,null,"Холодный",-13,-10.5,5.3,-25,-24.3,4.7,"-"]
["174. Симферополь",44,970,"Теплый",26.1,59.5,1,31.8,63.2,1,14]
[null,null,null,"Холодный",-4,1.3,3.2,-16,-14.2,8,"-"]
["175. Сковородино",52,950,"Теплый",24,52.3,1,25.6,58.6,1,15.3]
[null,null,null,"Холодный",-32,-31.8,3,-40,-39.9,3,"-"]
["176. Славянск",48,990,"Теплый",27.1,54.4,"-",31.2,58.2,"-",13.2]
[null,null,null,"Холодный",-10,-6.7,6.8,-23,-24.3,5.2,"-"]
["177. Смоленск",56,990,"Теплый",20.8,49,3.2,25.3,53.2,3.2,11.3]
[null,null,null,"Холодный",-13,-10.5,4.7,-26,-25.5,4.2,"-"]
["178. Сочи",44,1010,"Теплый",25.9,66.2,1,30.2,69.5,1,7.7]
[null,null,null,"Холодный",2,9.6,5.2,-3,2.1,4,"-"]
["179. Среднеколымск",68,1010,"Теплый",16.2,44.4,1,25.3,45.6,1,10.1]
[null,null,null,"Холодный",-41,-41,3.2,-51,-51.3,6.8,"-"]
["180. Стерлитамак",52,990,"Теплый",24.1,49.4,"-",28.8,54,"-",12.4]
[null,null,null,"Холодный",-20,-18.8,4.3,-36,-36,3.9,"-"]
["181. Сургут",60,990,"Теплый",19.6,49.4,4.5,26.2,53.2,4.5,9.7]
[null,null,null,"Холодный",-28,-27.6,4.4,-43,-43.2,4.3,"-"]
["182. Сыктывкар",60,990,"Теплый",20.3,49,5.4,25.7,52.8,4.6,11.1]
[null,null,null,"Холодный",-20,-18.8,5,-36,-36,3.5,"-"]
["183. Талды-Курган",44,930,"Теплый",28.7,51.5,1,33.5,56.1,1,15.9]
[null,null,null,"Холодный",-16,-14.2,3,-30,-29.7,1.3,"-"]
["184. Таллинн",60,1010,"Теплый",19,47.3,3.9,23.5,51.1,3.9,7.5]
[null,null,null,"Холодный",-9,-5.4,5.3,-22,-20.7,5.1,"-"]
["185. Тамбов",52,990,"Теплый",24.5,52.3,2.8,28.9,54.4,2.8,11.9]
[null,null,null,"Холодный",-15,-13,4.5,-28,-27.8,3,"-"]
["186. Тара",56,990,"Теплый",21.5,50.2,3.7,26.3,53.6,3.7,11.6]
[null,null,null,"Холодный",-26,-25.5,6.1,-40,-20.1,5,"-"]
["187. Тарту",60,990,"Теплый",20.8,48.6,4.6,25.3,52.8,4.6,10.2]
[null,null,null,"Холодный",-10,-6.7,4.5,-24,-23.2,4.3,"-"]
["188. Татарск",56,1010,"Теплый",22.8,49.4,3.9,27.5,53.2,3.9,12.2]
[null,null,null,"Холодный",-25,-24.3,5.5,-39,-38.8,5,"-"]
["189. Ташкент",40,930,"Теплый",33.2,58.2,1.4,35.7,62.8,1.4,16.9]
[null,null,null,"Холодный",-6,-2.5,2.7,-15,-13.4,1.4,"-"]
["190. Тбилиси",40,950,"Теплый",28.8,60.3,1,34.7,62.8,1,11.8]
[null,null,null,"Холодный",0,5.9,1,-8,-4.8,1,"-"]
["191. Тверь",56,990,"Теплый",21.7,49.4,1,26.6,52.8,1,11.5]
[null,null,null,"Холодный",-15,-13,4.7,-29,-27.6,3.2,"-"]
["192. Тернополь",48,970,"Теплый",22.1,52.8,1,26.8,57.4,1,11.8]
[null,null,null,"Холодный",-9,-5,7.1,-21,-19.7,5.1,"-"]
["193. Термез",36,970,"Теплый",36.3,61.5,1,39.8,64.9,1,18.8]
[null,null,null,"Холодный",2,9.2,3.3,-9,-6.7,2.6,"-"]
["194. Тобольск",60,990,"Теплый",21.2,49.8,4.1,26.4,54.4,4.1,9.7]
[null,null,null,"Холодный",-22,-20.9,5.5,-39,-39,4.6,"-"]
["195. Томск",56,990,"Теплый",21.7,49,1,25.9,52.8,1,11]
[null,null,null,"Холодный",-25,-24.3,4.7,-40,-40.2,3,"-"]
["196. Тула",56,990,"Теплый",22.2,50.2,3.4,27,53.6,3.4,11.4]
[null,null,null,"Холодный",-14,-11.7,4.5,-27,-26.6,3,"-"]
["197. Тургай",48,990,"Теплый",29,49.8,5,32.8,51.9,5,13.9]
[null,null,null,"Холодный",-22,-20.9,6.2,-32,-31.8,5.8,"-"]
["198. Туркестан",44,970,"Теплый",34.4,51.9,3.6,39.4,54,3.6,18.4]
[null,null,null,"Холодный",-8,-4.2,3.3,-22,-20.6,3,"-"]
["199. Туруханск",64,990,"Теплый",18.7,48.1,4,24.3,50.2,4,9.9]
[null,null,null,"Холодный",-33,-33.1,3.7,-50,-50.2,2.7,"-"]
["200. Тюмень",56,990,"Теплый",22.4,51.5,1,28,55.3,1,11]
[null,null,null,"Холодный",-21,-19.7,5.6,-37,-37.2,4.6,"-"]
["201. Ужгород",48,990,"Теплый",24.2,54.4,1,28.1,58.6,1,11.1]
[null,null,null,"Холодный",-6,-1.3,6,-18,-16.3,4.3,"-"]
["202. Улан-Удэ",52,930,"Теплый",23.7,49.8,1,29.7,54,1,12.9]
[null,null,null,"Холодный",-28,-27.6,3.4,-37,-37.1,3,"-"]
["203. Ульяновск",56,990,"Теплый",23.8,51.1,3.7,28.5,54.4,3.7,11.8]
[null,null,null,"Холодный",-18,-16.3,4.5,-31,-30.6,5,"-"]
["204. Умань",48,990,"Теплый",24.1,53.6,1,28.7,57.8,1,12.7]
[null,null,null,"Холодный",-9,-5,7.1,-22,-19.7,5.7,"-"]
["205. Уральск",52,1010,"Теплый",28.1,53.6,1,32.8,56.9,1,14.3]
[null,null,null,"Холодный",-18,-16.3,5.7,-31,-30.7,5.7,"-"]
["206. Урюпинск",52,990,"Теплый",26.2,52.8,1,31,56.5,1,13.2]
[null,null,null,"Холодный",-15,-13,5.9,-27,-26.5,5.3,"-"]
["207. Усть-Большерецк",52,1010,"Теплый",14.1,38.5,5.2,16,40.6,5.2,4.4]
[null,null,null,"Холодный",-15,-13,7.4,-25,-24.3,7.2,"-"]
["208. Усть-Каменогорск",48,970,"Теплый",26.4,51.1,1,31.6,54,1,14.2]
[null,null,null,"Холодный",-18,-16.3,2.7,-39,-39.1,2,"-"]
["209. Усть-Камчатск",56,1010,"Теплый",15.7,39.8,1,18,41,1,5.9]
[null,null,null,"Холодный",-16,-14.2,7.2,-27,-26.8,9.5,"-"]
["210. Усть-Мая",60,990,"Теплый",22.2,47.3,1,25.4,53.2,1,13.6]
[null,null,null,"Холодный",-45,-45.2,1,-54,-54.4,1,"-"]
["211. Усть-Хайрюзово",56,1010,"Теплый",15.8,40.2,1,18.2,41.4,1,7]
[null,null,null,"Холодный",-19,-17.6,7.3,-31,-30.8,7,"-"]
["212. Уфа",56,990,"Теплый",23.4,50.7,1,28,54.4,1,10.8]
[null,null,null,"Холодный",-19,-17.6,3.4,-35,-34.5,4.2,"-"]
["213. Фергана",40,930,"Теплый",32.2,62.4,1,36.2,65.7,1,15.1]
[null,null,null,"Холодный",-7,-3.3,2,-15,-13,7,"-"]
["214. Форт-Шевченко",44,1010,"Теплый",27.5,62,5.1,34.1,66.2,5.1,7.8]
[null,null,null,"Холодный",-7,-2.9,8.7,-15,-12.7,7.3,"-"]
["215. Хабаровск",48,990,"Теплый",24.1,60.7,4.6,28.4,65,4.6,8.5]
[null,null,null,"Холодный",-23,-22.2,8.4,-31,-30.8,6.8,"-"]
["216. Харагун",52,950,"Теплый",18.5,49.8,4.9,21.3,54,4.9,7.6]
[null,null,null,"Холодный",-20,-18.8,1.5,-30,-29.7,1,"-"]
["217. Харьков",52,990,"Теплый",25.1,52.8,1,29.4,56.1,1,11.6]
[null,null,null,"Холодный",-11,-8,6.7,-23,-22.2,6.1,"-"]
["218. Херсон",48,1010,"Теплый",29,57.8,1,30.6,61.5,1,12.7]
[null,null,null,"Холодный",-7,-2.9,9.9,-19,-17.3,8,"-"]
["219. Хибины",68,930,"Теплый",18.1,44.8,3.2,22,46.1,3.2,9.5]
[null,null,null,"Холодный",-19,-17.6,5.5,-30,-29.5,5.5,"-"]
["220. Целиноград",52,970,"Теплый",24.9,48.1,1,31,51.1,1,13.6]
[null,null,null,"Холодный",-22,-20.9,6.5,-35,-35.2,5.8,"-"]
["221. Чарджоу",40,970,"Теплый",35.2,59,4.3,39.5,62.8,4.3,14.3]
[null,null,null,"Холодный",-2,3.3,3,-13,-10.5,3.2,"-"]
["222. Чебоксары",56,990,"Теплый",22.9,51.1,"-",27,54.4,"-",9.9]
[null,null,null,"Холодный",-18,-16.3,5.4,-32,-31.8,4.8,"-"]
["223. Челябинск",56,990,"Теплый",22.8,48.1,3.2,27.3,52.3,3.2,10.6]
[null,null,null,"Холодный",-21,-18.8,5,-34,-33.5,4.8,"-"]
["224. Чердынь",60,990,"Теплый",20.7,48.1,4.6,25.9,51.9,4.6,10.1]
[null,null,null,"Холодный",-22,-20.9,5.4,-36,-35.2,8.6,"-"]
["225. Чернигов",52,990,"Теплый",23.2,51.5,1,27.8,54.4,1,11]
[null,null,null,"Холодный",-10,-6.7,4.2,-23,-21.9,3.8,"-"]
["226. Чита",52,930,"Теплый",24,49.4,1,25.2,53.2,1,14]
[null,null,null,"Холодный",-31,-29.7,1,-38,-38.1,1,"-"]
["227. Шадринск",56,990,"Теплый",23.3,48.1,"-",27.8,52.3,"-",12.7]
[null,null,null,"Холодный",-21,-19.7,4.7,-37,-33.9,5.2,"-"]
["228. Эльтон",48,1010,"Теплый",29.4,56.5,1,33.2,59.6,1,13.5]
[null,null,null,"Холодный",-14,-11.7,9,-26,-25.6,8,"-"]
["229. Якутск",62,990,"Теплый",23,48.1,1,28.6,52.3,1,14.1]
[null,null,null,"Холодный",-45,-45.2,1,-55,-55.3,1,"-"]
["230. Ялта",44,1010,"Теплый",26.3,61.1,1,30.5,64.5,1,8.4]
[null,null,null,"Холодный",1,8,9,-6,-2.5,8.7,"-"]
["231. Ямск",60,1010,"Теплый",15.9,39.8,1,18.4,41.1,1,6.8]
[null,null,null,"Холодный",-23,-22.2,9.2,-36,-36.2,9.2,"-"]
["232. Ярославль",56,990,"Теплый",21.6,49.8,3.9,25.8,52.8,3.9,10.3]
[null,null,null,"Холодный",-16,-14.2,4.8,-31,-30.6,4,"-"]
[]
["Республика, край, область, пункт","Температура воздуха наиболее холодных суток, °С, обеспеченностью",null,"Температура воздуха наиболее холодной пятидневки, °С, обеспеченностью",null,"Температура воздуха, °С, обеспеченностью 0,94","Абсолютная минимальная температура воздуха, °С","Средняя суточная амплитуда температуры воздуха наиболее холодного","Продолжительность, сут, и средняя температура воздуха, °С, периода со средней суточной температурой воздуха",{"$nulls":5},"Средняя месячная относительная влажность воздуха наиболее холодного ","Средняя месячная относительная влажность воздуха в 15 ч. наиболее","Количество осадков за ноябрь-март, мм","Преобладающее направление ветра  за декабрь-февраль","Максимальная из средних скоростей ветра по румбам за январь, м/с","Средняя скорость ветра, м/с, за период со средней суточной температ"]
[{"$nulls":7},"месяца, ","£ 0°С",null,"£ 8°С",null,"£ 10°С",null,"месяца, %","холодного",null,null,null,"урой"]
[null,0.98,0.92,0.98,0.92,null,null,"°С","продолжительность","средняя температура","продолжительность","средняя температура","продолжительность","средняя температура",null,"месяца, %.",null,null,null,"воздуха £ 8 °С"]
[1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,16,17,18,19,20]
[]
["РОССИЙСКАЯ ФЕДЕРАЦИЯ"]
["Республика Адыгея"]
["Майкоп",-27,-22,-21,-19,-6,-34,9,40,-1,148,2.3,169,3.1,79,72,276,"Ю",5.7,3]
["Республика Алтай"]
["Алейск",-44,-42,-41,-38,-23,-46,9.5,164,-11.5,216,-7.8,230,-6.7,80,78,130,"ЮЗ",6.8,"—"]
["Барнаул",-44,-42,-41,-39,-23,-52,10.2,168,-11.4,221,-7.7,235,-6.7,79,76,145,"ЮЗ",5.9,3.9]
["Беля",-27,-26,-25,-23,-14,-35,5.9,149,-6,223,-2.7,242,-1.7,59,55,121,"ЮВ",7,4.5]
["Бийск",-45,-43,-41,-38,-23,-51,11,168,-11.6,222,-7.8,236,-6.7,81,79,165,"ЮЗ",4.7,3.7]
["Змеиногорск",-44,-41,-40,-38,-20,-49,10.5,163,-10.2,217,-6.6,232,-5.6,78,74,204,"Ю",6.9,3.7]
["Катанда",-43,-42,-42,-40,-28,-48,12.3,175,-14,237,-9.2,258,-7.8,81,79,81,"С",1.8,1.7]
["Кош-Агач",-49,-48,-48,-46,-36,-55,13,199,-18.1,262,-12.8,282,-11.2,76,74,20,"В",4.1,1.7]
["Онгудай",-42,-41,-40,-38,-26,-46,11.1,168,-13,231,-8.3,249,-7.3,79,71,46,"З",2.3,9.1]
["Родино",-44,-42,-41,-38,-23,-49,9.6,165,-11.8,215,-8.1,228,-7,80,79,76,"ЮЗ",6,4.8]
["Рубцовск",-44,-41,-41,-38,-23,-49,9.7,162,-11,213,-7.4,227,-6.4,80,79,115,"Ю",7.9,"—"]
["Славгород",-43,-40,-41,-37,-24,-48,9.2,166,-12.5,215,-8.7,228,-7.7,81,80,73,"ЮЗ",6.2,5.2]
["Тогул",-43,-41,-40,-37,-22,-48,8.6,170,-11,225,-7.3,240,-6.3,79,77,145,"ЮЗ","—","—"]
["Амурская область"]
["Архара",-42,-40,-38,-36,-32,-50,11.7,171,-16.4,219,-11.8,233,-10.6,77,73,75,"СЗ",3.4,3.2]
["Белогорск",-43,-40,-41,-37,-32,-48,10,174,-16.4,223,-11.9,236,-10.7,76,73,53,"СЗ",2.7,2.9]
["Благовещенск",-38,-37,-36,-34,-29,-45,10.5,170,-14.8,218,-10.6,232,-9.4,72,64,47,"СЗ",3.4,2.9]
["Бомнак",-46,-45,-44,-42,-37,-52,11.1,194,-19.2,242,-14.7,259,-13.1,73,66,54,"СВ",1.9,1.4]
["Братолюбовка",-41,-40,-39,-37,-33,-51,11.2,179,-17.1,229,-12.4,242,-11.2,75,72,58,"СЗ","—","—"]
["Бысса",-44,-43,-42,-41,-36,-51,14.8,186,-18.4,236,-13.6,252,-12.2,76,69,71,"ЮВ",1.3,"—"]
["Гош",-46,-44,-43,-42,-36,-52,15.9,183,-18.9,233,-14,247,-12.7,73,66,50,"З",1.5,"—"]
["Дамбуки",-47,-46,-46,-43,-36,-54,13.6,196,-18.8,244,-14.3,261,-12.8,66,59,57,"СЗ",5.2,1.7]
["Ерофей Павлович",-43,-42,-40,-38,-33,-51,15.6,195,-17,245,-12.7,262,-11.3,79,71,47,"С","—",2]
["Примечание — Абсолютная минимальная температура воздуха выбрана из ряда наблюдений за период 1881—1985 гг.; в СНиП 2.01.01-82 «Строительная климатология и геофизика» абсолютная минимальная температура воздуха для отдельных пунктов определялась методом приведения."]
["Завитинск",-41,-39,-38,-36,-32,-50,9.5,176,-16.4,226,-11.8,240,-10.7,79,74,78,"СЗ",3.3,"—"]
["Зея",-46,-44,-43,-42,-35,-52,14.7,190,-18.3,238,-13.8,254,-12.4,69,63,35,"—",3.5,"—"]
["Норский Склад",-46,-44,-44,-43,-37,-55,15,183,-19.2,232,-14.3,246,-13,74,68,58,"СВ",2.1,1.6]
["Огорон",-43,-41,-41,-40,-34,-50,10.4,198,-17.6,247,-13.3,265,-11.7,70,64,64,"С",3.2,2.5]
["Поярково",-43,-40,-39,-37,-32,-50,12.5,173,-16.5,222,-11.9,235,-10.7,76,70,53,"З",3.4,"—"]
["Свободный",-44,-42,-41,-39,-33,-52,12.2,179,-17.1,229,-12.4,242,-11.3,70,63,66,"СЗ","—","—"]
["Сковородино",-46,-44,-43,-40,-34,-52,15.1,198,-17.8,247,-13.4,264,-12,74,66,40,"СЗ",4.7,2.4]
["Средняя Нюкжа",-52,-49,-47,-45,-40,-58,13.3,213,-20.8,262,-16.1,278,-14.7,76,72,77,"ЮВ","—","—"]
["Тыган-Уркан",-43,-41,-38,-37,-31,-50,12.8,196,-16.5,245,-12.4,262,-11,69,61,52,"СЗ",5.2,2.6]
["Тында",-48,-46,-44,-42,-37,-54,12.5,208,-19.2,258,-14.7,274,-13.3,75,71,62,"З",5.3,2.9]
["Унаха",-48,-45,-44,-42,-35,-55,16.1,206,-18.4,255,-14,271,-12.6,67,59,64,"СЗ","—","—"]
["Усть-Нюкжа",-47,-46,-45,-44,-37,-51,8.2,204,-19.5,253,-14.9,269,-13.5,76,72,54,"С",4.3,1.6]
["Черняево",-45,-43,-42,-41,-33,-52,13,184,-17.2,235,-12.7,249,-11.5,72,67,40,"СЗ",1.9,"—"]
["Шимановск",-43,-41,-40,-38,-33,-52,13.4,182,-17,233,-12.5,246,-11.3,"—",70,60,"СЗ",2.3,2.4]
["Экимчан",-47,-45,-45,-44,-38,-52,11.4,202,-19.1,253,-14.4,270,-12.8,74,66,73,"В",2.2,1.2]
["Архангельская область"]
["Архангельск",-39,-37,-34,-31,-18,-45,7.8,177,-8,253,-4.4,273,-3.4,86,83,188,"ЮВ",5.9,3.7]
["Борковская",-49,-47,-44,-42,-23,-55,10,203,-10.5,277,-6.6,297,-5.6,83,83,191,"ЮЗ","—",2.6]
["Емецк",-39,-38,-35,-33,-19,-48,7.6,175,-8.3,249,-4.7,268,-3.7,85,85,150,"ЮВ","—",3.9]
["Кой нас",-49,-47,-41,-40,-22,-52,9,190,-9.8,264,-5.9,282,-5,84,82,190,"Ю",3.7,3]
["Мезень",-40,-39,-36,-35,-19,-49,7.8,196,-8.8,272,-5.2,293,-4.2,86,86,133,"Ю",5.8,4.9]
["Онега",-38,-36,-35,-31,-17,-43,7.3,170,-7.5,248,-3.9,269,-3,85,84,200,"ЮВ",4.6,3.4]
["Астраханская область"]
["Астрахань",-27,-26,-24,-23,-12,-33,7.3,106,-4.2,167,-1.2,184,-0.3,84,71,82,"В",4.8,4.3]
["Верхний Баскунчак",-32,-30,-28,-26,-14,-37,7.2,124,-6.1,179,-3,191,-2.2,84,84,117,"В",5.9,4.3]
["Республика Башкортостан"]
["Белорецк",-39,-37,-37,-34,-21,-45,8.5,171,-10.3,231,-6.5,249,-5.4,79,76,132,"ЮЗ",5.6,3.5]
["Дуван",-42,-39,-39,-36,-21,-50,7.7,169,-9.9,228,-6.3,244,-5.2,80,77,120,"ЮЗ","—",3.6]
["Мелеуз",-42,-39,-38,-35,-20,-45,8.9,158,-9.9,210,-6.4,224,-5.4,80,78,151,"Ю",5,3.4]
["Уфа",-41,-39,-38,-35,-20,-49,8.3,159,-9.4,213,-5.9,227,-5,81,76,195,"Ю",5.5,3.5]
["Янаул",-44,-40,-41,-37,-20,-51,8.2,169,-9.4,226,-6,243,-5,82,82,126,"ЮЗ",7.6,4.6]
["Белгородская область"]
["Белгород",-29,-28,-27,-23,-13,-35,5.9,126,-5,191,-1.9,209,-1,84,84,191,"ЮЗ",5.9,5.3]
["Брянская область"]
["Брянск",-34,-30,-30,-26,-14,-42,6.6,134,-5.6,205,-2.3,223,-1.4,85,84,177,"ЮВ",6.3,4.7]
["Республика Бурятия"]
["Бабушкин",-33,-30,-30,-28,-21,-38,8.8,175,-9.9,254,-5.6,275,-4.4,77,72,178,"З","—",4.2]
["Баргузин",-46,-44,-44,-42,-32,-52,9.9,185,-16.3,241,-11.5,258,-10.2,76,76,104,"З","—",3]
["Багдарин",-46,-44,-44,-42,-34,-51,16.3,209,-17.8,267,-13,284,-11.7,76,69,18,"СЗ","—",1.4]
["Кяхта",-44,-37,-41,-35,-27,-46,10.4,174,-13.4,232,-9,248,-7.9,74,62,28,"Ю",4,1.6]
["Монды",-38,-36,-36,-33,-25,-48,16,198,-12.2,266,-8.1,284,-6.9,65,51,20,"З",5.2,2.5]
["Нижнеангарск",-38,-36,-35,-33,-28,-47,7.8,197,-13.8,258,-9.6,276,-8.4,74,71,80,"СВ","—",2]
["Сосново -Озерское",-42,-40,-41,-38,-30,-48,11.4,202,-14.8,261,-10.6,276,-9.5,75,73,23,"ЮЗ","—",3.7]
["Уакит",-43,-42,-42,-40,-33,-48,10.4,217,-17.1,274,-12.7,290,-11.4,74,70,26,"СЗ","—","—"]
["Улан-Удэ",-46,-40,-40,-37,-30,-51,11.1,179,-15,237,-10.4,253,-9.2,74,68,36,"З",2.8,2.5]
["Хоринск",-44,-41,-43,-39,-31,-49,12.7,184,-15.4,241,-10.8,257,-9.6,75,72,25,"З","—","—"]
["Владимирская область"]
["Владимир",-38,-34,-32,-28,-16,-48,6.3,148,-6.9,213,-3.5,230,-2.6,84,83,194,"Ю",4.5,3.4]
["Муром",-39,-35,-33,-30,-16,-45,6.4,150,-7.4,214,-4,230,-3.1,84,83,166,"Ю","—",4.1]
["Волгоградская область"]
["Волгоград",-33,-30,-28,-25,-14,-35,5.6,117,-5.4,178,-2.2,190,-1.5,85,83,174,"СВ",8.1,4.4]
["Котельниково",-32,-29,-27,-24,-12,-38,6.8,112,-4.7,176,-1.6,190,-0.8,85,84,161,"В",4.2,4.1]
["Эльтон",-32,-31,-29,-26,-15,-36,7.4,128,-6.7,181,-3.6,194,-2.8,83,82,127,"В",4.6,4.6]
["Вологодская область"]
["Вологда",-42,-37,-38,-32,-17,-47,7.2,160,-7.7,231,-4.1,250,-3.1,85,82,171,"ЮЗ",6,4.4]
["Вытегра",-40,-36,-35,-32,-16,-49,7.1,159,-6.9,235,-3.4,256,-2.4,84,83,201,"ЮВ",5.3,3.6]
["Никольск",-42,-39,-38,-34,-18,-48,8,166,-8.6,236,-4.9,256,-3.8,84,84,177,"Ю","—",3]
["Тотьма",-39,-37,-36,-32,-18,-46,7.3,165,-8.2,235,-4.5,255,-3.4,86,86,199,"ЮЗ",4.5,3.6]
["Воронежская область"]
["Воронеж",-32,-31,-28,-26,-15,-37,6.7,134,-6.3,196,-3.1,212,-2.2,83,76,172,"З",5.1,4.2]
["Республика Дагестан"]
["Дербент",-16,-13,-11,-9,-3,-19,5.2,0,null,138,3.7,161,4.5,84,82,179,"СЗ",5.2,3.1]
["Махачкала",-21,-19,-17,-14,-5,-25,5.7,37,-0.4,148,2.7,167,3.4,83,79,185,"СЗ",8.5,5.8]
["Ивановская область"]
["Иваново",-38,-34,-34,-30,-17,-45,7.1,152,-7.4,219,-3.9,236,-2.9,85,84,209,"Ю",4.9,4.2]
["Кинешма",-39,-35,-33,-31,-17,-45,6.4,155,-7.6,221,-4.1,238,-3.2,84,83,268,"ЮЗ","—",4.1]
["Иркутская область"]
["Алыгджер",-41,-39,-38,-36,-22,-47,11.3,187,-10.8,264,-6.4,284,-5.3,64,59,63,"Ю",3.8,"—"]
["Бодайбо",-52,-50,-50,-47,-36,-55,9,200,-18.7,254,-13.9,270,-12.6,80,78,113,"—","—",1.4]
["Братск",-47,-46,-46,-43,-26,-44,8.2,188,-12.7,249,-8.6,266,-7.5,81,78,95,"ЮВ",3.4,2.1]
["Верхняя Гутара",-42,-40,-40,-37,-25,-47,17,200,-12.1,273,-7.7,292,-6.6,75,61,44,"ЮЗ","—",1.7]
["Дубровское",-53,-52,-52,-50,-34,-55,9.2,200,-16.9,257,-12.3,272,-11.1,78,76,143,"—","—","—"]
["Ербогачен",-57,-54,-53,-51,-36,-61,11.6,213,-19.3,264,-14.8,278,-13.6,79,79,101,"ЮЗ",3.1,2]
["Жигалово",-51,-49,-49,-47,-33,-54,12.4,193,-17.2,252,-13.3,268,-11,79,76,75,3,"—",1]
["Зима",-47,-45,-43,-42,-28,-50,11.8,179,-14.4,239,-9.7,257,-8.5,80,76,92,"СЗ",4.9,2.1]
["Ика",-56,-53,-51,-50,-34,-58,11.8,206,-17.7,262,-13,278,-11.8,77,77,57,"ЮЗ","—","—"]
["Илимск",-50,-49,-48,-45,-30,-59,11.8,195,-15.6,255,-11,270,-9.8,79,76,109,"В","—",1.8]
["Иркутск",-40,-38,-38,-36,-26,-50,10.5,177,-13,240,-8.5,258,-7.3,80,78,87,"ЮВ",2.9,2.3]
["Ичера",-56,-54,-53,-50,-33,-60,11.9,200,-17.5,254,-12.9,270,-11.6,78,76,131,"Ю","—",1.6]
["Киренск",-55,-53,-53,-49,-32,-58,12.2,197,-16.8,251,-12.3,266,-11.1,78,77,132,"ЮЗ",4.4,1.9]
["Мама",-50,-49,-48,-46,-34,-56,7.4,198,-17.3,255,-12.6,271,-11.3,77,76,179,"ЮВ","—",2.7]
["Марково",-53,-51,-51,-49,-33,-55,11.1,194,-16.9,250,-12.3,265,-11,78,76,117,"З",4.2,1.8]
["Наканно",-59,-57,-56,-54,-40,-61,11.7,218,-21.3,268,-16.5,283,-15.2,77,77,94,"—","—",1.8]
["Невон",-52,-50,-50,-48,-30,-56,11.3,193,-15.8,253,-11.1,269,-9.9,78,76,103,"ЮЗ","—",2.1]
["Непа",-55,-52,-51,-50,-33,-58,11.1,206,-17.4,261,-12.9,277,-11.6,78,77,100,"ЮВ","—",2]
["Орлинга",-50,-49,-48,-46,-32,-55,11.6,195,-16.3,253,-11.6,270,-10.4,80,77,101,"Ю","—",1.4]
["Перевоз",-51,-50,-48,-46,-31,-56,9.6,206,-16.9,262,-12.4,277,-11.2,73,71,41,"СЗ","—",1.9]
["Преображенка",-55,-53,-51,-50,-34,-60,10.5,207,-17.8,259,-13.3,274,-12.1,78,77,124,"—","—",2.6]
["Слюдянка",-32,-31,-30,-28,-22,-40,8.8,177,-11,254,-6.4,274,-5.3,76,68,50,"ЮЗ",1.5,"—"]
["Тайшет",-46,-45,-42,-40,-25,-50,10.8,179,-12.6,240,-8.3,257,-7.2,78,75,125,"З",6.4,3.1]
["Тулун",-45,-44,-42,-40,-26,-54,12.3,184,-13.5,247,-9,265,-7.8,80,70,79,"ЮВ",4.4,2]
["Усть-Ордынский — Бурятский АО",-46,-44,-44,-41,-30,-50,11.1,183,-15.8,243,-10.9,259,-9.6,80,79,46,"С","—",3.1]
["Кабардино-Балкарская Республика"]
["Нальчик",-24,-21,-20,-18,-9,-31,7,86,-2.5,168,0.6,187,1.4,86,81,136,"ЮЗ",2.5,1.8]
["Калининградская область"]
["Калининград",-29,-24,-21,-19,-8,-33,5,92,-1.9,193,1.1,216,1.9,85,82,280,"ЮВ",5.9,4.1]
["Республика Калмыкия — Хальмг Тангч"]
["Элиста",-30,-27,-25,-23,-12,-34,5.9,109,-4.2,173,-1.2,188,-0.4,90,90,132,"В",7.6,6.5]
["Калужская область"]
["Калуга",-34,-31,-30,-27,-15,-46,7.3,142,-6.2,210,-2.9,228,-1.9,83,83,213,"Ю",4.9,3.9]
["Камчатская область"]
["Апука — Корякский ДО",-36,-33,-31,-29,-18,-40,6.7,215,-8.9,300,-5.1,341,-3.4,76,75,"—","СВ","—","—"]
["Ича — Корякский АО",-30,-28,-27,-25,-18,-36,7.5,187,-7.8,282,-3.8,316,-2.4,78,75,349,"СВ","—","—"]
["Ключи",-43,-39,-40,-35,-21,-49,9,188,-10.1,257,-6.3,277,-5.1,82,81,492,"З",7.2,5.2]
["Козыревск",-41,-39,-39,-37,-23,-48,12,189,-11.3,256,-7.3,276,-6.1,82,81,234,"С","—","—"]
["Корф — Корякский АО",-36,-34,-32,-30,-21,-41,5.8,216,-10.2,281,-6.9,307,-5.6,68,67,"—","С","—",6.9]
["Лопатка, мыс",-18,-15,-15,-13,-10,-21,3.7,166,-3.5,306,0,365,1.3,84,83,"—","СЗ","—",10.1]
["Мильково",-43,-40,-40,-38,-25,-51,12.8,191,-12.5,256,-8.3,276,-7,82,80,291,"ЮЗ","—",1.6]
["Начики",-40,-39,-37,-36,-23,-51,14.8,201,-11.4,280,-7,308,-5.6,80,77,508,"СЗ",5.4,2.6]
["о.Беринга",-15,-14,-12,-11,-9,-24,4.6,158,-2.5,292,0.4,347,1.8,83,81,"—","СВ",10.1,7.6]
["Оссора — Корякский АО",-35,-34,-32,-31,-19,-41,8.9,209,-9.5,281,-6,308,-4.7,78,74,401,"С","—","—"]
["Петропавловск-Камчатский",-26,-22,-22,-20,-12,-32,5.5,162,-4.9,259,1.6,286,-0.6,67,66,863,"СЗ",9,2.9]
["Семлячики",-19,-18,-18,-16,-11,-25,4.8,167,-4.4,267,1.2,294,-0.2,65,63,"—","СВ",12.2,"—"]
["Соболево",-36,-34,-32,-30,-19,-45,13.5,189,-9,275,-4.8,307,-3.4,80,71,331,"СВ",3.8,"—"]
["Кроноки",-26,-22,-23,-20,-13,-36,7.3,179,-5.7,280,-2.2,312,-1.1,69,64,865,"С","—","—"]
["Ука",-39,-37,-36,-34,-21,-43,9.6,210,-10.3,281,-6.7,305,-5.5,82,81,407,"С",9.2,"—"]
["Октябрьская",-32,-30,-28,-25,-18,-42,9.2,180,-7.8,281,-3.5,318,-2,81,79,"—","СВ",6.4,6.8]
["Усть-Воямполка — Корякский АО",-42,-38,-37,-35,-22,-45,10.1,205,-10.8,295,-6.2,326,-5,83,83,224,"ЮВ",9.1,"—"]
["Усть-Камчатск",-37,-33,-30,-28,-16,-42,8.3,192,-7.6,277,-4,305,-2.8,81,80,664,"СЗ",7.1,4.9]
["Усть-Хайрюзово",-38,-35,-34,-31,-19,-42,9.1,195,-9.2,278,-5.2,311,-3.8,84,81,287,"СВ",8.1,5.5]
["Карачаево-Черкесская Республика"]
["Черкесск",-23,-21,-20,-18,-9,-29,8.3,85,-2.5,169,0.6,189,1.5,81,73,119,"В","—",3.2]
["Республика Карелия"]
["Кемь",-35,-32,-29,-27,-16,-40,7.1,174,-6.6,258,-3.2,281,-2.2,86,81,116,"З",5.7,5.1]
["Лоухи",-38,-36,-34,-31,-17,-47,8.7,184,-7.6,261,-4.2,281,-3.2,86,86,159,"ЮЗ","—",3.1]
["Олонец",-38,-35,-34,-29,-15,-54,8.4,156,-6.7,233,-3.2,255,-2.1,86,86,215,"ЮЗ",6.5,4.2]
["Паданы",-35,-34,-30,-29,-16,-46,7.1,169,-7.1,251,-3.5,272,-2.5,86,86,126,"З",4.6,3.8]
["Петрозаводск",-37,-34,-32,-29,-16,-38,6.6,160,-6.7,240,-3.1,261,-2.1,86,84,169,"ЮЗ",5.9,3.9]
["Реболы",-40,-37,-35,-32,-17,-45,7.8,174,-7.5,251,-4,271,-3,86,86,166,"ЮЗ","—",3.2]
["Кемеровская область"]
["Кемерово",-46,-42,-42,-39,-24,-50,9.8,175,-12.2,231,-8.3,246,-7.2,82,81,94,"Ю",6.8,4.9]
["Киселевск",-45,-42,-40,-39,-22,-50,8.5,169,-11.2,227,-7.3,242,-6.7,78,75,98,"ЮЗ",5.5,"—"]
["Кондома",-46,-44,-43,-40,-24,-52,13.6,175,-12,236,-7.8,254,-6.6,82,74,315,"ЮЗ",3.6,1.5]
["Мариинск",-47,-43,-44,-40,-23,-55,9.5,176,-11.6,235,-7.7,251,-6.6,80,77,99,"ЮЗ",5.7,"—"]
["Тайга",-44,-43,-42,-39,-24,-53,9.4,182,-12.2,240,-8.3,259,-7,81,79,171,"ЮЗ",6.6,"—"]
["Тисуль",-44,-43,-42,-40,-22,-48,10.4,176,-11.2,236,-7.3,253,-6.2,76,72,84,"ЮЗ","—","—"]
["Топки",-46,-42,-42,-39,-23,-51,7.7,180,-11.9,235,-8.2,251,-7.1,84,82,256,"Ю","—","—"]
["Устъ-Кабырза",-46,-44,-43,-41,-27,-54,13.8,182,-13.2,241,-9,259,-7.7,80,73,243,"З","—","—"]
["Кировская область"]
["Вятка",-39,-37,-35,-33,-19,-45,7.2,168,-9,231,-5.4,247,-4.8,86,82,167,"Ю",5.3,3.9]
["Нагорское",-42,-38,-36,-34,-20,-47,6.3,174,-9.5,239,-5.8,258,-4.7,87,87,172,"Ю","—",4.4]
["Савали",-40,-37,-37,-33,-19,-48,7.2,162,-9.1,220,-5.7,235,-4.7,82,80,229,"ЮЗ","—",4.7]
["Республика Коми"]
["Вендинга",-46,-44,-40,-39,-21,-52,8.7,183,-9.9,257,-5.9,277,-4.8,83,83,159,"Ю",3.8,3.1]
["Воркута",-46,-45,-43,-41,-26,-52,8.6,239,-12.8,306,-9.1,328,-7.8,81,81,178,"Ю",10.1,5.8]
["Объячево",-41,-39,-37,-34,-20,-47,7,172,-8.9,239,-5.3,259,-4.2,83,83,182,"Ю","—",3.8]
["Петрунь",-49,-47,-45,-43,-25,-53,9.3,224,-12.2,286,-8.6,307,-7.4,82,82,124,"ЮЗ","—",4.7]
["Печора",-51,-48,-46,-43,-25,-55,-8.4,206,-11.6,270,-7.9,288,-6.8,82,80,183,"ЮВ",5.6,3.8]
["Сыктывкар",-42,-41,-39,-36,-20,-47,7.8,177,-9.6,245,-5.8,265,-4.7,83,82,156,"ЮЗ",5.5,4.1]
["Троицко-Печорск",-47,-46,-43,-41,-23,-51,8.9,187,-11.1,258,-6.9,276,-5.9,83,80,181,"Ю",4.8,3.2]
["Усть-Уса",-47,-44,-43,-41,-23,-53,8.2,213,-11.2,279,-7.6,298,-6.5,85,85,151,"Ю","—",4.8]
["Усть-Цильма",-46,-44,-41,-39,-22,-52,8.4,201,-10.4,272,-6.6,290,-5.6,84,82,158,"В","—",4.5]
["Усть-Щугор",-53,-50,-49,-45,-25,-58,10,200,-12,268,-7.9,286,-6.8,82,82,198,"Ю",5,3.3]
["Ухта",-46,-44,-41,-39,-22,-49,7.4,189,-10.4,261,-6.4,280,-5.4,83,83,161,"ЮЗ",4.8,4.1]
["Костромская область"]
["Кострома",-40,-35,-34,-31,-17,-46,6.5,154,-7.4,222,-3.9,239,-3,85,81,169,"Ю",5.8,4.9]
["Чухлома",-41,-37,-36,-32,-18,-46,6.9,160,-7.9,230,-4.3,248,-3.3,85,84,175,"Ю"," ",3.9]
["Шарья",-40,-37,-36,-32,-18,-44,6.9,162,-8.3,228,-4.7,245,-3.7,86,85,273,"Ю",4.5,4.2]
["Краснодарский край"]
["Краснодар",-27,-23,-23,-19,-7,-36,8.1,49,-1.2,149,2,168,2.8,83,79,293,"В",3.2,2.9]
["Сочи",-9,-6,-5,-3,1,-18,6.5,0,null,72,6.4,121,7.4,72,66,786,"СВ",6.5,3.2]
["Тихорецк",-28,-25,-24,-22,-8,-32,6.4,74,-2.1,158,1.1,177,1.9,85,82,243,"В",6.8,5.2]
["Красноярский край"]
["Агата",-57,-55,-54,-53,-40,-59,11.9,237,-21.1,293,-16.3,312,-14.7,75,75,130,"СВ","—",2]
["Ачинск",-49,-45,-46,-41,-23,-60,9.2,178,-11.4,237,-7.6,254,-6.5,75,73,102,"ЮЗ",5.7,4.7]
["Байкит — Эвенкийский АО",-55,-53,-52,-50,-36,-57,10.9,211,-18.7,267,-13.9,283,-12.7,79,76,143,"ЮЗ",1.9,1.1]
["Боготол",-46,-43,-43,-39,-22,-53,7.8,178,-11.5,239,-7.6,257,-6.4,77,75,106,"ЮЗ","—",4.3]
["Богучаны",-51,-49,-49,-46,-29,-54,10.8,185,-15.6,245,-10.8,261,-9.6,76,75,85,"З",5.3,2.7]
["Ванавара — Эвенкийский АО",-57,-55,-52,-51,-35,-61,14.3,208,-18.3,262,-13.7,277,-12.4,79,77,107,"ЮЗ",3.3,1.8]
["Вельмо",-55,-54,-52,-49,-33,-59,13.2,207,-17.1,264,-12.5,280,-11.3,79,79,184,"З","—",1.6]
["Верхнеимбатск",-56,-52,-51,-48,-30,-57,9,213,-15.5,266,-11.5,283,-10.4,81,81,160,"ЮВ",4.3,3.6]
["Волочанка",-56,-53,-53,-50,-36,-59,9.5,253,-20.4,306,-16.1,326,-14.5,76,76,97,"З",6.1,3.8]
["Диксон — Таймырский АО",-45,-44,-42,-41,-31,-49,7.7,267,-16.7,365,-11.4,365,-11.4,86,86,"—","Ю",12.2,7.5]
["Дудинка — Таймырский АО",-53,-51,-48,-47,-33,-57,8.9,249,-18.3,303,-14.3,320,-13.1,76,76,136,"ЮВ",7.7,5.5]
["Енисейск",-53,-49,-50,-46,-27,-59,11.5,187,-13.9,245,-9.6,262,-8.4,79,78,141,"ЮВ",3.7,2.8]
["Ессей — Эвенкийский АО",-58,-56,-56,-55,-41,-60,13.3,246,-22.3,298,-17.7,316,-16.2,76,76,52,"СЗ",2.5,2.8]
["Игарка",-54,-53,-50,-49,-33,-60,9.2,235,-17.8,285,-13.9,303,-12.6,77,76,152,"ЮВ",7.8,4.1]
["Канск",-48,-46,-45,-42,-25,-51,10.4,178,-13.1,237,-8.8,254,-7.7,77,75,80,"З",7.3,3.7]
["Кежма",-54,-52,-51,-48,-32,-60,11.9,196,-17,252,-12.3,268,-11.1,78,77,79,"ЮЗ",4.5,2.7]
["Ключи",-45,-43,-40,-39,-23,-50,9.1,177,-11.5,240,-7.4,257,-6.3,75,71,156,"З","—",2.5]
["Красноярск",-48,-44,-43,-40,-22,-53,8.4,172,-11.1,234,-7.1,252,-5.9,71,70,85,"З",6.2,3.8]
["Минусинск",-46,-44,-42,-40,-26,-52,12.6,168,-13.1,225,-8.8,240,-7.6,77,75,55,"ЮЗ",4.8,1.8]
["Таимба",-55,-53,-53,-51,-35,-58,12.6,207,-18.5,264,-13.6,280,-12.3,76,73,101,"З","—",1.2]
["Троицкое",-51,-50,-49,-47,-28,-57,13.1,188,-14.4,251,-9.8,268,-8.6,76,73,121,"ЮЗ","—",1.9]
["Тура — Эвенкийский АО",-59,-57,-57,-55,-42,-60,12.7,220,-21.8,271,-16.9,286,-15.6,77,76,76,"СЗ",2.7,2]
["Туруханск",-59,-56,-54,-50,-32,-61,9,228,-16.6,279,-12.9,295,-11.7,78,74,149,"В",5.7,3.9]
["Хатанга — Таймырский АО",-55,-52,-52,-49,-38,-59,8.3,256,-21.6,311,-17.1,331,-15.4,79,79,91,"ЮЗ",5.8,4.8]
["Челюскин, мыс — Таймырский АО",-46,-44,-44,-41,-33,-49,7,311,-17.3,365,-14.7,365,-14.7,84,84,"—","ЮЗ",9.3,6.7]
["Ярцево",-53,-50,-50,-47,-29,-56,9.9,198,-14.9,254,-10.8,270,-9.6,79,78,170,"ЮВ",4.7,3.6]
["Курганская область"]
["Курган",-43,-41,-39,-37,-23,-48,8.4,164,-11.4,216,-7.7,230,-6.6,79,74,95,"Ю","—",4.4]
["Курская область"]
["Курск",-32,-30,-29,-26,-14,-35,6.3,132,-5.6,198,-2.4,216,-1.4,86,78,212,"ЮЗ",5.3,4.4]
["Липецкая область"]
["Липецк",-34,-31,-29,-27,-15,-38,6.8,141,-6.6,202,-3.4,218,-2.5,85,84,248,"ЮЗ",5.9,4.8]
["Ленинградская область"]
["Свирица",-37,-34,-32,-29,-15,-48,7.1,152,-6.4,228,-2.9,249,-1.9,86,86,231,"Ю",5.5,4.2]
["Тихвин",-37,-34,-32,-29,-15,-51,7.3,150,-6.3,227,-2.8,247,-1.8,85,85,210,"ЮЗ",5.5,3.6]
["Санкт-Петербург",-33,-30,-30,-26,-13,-36,5.6,139,-5.1,220,-1.8,239,-0.9,86,83,200,"ЮЗ",4.2,2.8]
["Магаданская область"]
["Аркагала",-56,-54,-54,-51,-42,-58,7.5,238,-24.1,289,-19,304,-17.7,73,72,45,"СЗ",6.4,2.5]
["Брохово",-41,-38,-38,-36,-25,-46,7.8,218,-12.7,285,-8.7,309,-7.4,77,74,211,"СЗ",11.7,5.6]
["Магадан (Нагаева, бухта)",-34,-32,-31,-29,-22,-35,5.2,214,-11.1,288,-7.1,316,-5.7,63,62,114,"СВ",7.3,5.2]
["Омсукчан",-56,-53,-54,-50,-38,-56,8,234,-21.9,286,-17.2,301,-15.9,74,74,80,"СВ",6.9,2.8]
["Палатка",-46,-41,-44,-38,-27,-44,9.1,222,-14.6,280,-10.7,301,-9.3,69,69,77,"В",7.6,3]
["Среднекан",-58,-53,-55,-52,-42,-56,6.3,229,-23.9,274,-19.3,287,-17.9,77,76,160,"ЮЗ",2,1.6]
["Сусуман",-59,-57,-58,-55,-43,-61,9.2,236,-25.1,286,-19.9,300,-18.5,73,73,50,"СВ",4.4,2]
["Республика Марий Эл"]
["Йошкар-Ола",-42,-39,-38,-34,-19,-47,8,159,-8.6,220,-5.1,236,-4.1,83,82,151,"Ю",6.2,4.7]
["Республика Мордовия"]
["Саранск",-38,-34,-34,-30,-17,-44,6.7,150,-7.9,209,-4.5,225,-3.6,83,83,155,"Ю",6.9,5.8]
["Московская область"]
["Дмитров",-36,-33,-32,-28,-15,-43,6.3,147,-6.5,216,-3.1,235,-2.2,84,84,183,"Ю",5.2,3.8]
["Кашира",-36,-32,-31,-27,-16,-44,6.3,147,-6.7,212,-3.4,229,-2.5,85,85,167,"З","—",5]
["Москва",-36,-32,-30,-28,-15,-42,6.5,145,-6.5,214,-3.1,231,-2.2,84,77,201,"ЮЗ",4.9,3.8]
["Мурманская область"]
["Вайда-Губа",-22,-20,-19,-17,-11,-27,5.8,176,-3.9,294,-0.7,331,0.4,84,83,217,"ЮЗ","—",6.9]
["Кандалакша",-38,-34,-35,-30,-17,-44,8.2,184,-7.4,266,-3.9,286,-3,85,81,132,"С",5.7,3.7]
["Ковдор",-45,-39,-41,-34,-19,-44,9.4,201,-8.7,276,-5.2,296,-4.3,83,80,159,"ЮЗ",3.5,2.4]
["Краснощелье",-41,-37,-35,-32,-19,-49,9.2,203,-8.4,279,-5,300,-4,85,85,141,"ЮЗ",3,2.8]
["Ловозеро",-40,-38,-33,-31,-19,-47,10.3,204,-8.5,281,-5,304,-4,85,85,114,"З",3.9,3.3]
["Мончегорск",-40,-38,-34,-30,-18,-44,9.5,193,-7.9,271,-4.5,291,-3.6,84,84,126,"Ю",5.7,4.3]
["Мурманск",-35,-32,-29,-27,-16,-39,6.2,187,-6.6,275,-3.2,302,-2.1,84,81,166,"Ю",7.5,5.6]
["Ниванкюль",-46,-40,-38,-36,-18,-45,9,191,-8.2,271,-4.6,292,-3.6,83,83,169,"ЮЗ","—",2.5]
["Пулозеро",-44,-39,-40,-35,-19,-47,9.3,198,-8.3,277,-4.8,299,-3.8,84,81,129,"Ю",2.5,3]
["Пялица",-32,-29,-28,-25,-16,-38,7.2,194,-6.5,298,-2.8,354,-0.9,86,86,133,"ЮЗ","—",5.7]
["Териберка",-26,-24,-23,-21,-13,-31,6.8,185,-5.2,286,-2,318,-0.9,79,79,149,"Ю","—",7.5]
["Терско-Орловский",-29,-27,-24,-22,-16,-38,6.5,200,-6.3,312,-2.5,365,-0.9,87,87,134,"ЮЗ","—",7.1]
["Умба",-37,-33,-34,-29,-17,-40,7.1,183,-7.1,265,-3.7,286,-2.8,86,85,164,"С","—",4.6]
["Юкспор",-31,-26,-27,-24,-18,-35,4.8,243,-8.1,340,-4.5,365,-3.7,92,91,389,"ЮЗ","—",5.1]
["Нижегородская область"]
["Арзамас",-40,-36,-35,-32,-17,-43,7,156,-8.1,216,-4.7,232,-3.8,85,84,238,"ЮЗ",7.5,4.1]
["Выкса",-38,-34,-33,-30,-16,-45,6.9,149,-7.3,212,-4,228,-3.1,85,82,232,"ЮЗ","—",3.4]
["Нижний Новгород",-38,-34,-34,-31,-17,-41,6.1,151,-7.5,215,-4.1,231,-3.2,84,80,172,"ЮЗ",5.1,3.7]
["Новгородская область"]
["Новгород",-38,-31,-33,-27,-14,-45,6.8,143,-5.7,221,-2.3,239,-1.4,85,85,176,"Ю",6.6,4.6]
["Новосибирская область"]
["Барабинск",-44,-42,-42,-39,-25,-48,9.2,177,-12.9,230,-9,243,-8,82,81,104,"ЮЗ",6.5,6.3]
["Болотное",-43,-42,-40,-39,-24,-51,8.3,175,-12.1,231,-8.2,246,-7.1,82,80,154,"ЮЗ",5.6,4.4]
["Карасук",-42,-41,-40,-37,-24,-46,9.5,169,-12.7,218,-8.9,232,-7.8,80,79,68,"ЮЗ","—","—"]
["Кочки",-45,-42,-43,-39,-25,-50,9.3,175,-12.9,228,-8.9,242,-7.9,81,80,90,"ЮЗ","—","—"]
["Купино",-42,-41,-41,-38,-25,-49,9,173,-12.9,224,-9,237,-8,80,79,59,"ЮЗ",6.7,5.7]
["Кыштовка",-46,-43,-42,-40,-25,-52,9.9,176,-12.9,231,-8.9,248,7.7,80,78,87,"ЮЗ","—","—"]
["Новосибирск",-44,-42,-42,-39,-24,-50,9.3,178,-12.4,230,-8.7,243,-7.7,80,77,104,"ЮЗ",5.7,3.9]
["Татарск",-43,-41,-40,-39,-25,-48,9.6,176,-12.8,229,-8.9,242,-7.9,83,82,84,"ЮЗ",4.8,4.9]
["Чулым",-44,-42,-42,-39,-25,-52,9.2,177,-12.7,230,-8.8,244,-7.8,80,79,111,"ЮЗ",6.2,"—"]
["Омская область"]
["Исиль-Куль",-43,-40,-39,-36,-24,-46,9.4,174,-12.3,225,-8.6,238,-7.7,82,80,78,"ЮЗ",5.2,"—"]
["Омск",-42,-41,-39,-37,-24,-49,8.8,169,"-12, 3",221,-8.4,235,-7.4,80,80,79,"ЮЗ",5.1,5]
["Тара",-46,-43,-42,-40,-25,-50,9.4,180,-12.8,234,-8.8,251,-7.6,83,81,157,"ЮВ",4.5,"—"]
["Черлак",-41,-40,-39,-37,-24,-44,8.8,168,-12.5,217,-8.7,231,-7.6,82,81,82,"ЮЗ",5.4,"—"]
["Оренбургская область"]
["Оренбург",-37,-36,-34,-31,-20,-43,8.1,153,-9.6,202,-6.3,215,-5.4,80,78,143,"В",5.5,4.5]
["Орловская область"]
["Орел",-35,-31,-30,-26,-15,-39,6.5,138,-6,205,-2.7,222,-1.8,86,86,178,"ЮЗ",6.5,4.8]
["Пензенская область"]
["Земетчино",-37,-34,-32,-29,-17,-43,7.9,148,-7.5,208,-4.2,223,-3.2,84,83,160,"ЮВ",6.2,4.3]
["Пенза",-35,-33,-32,-29,-17,-43,7.1,149,-7.9,207,-4.5,222,-3.6,84,84,221,"Ю",5.6,4.8]
["Пермская область"]
["Бисер",-44,-40,-39,-36,-23,-53,7.2,185,-10.9,254,-6.8,275,-5.6,86,83,267,"ЮЗ",3.5,3]
["Пермь",-42,-39,-38,-35,-20,-47,7.1,168,-9.5,229,-5.9,245,-4.9,81,78,192,"Ю",5.2,3.3]
["Приморский край"]
["Анучино",-35,-33,-33,-31,-25,-44,16.6,152,-12.2,203,-8.1,219,-6.8,73,59,120,"ЮЗ","—",2.2]
["Астраханка",-30,-29,-28,-26,-23,-40,10.6,148,-10.5,202,-6.6,218,-5.5,68,63,47,"ЮЗ","—",3.4]
["Богополь",-26,-25,-23,-21,-18,-30,9.3,142,-8.1,208,-4.2,229,-2.9,52,46,101,"СЗ","—",4.1]
["Владивосток",-27,-26,-25,-24,-18,-30,8.7,132,-7.7,196,-3.9,214,-2.7,61,58,129,"С",9,6.9]
["Дальнереченск",-36,-34,-33,-31,-25,-42,10.6,155,-12.6,205,-8.5,220,-7.2,73,66,87,"ЮЗ",4.1,3.5]
["Мельничное",-39,-34,-36,-32,-28,-49,16.2,169,-13.8,225,-9.3,241,-8,73,62,97,"З","—",2.4]
["Партизанск",-26,-24,-23,-22,-18,-30,9.9,139,-8.2,198,-4.5,216,-3.4,54,47,128,"С",8.4,5]
["Посьет",-23,-22,-20,-19,-16,-27,8.4,126,-6.5,192,-2.9,211,-1.8,52,46,66,"З","—",5]
["Преображение",-23,-21,-18,-17,-14,-27,9.4,124,-5.4,205,-1.6,230,-0.4,45,40,120,"С","—",4.5]
["Рудная Пристань",-25,-23,-21,-20,-17,-30,10,140,-7.2,219,-3.1,245,-1.8,46,40,124,"З",9.1,4.1]
["Чугуевка",-36,-35,-33,-32,-26,-47,17.2,158,-12.9,211,-8.6,227,-7.3,76,65,129,"СЗ","—",1.4]
["Псковская область"]
["Великие Луки",-34,-31,-31,-27,-14,-46,7.1,133,-5.4,212,-1.9,232,-0.9,84,78,177,"ЮВ",6.1,4.2]
["Псков",-35,-31,-30,-26,-12,-41,6.1,134,-4.9,212,-1.6,232,-0.7,86,81,179,"Ю",4.8,3.9]
["Ростовская область"]
["Миллерово",-31,-29,-27,-25,-13,-36,6.5,121,-5.2,184,-2.1,199,-1.2,84,83,188,"В",7.9,5.2]
["Ростов-на-Дону",-29,-27,-25,-22,-11,-33,6.1,102,-3.6,171,-0.6,188,0.2,85,77,219,"В",6.5,4.4]
["Таганрог",-28,-26,-25,-22,-10,-32,5.5,100,-3.3,167,-0.4,185,0.4,86,85,214,"В","—",4.6]
["Рязанская область"]
["Рязань",-36,-33,-30,-27,-16,-41,7,145,-6.8,208,-3.5,224,-2.6,83,84,172,"Ю",7.3,4.8]
["Самарская область"]
["Самара",-39,-36,-36,-30,-18,-43,6.7,149,-8.5,203,-5.2,217,-4.3,84,78,176,"ЮВ",5.4,4]
["Свердловская область"]
["Верхотурье",-46,-42,-41,-37,-22,-52,10.1,172,-10.8,236,-6.8,255,-5.6,78,76,118,"ЮВ","—",2.9]
["Екатеринбург",-42,-40,-38,-35,-20,-47,7.1,168,-9.7,230,-6,245,-5.3,79,73,114,"З",5,3.7]
["Ивдель",-46,-43,-43,-39,-24,-49,14.4,179,-11.6,245,-7.4,265,-6.2,78,75,112,"С","—",2.2]
["Саратовская область"]
["Саратов",-34,-33,-30,-27,-16,-37,6.9,142,-7.5,196,-4.3,210,-3.4,82,82,159,"СЗ",5.6,4.4]
["Сахалинская область"]
["Александровск-Сахалинский",-32,-30,-29,-27,-23,-41,9,168,-10.7,240,-6.2,260,-5.1,77,77,209,"ЮВ",7.8,5.2]
["Долинск",-29,-27,-25,-24,-18,-35,10.1,154,-8.1,231,-4,253,-2.9,78,67,348,"Ю",5.6,3.8]
["Кировское",-40,-39,-38,-36,-29,-48,14.4,183,-13.9,246,-9.2,263,-8,79,77,172,"СЗ",5.7,2.7]
["Корсаков",-25,-23,-23,-20,-16,-33,8,147,-6.7,232,-2.7,255,-1.9,76,66,223,"С",5.6,4.7]
["Курильск",-21,-17,-19,-15,-12,-27,6.9,122,-4,227,-0.2,257,0.8,80,75,466,"СЗ",11.9,6.4]
["Макаров",-27,-26,-24,-23,-19,-32,8.6,158,-8.6,241,-4.2,264,-3,66,59,212,"СЗ","—",3.4]
["Невельск",-20,-19,-18,-16,-14,-25,5.4,136,-5.4,218,-1.8,242,-0.7,72,66,332,"С",7,7]
["Ноглики",-36,-35,-33,-32,-25,-48,10.3,187,-11.7,260,-7.2,281,-6,76,69,149,"ЮЗ","—",4.2]
["Оха",-34,-32,-31,-29,-25,-39,6.8,194,-11.5,266,-7.3,286,-6.1,81,81,192,"СЗ",11.2,5.9]
["Погиби",-34,-33,-32,-30,-26,-44,8.4,191,-12.3,255,-8.2,273,-7.1,78,74,145,"СЗ","—",5.6]
["Поронайск",-34,-31,-30,-28,-22,-40,9.5,168,-10.2,249,-5.5,271,-4.4,69,64,194,"С",4.8,3.7]
["Рыбновск",-38,-36,-35,-33,-27,-45,8.5,193,-13.1,255,-8.9,272,-7.3,84,84,135,"СЗ","—",5.3]
["Холмск",-22,-21,-19,-18,-15,-25,5.9,140,-6,220,-2.3,244,-1.2,75,68,305,"ЮВ",10.7,6.4]
["Южно-Курильск",-16,-15,-13,-12,-11,-20,6.1,118,-3.7,228,0.1,253,1,74,73,410,"СЗ",8.5,6.1]
["Южно-Сахалинск",-28,-26,-25,-24,-19,-36,10.8,154,-8.4,230,-4.3,252,-3.1,81,71,263,"С",4.8,3.4]
["Республика Северная Осетия"]
["Владикавказ",-24,-20,-20,-18,-9,-28,9.5,91,-2.7,174,0.4,194,1.3,82,77,163,"ЮВ",3,1.6]
["Смоленская область"]
["Вязьма",-35,-32,-29,-27,-15,-43,6.3,145,-6.1,217,-2.8,236,-1.8,87,86,284,"ЮВ","—",4.4]
["Смоленск",-34,-31,-28,-26,-14,-41,6.1,141,-5.8,215,-2.4,234,-1.5,86,81,234,"Ю",6.8,5]
["Ставропольский край"]
["Арзгир",-30,-26,-25,-22,-10,-37,6.2,88,-3,163,0.1,180,1,86,83,115,"В",4.6,3.1]
["Ставрополь",-26,-23,-22,-19,-8,-31,6.6,83,-2,168,0.9,187,1.7,82,78,196,"З",7.4,4.4]
["Тамбовская область"]
["Тамбов",-34,-32,-30,-28,-16,-39,6.7,140,-7,201,-3.7,217,-2.7,84,83,194,"ЮВ",4.7,4]
["Республика Татарстан"]
["Бугульма",-40,-36,-36,-33,-19,-47,6.7,164,-9.2,221,-5.8,235,-4.9,86,85,264,"ЮЗ",7.5,5.4]
["Елабуга",-42,-38,-38,-34,-19,-47,7.7,158,-9,215,-5.5,229,-4.6,81,80,173,"ЮЗ",4.7,3.6]
["Казань",-41,-36,-36,-32,-18,-47,6.8,156,-8.7,215,-5.2,229,-4.3,83,79,135,"Ю",5.7,4.3]
["Тверская область"]
["Бежецк",-38,-34,-34,-31,-16,-52,6.8,151,-6.8,222,-3.4,240,-2.4,84,84,169,"ЮЗ",5,4]
["Тверь",-37,-33,-33,-29,-15,-50,7.2,146,-6.4,218,-3,236,-2,85,85,206,"ЮЗ",6.2,4.1]
["Ржев",-37,-33,-31,-28,-15,-47,6.6,144,-6.1,217,-2.7,236,-1.8,85,85,210,"Ю","—",3.6]
["Томская область"]
["Александровское",-49,-46,-44,-42,-27,-51,9.2,193,-13.6,252,-9.6,270,-8.3,82,81,110,"ЮВ",4.3,3.9]
["Колпашево",-47,-45,-44,-42,-26,-51,8.7,184,-13.4,243,-9.1,260,-7.9,80,79,119,"Ю",4.8,"—"]
["Средний Васюган",-47,-46,-44,-41,-25,-51,8.9,184,-13,244,-8.8,262,-7.6,80,79,147,"ЮЗ",3.8,3.5]
["Томск",-47,-44,-44,-40,-24,-55,8.7,179,-12.4,236,-8.4,253,-7.3,80,78,185,"Ю",5.6,4.7]
["Усть-Озерное",-48,-47,-46,-43,-27,-51,9.8,188,-13.8,248,-9.5,265,-8.3,81,79,155,"ЮЗ",3.6,"—"]
["Республика Тыва"]
["Кызыл",-49,-48,-48,-47,-37,-54,10.9,178,-20.1,225,-15,238,-13.7,73,69,58,"В",1.7,1.4]
["Тульская область"]
["Тула",-35,-31,-30,-27,-15,-42,6.8,140,-6.4,207,-3,224,-2.1,83,82,187,"ЮВ",4.9,4]
["Тюменская область"]
["Березово — Ханты-Мансийский АО",-50,-48,-45,-43,-27,-53,9.5,209,-13.6,267,-9.7,284,-8.6,84,83,110,"Ю",4.1,3.5]
["Демьянское",-47,-45,-44,-40,-24,-51,8.4,179,-12.1,241,-8,258,-6.8,81,80,115,"Ю",4.6]
["Кондинское — Ханты-Мансийский АО",-47,-44,-44,-40,-25,-49,8.9,183,-12.3,238,-8.6,256,-7.4,84,84,107,"Ю",4.7,3.8]
["Леуши",-46,-43,-44,-39,-23,-48,7.7,176,-11.4,238,-7.4,256,-6.2,81,80,100,"ЮЗ","—",4.6]
["Марресаля",-45,-44,-41,-39,-26,-50,6.8,252,-13.6,365,-8.1,365,-8.1,86,86,"—","ЮЗ","—",7]
["Надым",-53,-49,-47,-44,-30,-58,9.6,230,-15.3,283,-11.6,302,-10.4,78,78,118,"ЮЗ","—","—"]
["Октябрьское",-47,-45,-44,-41,-28,-49,8.2,200,-13,261,-9,280,-7.8,83,83,177,"В",5.2,"—"]
["Салехард",-48,-46,-43,-42,-29,-54,10.2,233,-15.3,292,-11.4,313,-10,84,84,101,"Ю",4.6,5.1]
["Сосьва",-51,-48,-49,-44,-28,-55,11.3,198,-13.9,261,-9.5,280,-8.3,80,80,127,"ЮВ","—","—"]
["Сургут — Ханты-Мансийский АО",-48,-47,-45,-43,-27,-55,9.7,200,-13.8,257,-9.9,274,-8.8,79,78,209,"ЮЗ",5.3,5]
["Тарко-Сале — Ямало-Ненецкий АО",-53,-50,-48,-46,-30,-55,9.9,228,-15.8,278,-12.2,294,-11,79,79,123,"Ю",5,3.7]
["Тобольск",-47,-43,-44,-39,-25,-52,9.5,177,-11.8,232,-8.1,249,-6.9,82,81,113,"ЮВ",6.3,4]
["Тюмень",-45,-42,-42,-38,-22,-50,9.2,169,-10.9,225,-7.2,240,-6.1,81,78,107,"ЮЗ",3.9,3.6]
["Угут",-49,-46,-45,-42,-26,-54,9.4,191,-13.3,251,-9.1,270,-7.9,82,80,123,"ЮЗ",4.4,"—"]
["Уренгой — Ямало-Ненецкий АО",-53,-50,-49,-46,-31,-56,9.9,236,-16.8,286,-13.1,304,-11.8,78,78,117,"ЮЗ","—","—"]
["Ханты-Мансийск — Ханты-Мансийский АО",-47,-45,-45,-41,-27,-49,8.7,192,-12.6,250,-8.8,270,-7.4,82,81,139,"ЮЗ",6.9,"—"]
["Удмуртская Республика"]
["Глазов",-42,-39,-38,-35,-20,-50,8,168,-9.7,231,-6,247,-5,85,84,248,"ЮЗ",4.9,"—"]
["Ижевск",-41,-38,-38,-34,-20,-48,6.9,162,-9.2,222,-5.6,237,-4.7,85,80,168,"ЮЗ",4.8,4]
["Сарапул",-41,-38,-38,-34,-19,-48,6.5,163,-9.4,220,-5.9,236,-4.9,84,81,228,"ЮЗ","—",3.5]
["Ульяновская область"]
["Сурское",-39,-36,-36,-31,-18,-46,9.3,152,-8.2,211,-4.8,226,-3.9,81,80,140,"ЮЗ","—",3.4]
["Ульяновск",-38,-36,-36,-31,-19,-48,7.4,155,-8.9,212,-5.4,228,-4.4,82,81,220,"—","—","—"]
["Хабаровский край"]
["Аян",-33,-31,-30,-28,-24,-37,7.2,203,-11.7,278,-7.4,300,-6.2,50,47,129,"СЗ","—",3.4]
["Байдуков",-37,-35,-34,-31,-27,-44,7.6,198,-12.8,255,-9,271,-7.9,81,80,"—","СЗ","—",5.9]
["Бикин",-38,-34,-35,-32,-27,-46,12.8,159,-13.3,208,-9.1,223,-7.8,76,66,96,"ЮВ",3.2,2]
["Бира",-37,-35,-34,-31,-27,-43,11,166,-13.4,220,-9.1,234,-7.9,70,64,85,"З","—","—"]
["Биробиджан",-38,-34,-35,-32,-28,-43,14.9,169,-14.8,219,-10.4,234,-9.2,74,65,84,"З","—","—"]
["Вяземский",-38,-34,-34,-31,-27,-48,11.9,163,-13.5,213,-9.3,227,-8.1,74,66,114,"ЮЗ",4.1,"—"]
["Гвасюги",-39,-37,-37,-35,-30,-52,17.3,174,-14.9,228,-10.4,242,-9.2,77,64,128,"—","—","—"]
["Гроссевичи",-26,-25,-23,-22,-20,-36,8.7,161,-8.8,248,-4.3,270,-3.2,54,47,"—","СЗ","—","—"]
["Де-Кастри",-30,-29,-28,-27,-24,-39,7.8,183,-11.4,256,-6.9,276,-5.8,68,61,131,"СЗ","—","—"]
["Джаорэ",-36,-32,-33,-30,-25,-42,7.7,191,-11.7,252,-7.9,268,-7,70,65,"—","—","—","—"]
["Екатерино-Никольское",-34,-32,-32,-30,-26,-43,10.7,162,-12.9,213,-8.8,228,-7.6,70,62,57,"СЗ",7.9,4.5]
["Комсомольск-на-Амуре",-38,-37,-37,-35,-31,-45,9.9,171,-15.4,223,-10.8,238,-9.5,79,77,93,"Ю",5.7,3.9]
["Нижнетамбовское",-40,-38,-38,-36,-31,-53,13.7,175,-15.5,229,-10.9,244,-9.6,78,72,119,"ЮЗ","—","—"]
["Николаевск-на-Амуре",-41,-38,-39,-35,-29,-47,8.5,189,-13.9,249,-9.6,263,-8.6,78,76,210,"З",4.5,"—"]
["Облучье",-40,-39,-37,-36,-31,-46,13.1,176,-16.2,227,-11.5,241,-10.4,79,70,82,"СЗ","—","—"]
["Охотск",-38,-36,-35,-33,-27,-45,6.3,213,-13.7,280,-9.5,304,-8.1,64,62,72,"С","—",4.2]
["Им.Полины Осипенко",-45,-43,-43,-41,-34,-52,14.7,183,-17.2,240,-12.2,255,-10.9,77,72,65,"С","—",2.6]
["Сизиман",-30,-29,-28,-26,-23,-43,11.6,181,-10.8,263,-6.2,283,-5.1,65,53,133,"З","—",3]
["Советская Гавань",-32,-30,-29,-27,-23,-40,11.3,166,-10.6,243,-6,264,-4.8,70,58,208,"ЮЗ","—","—"]
["Софийский Прииск",-47,-45,-44,-43,-37,-54,15,212,-19.2,268,-14.3,285,-12.9,76,70,65,"В",2.3,1.5]
["Средний Ургал",-43,-42,-41,-40,-36,-52,12.1,183,-18.4,238,-13.3,253,-11.9,76,69,57,"—","—","—"]
["Троицкое",-36,-34,-32,-31,-28,-47,8.7,166,-13.9,217,-9.7,231,-8.5,74,70,137,"Ю","—",4.2]
["Хабаровск",-37,-34,-34,-31,-27,-43,7.7,162,-13.4,211,-9.3,225,-8.1,75,71,116,"ЮЗ",5.9,5.3]
["Чумикан",-35,-34,-34,-32,-29,-43,5.3,198,-13.8,274,-8.8,292,-7.7,73,71,"—",3,10.3,6.3]
["Энкэн",-31,-30,-30,-28,-25,-41,6.2,206,-12,281,-7.7,303,-6.5,48,45,"—","СЗ","—",4.8]
["Республика Хакассия"]
["Абакан",-44,-42,-41,-40,-25,-47,10.8,165,-14.7,225,-9.7,242,-8.4,79,75,40,"—","—",2.8]
["Шира",-43,-40,-39,-38,-24,-49,10.5,174,-11.9,236,-7.7,254,-6.6,73,70,36,"ЮЗ",4.1,2.5]
["Челябинская область"]
["Челябинск",-39,-38,-35,-34,-21,-48,9.4,162,-10.1,218,-6.5,233,-5.5,78,78,104,"ЮЗ",4.5,3]
["Чеченская Республика"]
["Грозный",-23,-22,-20,-18,-9,-32,7.1,77,-2.2,160,0.9,178,1.7,89,81,128,"СЗ",3.5,2]
["Читинская область"]
["Агинское",-42,-38,-40,-36,-28,-48,13.9,182,-14.8,238,-10.4,255,-9.1,72,67,19,"З","—",2.9]
["Акша",-41,-38,-36,-34,-28,-47,14.7,179,-14,237,-9.6,254,-8.3,73,65,21,"СЗ",5.2,2.2]
["Александровский Завод",-43,-41,-40,-38,-32,-48,12.1,194,-16.6,250,-12,267,-10.6,80,75,38,"ЮЗ","—","—"]
["Борзя",-45,-42,-44,-40,-32,-52,13.9,183,-16.5,236,-12,250,-10.7,78,78,21,"СВ","—",3.1]
["Дарасун",-40,-37,-38,-34,-27,-48,13.9,188,-13.7,247,-9.5,265,-8.2,72,64,28,"СЗ","—",2]
["Калакан",-51,-49,-49,-47,-40,-56,15.6,209,-20.9,260,-16,276,-14.5,74,67,27,"З","—",1]
["Красный Чикой",-44,-42,-42,-39,-31,-48,12.5,184,-15.8,244,-10.9,262,-9.5,78,74,29,"З","—",1.5]
["Могоча",-47,-45,-43,-41,-35,-53,15.2,201,-18.1,254,-13.4,271,-12,76,76,32,"СЗ",5.2,1.8]
["Нерчинск",-48,-46,-47,-44,-36,-54,13.3,183,-19.1,233,-14.1,247,-12.8,77,73,23,3,4.4,2.1]
["Нерчинский Завод",-45,-43,-43,-41,-34,-53,10,184,-17.4,237,-12.7,252,-11.3,78,76,32,"СЗ",2.7,1.2]
["Средний Калар",-52,-50,-48,-46,-41,-56,17.2,218,-21.5,271,-16.4,287,-15,78,73,20,"СВ","—",0.9]
["Тунгокочен",-48,-46,-47,-45,-36,-54,18.7,205,-18.7,262,-13.8,278,-12.4,76,68,27,"ЮЗ","—",1.5]
["Тупик",-50,-46,-46,-44,-38,-56,15.4,207,-19.7,260,-14.8,276,-13.4,76,70,45,"Ю","—",1.5]
["Чара",-50,-49,-48,-46,-39,-56,13.4,214,-20.3,267,-15.5,282,-14.2,79,79,25,"СВ","—",1.2]
["Чита",-44,-41,-42,-38,-31,-47,14.5,189,-15.8,242,-11.4,258,-10.1,75,64,20,"В",3.2,2.4]
["Чувашская Республика- Чаваш республики"]
["Порецкое",-40,-36,-35,-31,-17,-45,7.4,152,-8,212,-4.6,227,-3.7,84,82,192,"ЮЗ",6.4,4.9]
["Чебоксары",-40,-36,-35,-32,-18,-44,6.8,156,-8.3,217,-4.9,232,-3.9,84,84,160,"Ю","—",5]
["Чукотский АО (Магаданская область)"]
["Анадырь",-43,-42,-42,-40,-27,-45,7.7,241,-14.7,311,-10.5,345,-8.5,81,81,140,"СЗ",11.4,6.7]
["Марково",-52,-50,-51,-48,-31,-60,11,238,-18.1,286,-14.3,300,-13.2,79,77,103,"С",6,2.3]
["Островное",-57,-53,-55,-51,-39,-58,9.2,238,-22.5,288,-17.8,305,-16.3,75,75,71,"СЗ",4.5,1.8]
["Усть-Олой",-57,-54,-55,-51,-41,-58,8.2,234,-23.5,286,-18.4,304,-16.8,77,77,84,"ЮЗ","—",1.5]
["Эньмувеем",-54,-51,-52,-48,-32,-55,10.5,242,-18.4,294,-14.5,313,-13,73,73,95,"СЗ","—",2.2]
["Республика Саха (Якутия)"]
["Алдан",-48,-44,-44,-42,-33,-51,8,216,-17.4,267,-13.3,281,-12.2,78,78,121,"ЮЗ",4.1,2.8]
["Аллах-Юнь",-57,-56,-55,-54,-49,-59,9.2,231,-27,280,-21.4,295,-19.9,75,75,32,"С",3.2,0.9]
["Амга",-59,-58,-57,-55,-48,-63,8.9,217,-26.1,259,-21.3,273,-19.7,76,76,58,"З",2.5,1.6]
["Батамай",-58,-56,-54,-52,-47,-63,7.9,222,-25.7,265,-20.8,279,-19.4,72,69,53,"В","—",2.3]
["Бердигястях",-58,-57,-56,-54,-45,-61,10.7,222,-24.5,268,-19.6,282,-18.1,73,72,56,"З","—",1.2]
["Буяга",-57,-55,-55,-52,-43,-61,12.3,218,-23.1,266,-18.2,280,-16.7,74,72,56,"—","—",0.9]
["Верхоянск",-63,-61,-62,-59,-53,-68,7.3,234,-29.6,279,-24.1,292,-22.6,74,74,37,"ЮЗ",2.1,1]
["Вилюйск",-58,-56,-53,-52,-43,-61,8.3,219,-22.7,262,-18.2,276,-16.9,75,75,65,"ЮЗ",3,2.2]
["Витим",-56,-54,-53,-51,-34,-61,11.2,204,-18.2,257,-13.7,272,-12.4,76,74,119,"Ю",4.9,2.4]
["Воронцово",-55,-53,-52,-51,-43,-57,8.7,246,-24.5,297,-19.6,324,-17.2,76,76,64,"СЗ","—",1.6]
["Джалинда",-62,-59,-60,-56,-44,-64,9.4,247,-24.2,296,-19.5,316,-17.7,74,74,53,"ЮВ","—",2.2]
["Джарджан",-58,-55,-54,-52,-44,-60,7.2,238,-23.5,284,-19,297,-17.8,73,73,69,"Ю",6.1,3.6]
["Джикимда",-56,-54,-54,-51,-40,-59,12.5,209,-21.4,259,-16.5,274,-15.1,77,75,85,"—","—",0.8]
["Дружина",-57,-56,-53,-52,-44,-58,8.8,236,-25.2,284,-20.2,297,-18.9,76,76,78,"СЗ",2.8,1.5]
["Екючю",-62,-60,-61,-58,-51,-65,7,234,-28.5,281,-23,294,-21.6,74,74,31,"ЮЗ","—",1.1]
["Жиганск",-57,-55,-54,-51,-44,-60,7.3,232,-24,278,-19.3,291,-18,74,72,59,"Ю",5.1,3.9]
["Зырянка",-54,-53,-53,-51,-42,-56,6.9,229,-23.9,274,-19.2,288,-17.9,77,77,97,"СЗ",5.3,2.2]
["Исить",-53,-52,-51,-50,-41,-54,7.6,211,-22.1,256,-17.4,271,-16,75,75,59,"З",5.4,2.4]
["Иэма",-61,-60,-59,-57,-51,-63,7.4,242,-28.6,292,-22.9,311,-21,73,73,38,"СЗ","—",1.2]
["Крест-Хальджай",-59,-58,-56,-55,-50,-62,7.2,216,-27,256,-22.1,270,-20.5,72,72,43,"З","—",1]
["Кюсюр",-58,-56,-56,-54,-43,-60,8,247,-23.4,298,-18.7,324,-16.5,74,74,90,"ЮЗ",7.7,3.9]
["Ленск",-55,-53,-52,-49,-35,-57,10,208,-18.8,259,-14.2,274,-13,75,75,103,"З","—",2.8]
["Нагорный",-48,-46,-44,-41,-35,-57,9.6,222,-18.7,275,-14.2,291,-13,74,71,46,"С",6.6,3]
["Нера",-62,-60,-60,-58,-51,-62,5.2,229,-29.1,272,-23.8,286,-22.2,71,70,2,"ЮЗ","—",1.8]
["Нюрба",-58,-56,-53,-52,-41,-62,10.2,217,-22.3,263,-17.7,277,-16.3,75,75,61,"ЮЗ",3.3,2.2]
["Нюя",-56,-53,-52,-50,-35,-61,9.3,203,-18.8,253,-14.2,268,-12.9,73,73,61,"З",5.3,2.4]
["Оймякон",-63,-62,-61,-60,-53,-68,9.3,238,-30.1,286,-24.3,299,-22.8,74,74,48,"З",1,0.9]
["Олекминск",-55,-52,-52,-50,-37,-59,7.7,208,-19.9,256,-15.3,271,-14,78,78,76,"ЮЗ",3.5,2.2]
["Оленек",-62,-59,-58,-57,-46,-63,10,240,-25,290,-20,303,-18.7,75,75,62,"СЗ",2.4,2.3]
["Охотский Перевоз",-58,-57,-56,-55,-49,-60,7.9,218,-26.7,260,-21.7,274,-20.1,74,74,54,"Ю",1.8,1.1]
["Сангар",-53,-52,-51,-50,-44,-61,6.4,220,-24,261,-19.6,274,-18.2,70,70,58,"В",7.6,3.6]
["Саскылах",-57,-54,-55,-53,-40,-58,7.9,257,-22.6,314,-17.8,340,-15.8,75,75,50,"ЮВ","—",3.4]
["Среднеколымск",-54,-53,-53,-51,-42,-58,8,237,-23.7,287,-18.9,301,-17.5,77,77,76,"ЮЗ",2.9,1.9]
["Сунтар",-56,-54,-53,-51,-39,-60,11.8,213,-21,260,-16.5,274,-15.2,76,73,69,"ЮЗ",3.3,2]
["Сухана",-60,-59,-59,-57,-48,-64,9.3,239,-25.6,286,-20.6,299,-19.3,72,72,58,"ЮЗ",4,1.4]
["Сюльдюкар",-61,-58,-56,-53,-43,-63,11.8,222,-22.8,270,-18,284,-16.7,75,75,64,"ЮЗ","—",1.1]
["Сюрен-Кюель",-51,-50,-49,-46,-40,-53,7.2,239,-22.1,292,-17.4,311,-15.8,75,75,34,"ЮЗ",8.7,3]
["Токо",-55,-53,-53,-51,-45,-59,14.7,226,-23.8,279,-18.4,294,-17,75,74,66,"СЗ","—",0.8]
["Томмот",-56,-54,-54,-51,-41,-60,12.1,214,-21.9,262,-17.1,277,-15.7,77,77,92,"СЗ","—",1]
["Томпо",-59,-58,-57,-55,-49,-60,7.7,230,-27.6,276,-22.2,290,-20.8,74,74,33,"СЗ",3.1,2.4]
["Туой-Хая",-58,-55,-54,-52,-38,-59,10.4,216,-20.4,266,-15.8,280,-14.5,76,75,72,"ЮЗ",3,1.9]
["Тяня",-55,-53,-52,-50,-38,-57,11.9,211,-20.5,262,-15.7,278,-14.4,78,77,89,"СЗ","—",0.8]
["Усть-Мая",-58,-56,-57,-54,-47,-60,8.8,213,-25,256,-20.1,271,-18.5,73,73,65,"С",2.2,1.5]
["Усть-Миль",-55,-54,-54,-51,-45,-59,10.4,213,-24,259,-18.9,274,-17.4,75,74,68,"В","—",1.1]
["Усть-Мома",-62,-60,-59,-58,-50,-62,9.3,232,-23.4,277,-23.1,291,-21.6,76,76,46,"ЮВ",3.8,1]
["Чульман",-55,-52,-51,-49,-42,-61,10.7,220,-22,270,-17.1,285,-15.7,78,77,74,"СЗ",2.3,2.4]
["Чурапча",-61,-59,-59,-56,-49,-64,9.1,219,-26.6,239,-21.8,273,-20.2,73,73,46,"В","—",1.4]
["Шелагонцы",-61,-59,-58,-57,-47,-64,10.4,236,-25.3,285,-20.1,299,-18.8,73,73,57,"В",2.3,1.3]
["Эйик",-56,-54,-54,-52,-43,-59,9.6,236,-23.1,284,-18.5,298,-17.3,75,75,38,"Ю","—",2.6]
["Якутск",-59,-57,-57,-54,-48,-64,8.9,216,-25.3,256,-20.6,269,-19.2,73,72,48,"С",2.6,1.9]
["Ненецкий АО (Архангельская область)"]
["Варандей",-40,-39,-37,-36,-24,-44,8.8,238,-11.5,323,-7.3,365,-5.6,86,85,126,"ЮЗ","—",6.1]
["Индига",-39,-38,-35,-33,-20,-43,8,215,-9,305,-5.1,350,-3.2,84,84,137,"ЮЗ",10.6,6.5]
["Канин Нос",-28,-25,-25,-23,-15,-38,5.6,203,-5.8,325,-2,365,-0.9,87,86,164,"Ю",10.1,7.7]
["Коткино",-49,-47,-43,-41,-23,-51,10,215,-10.7,285,-7.1,309,-5.8,82,81,148,"ЮЗ","—",3.7]
["Нарьян-Мар",-44,-42,-40,-37,-22,-48,8.6,220,-10.7,290,-7.2,313,-6,83,80,123,"Ю",6.3,5]
["Ходовариха",-39,-37,-34,-32,-22,-40,8.6,181,-8.4,330,-6.2,365,-4.5,86,86,167,"ЮЗ","—",6.6]
["Хоседа-Хард",-48,-46,-43,-42,-25,-53,9.5,229,-13.3,296,-8.6,318,-7.3,83,82,118,"Ю",7.2,4.4]
["Ярославская область"]
["Ярославль",-37,-34,-34,-31,-17,-46,8.3,152,-7.8,221,-4,239,-2.8,83,82,174,"Ю",5.5,4.3]
[]
["АЗЕРБАЙДЖАНСКАЯ РЕСПУБЛИКА"]
["Баку",-8,-6,-5,-4,2,-13,4.8,0,null,112,5.1,137,5.8,"—",72,125,"С","—",9.5]
[]
["РЕСПУБЛИКА АРМЕНИЯ"]
["Ванадзор",-20,-17,-16,-15,"—",-30,"—",89,-2.5,180,0.7,202,1.6,69,52,135,"СЗ",4.8,"—"]
["Горис",-15,-13,-13,-11,"—",-20,"—",45,-0.6,173,2.4,197,3.2,65,51,225,"СЗ",4.3,"—"]
["Ереван",-21,-19,-19,-17,"—",-27,8.3,70,-2.4,140,1,159,1.8,78,67,132,"ЮЗ",3.4,"—"]
["Ехегнадзор",-23,-19,-19,-16,"—",-26,"—",79,-2.6,148,0.5,168,1.4,73,62,175,"ЮЗ","—","—"]
["Камо",-24,-22,-21,-18,"—",-33,"—",134,-4.9,211,-1.5,243,-0.1,73,65,114,"ЮЗ",5.9,"—"]
["Кафан",-14,-12,-11,-9,"—",-22,"—",0,null,140,3.1,159,3.8,73,53,188,"В","—","—"]
["Севан",-23,-20,-20,-18,"—",-33,7.6,134,-5.6,213,-2,240,-0.7,81,78,161,"З",5.1,"—"]
["Сисиан",-26,-23,-21,-19,"—",-34,"—",105,-3.2,189,0.1,211,1,70,56,120,"СЗ",4.3,"—"]
["Спитак",-21,-18,-18,-14,"—","—","—",102,-3,184,0.1,204,1,70,59,106,"З",6.6,"—"]
["Степанаван",-22,-19,-18,-16,"—",-31,"—",99,-2.6,189,0.6,211,1.4,68,56,142,"ЮЗ",7.2,"—"]
[]
["РЕСПУБЛИКА БЕЛАРУСЬ"]
["Брестская область"]
["Брест",-30,-25,-24,-21,-7,-36,5.5,100,-3.1,186,0.1,206,1,85,80,185,"ЮЗ",3.7,3.4]
["Витебская область"]
["Витебск",-36,-31,-30,-25,-12,-41,6.2,135,-5.3,207,-2.1,225,-1.2,85,80,202,"Ю",4.8,4.3]
["Полоцк",-35,-30,-29,-25,-12,-39,6.3,133,5,207,-1.8,225,-0.9,85,82,202,"Ю",4.1,3.8]
["Гомельская область"]
["Василевичи",-30,-27,-26,-23,-10,-36,6.5,121,-4.4,194,-1.2,212,-0.3,85,79,198,"Ю",3.7,3.2]
["Гомель",-32,-28,-28,-24,-11,-35,6.3,125,-4.7,194,-1.6,211,-0.7,84,80,194,"Ю",4,3.9]
["Гродненская область"]
["Гродно",-31,-26,-25,-22,-9,-36,5.7,113,-3.5,194,-0.5,213,0.4,87,83,186,"З",5.6,4.1]
["Минская область"]
["Минск",-33,-28,-28,-24,-10,-39,6.2,131,-4.6,202,-1.6,221,-0.7,86,81,228,"Ю",3.7,3.9]
["Могилевская область"]
["Горки",-35,-30,-29,-26,-12,-40,6.3,139,-5.6,208,-2.4,226,-1.5,86,84,205,"Ю",5.3,4.4]
["Могилев",-34,-29,-28,-24,-12,-37,6.4,132,-5.1,204,-1.9,220,-1.1,86,82,217,"Ю",4.7,4.4]
[]
["ГРУЗИЯ"]
["Ахалкалаки",-24,-21,-18,-15,-8,-38,9.9,117,-4.5,206,-0.8,233,0.4,"—",61,152,"ЮВ","—",5.1]
["Казбеги",-30,-25,-24,-21,-9,-42,7.3,272,-8.6,365,-5.7,365,-5.7,"—",72,377,"З","—",4.9]
["Крестовый перевал",-17,-15,-15,-13,-3,-38,8.4,180,-6.7,291,-1.9,326,-1.3,"—",77,508,"СВ","—",4.2]
["Мамисонский перевал",-21,-18,-17,-14,-5,-35,5.5,210,-7.2,365,-2.1,365,-2.1,"—",81,321,"З","—",8]
["Местиа",-20,-16,-15,-13,-4,-35,10.5,148,-3.7,202,-0.4,228,0.7,"—",66,331,"С","—",1.3]
["Мта-Сабуети",-10,-8,-7,-4,2,-27,7.1,93,-2.2,195,0.8,221,1.8,"—",83,624,"В","—",10]
["Поти",-8,-6,-6,-3,3,-13,6.7,0,null,82,6.5,119,7.4,"—",64,723,"В","—",6.1]
["Сакара",-10,-8,-8,-3,2,-20,7.8,0,null,98,5.3,125,6.2,"—",61,604,"В","—",1.8]
["Самтредиа",-9,-7,-5,-3,2,-17,6.9,0,null,87,6.3,119,6.8,"—","—",624,"В","—",5.3]
["Тбилиси",-14,-11,-10,-8,1,-22,7.4,0,null,121,4.1,143,5.3,"—",57,120,"СЗ","—",2.9]
["Телави",-13,-12,-11,-8,2,-23,7.5,0,null,133,3.5,157,4.3,"—",63,186,"З","—",2]
["Цхинвали",-10,-9,-8,-4,2,-28,7.6,43,-0.8,154,2.2,178,3.1,"—",67,247,"С","—",3.1]
["Шираки",-21,-18,-17,-14,-5,-32,12.4,54,-1.2,153,1.8,174,2.6,"—",63,160,"СЗ","—",3]
["Абхазская Республика"]
["Гудаута",-8,-7,-6,-3,-2,-13,6.9,0,null,77,6.5,114,7.4,"—",66,711,"СВ","—",2.9]
["Псху",-17,-14,-12,-10,-4,-27,9.7,45,-0.8,165,2.1,190,3,"—",73,1120,"С","—",0]
["Сухуми",-5,-4,-3,-2,0,-12,6.5,0,null,79,6.4,115,7.3,"—",65,679,"СВ","—",3]
["Аджарская Республика"]
["Батуми",-4,-2,-2,-1,4,-8,6.4,0,null,64,7.3,112,8.1,"—",70,1231,"ЮВ","—",3.2]
["Хуло",-10,-7,-6,-3,2,-18,6.4,0,null,143,3.2,213,4.3,"—",65,718,"С","—",5]
[]
["РЕСПУБЛИКА КАЗАХСТАН"]
["Акмолинская область"]
["Астана",-41,-38,-36,-33,-23,-52,9,167,-11.7,215,-8.1,227,-7.2,80,77,88,"ЮЗ",5.9,5.2]
["Атбасар",-40,-39,-37,-34,-25,-57,9.6,169,-11.7,215,-8.9,229,-7.7,81,78,92,"ЮЗ",7.8,5.5]
["Актюбинская область"]
["Актюбинск",-38,-36,-33,-31,-22,-48,8.9,154,-10.1,200,-6.8,212,-5.9,80,"—",87,"Ю",6.1,4.3]
["Караулкельды",-39,-37,-35,-33,"—",-44,8.5,144,-8.7,191,-5.6,202,-4.8,"—","—",83,"ЮВ",5.3,4.2]
["Уил",-39,-38,-36,-34,-18,-42,8.6,142,-8.7,187,-5.6,201,-4.6,81,76,104,"ЮВ",6.1,4.4]
["Челкар",-39,-37,-35,-33,"—",-45,9.5,146,-9.8,190,-6.4,201,-4.6,81,"—",75,"СВ",6.2,4.9]
["Алматинская область"]
["Алматы",-30,-28,-23,-21,-11,"—",9.8,111,-4.6,168,-1.6,182,-0.8,75,75,213,"Ю",1.3,1.1]
["Баканас",-41,-40,-39,-35,"—",-43,12.1,125,-7.6,172,-4.5,185,-3.5,79,"—",75,"СВ",2.5,2.1]
["Атырауская область"]
["Атырау",-33,-30,-28,-25,-8,-38,8.1,125,-6.4,177,-3.4,191,-2.4,84,75,77,"В",6,5.8]
["Ганюшкино",-30,-28,-27,-23,"—","—",7.4,111,-5.1,174,-1.9,187,-1.2,82,"—",66,"В",7.3,4.9]
["Восточно-Казахстанская область"]
["Зайсан",-39,-38,-36,-33,-23,"—",8.3,151,-11.8,191,-8.3,203,-7.3,81,80,74,"—","—","—"]
["Зыряновск",-46,-44,-44,-41,"—",-51,12.3,172,-15.2,217,-11.1,231,-9.9,"—","—",218,"—","—","—"]
["Катон-Карагай",-37,-35,-31,-29,"—","—",9.9,167,-9.6,225,-6,244,-4.8,65,"—",97,"—","—","—"]
["Лениногорск",-45,-39,-42,-36,"—","—",11.4,164,-9,223,-5.5,240,-4.4,67,"—",126,"В",6.6,2.7]
["Усть-Каменогорск",-46,-44,-42,-39,"—",-49,11.3,154,-11.8,204,-7.8,219,-6.6,75,"—",166,"ЮВ",5,2.4]
["Шемонаиха",-46,-44,-42,-38,"—","—",-11.4,160,-12,209,-8.2,223,-7.1,78,"—",152,"Ю",6,2.9]
["Джамбулская область"]
["Джамбул",-30,-28,-27,-23,"—",-41,10.4,100,-3.6,162,-0.7,186,0.6,76,"—",162,"Ю",4.5,3]
["Фурмановка",-32,-29,-27,-24,"—","—",10.4,113,-5.6,166,-2.5,179,-1.6,72,"—",112,"СВ",4.3,3.3]
["Джезказганская область"]
["Балхаш",-37,-35,-33,-31,-20,"—",9.1,144,-9.9,189,-6.5,203,-5.4,"—","—",61,"СВ",5.1,4.8]
["Карсакпай",-39,-37,-35,-32,-21,"—",9,154,-10.5,199,-7.2,212,-6.1,80,76,68,"—","—","—"]
["Западно-Казахстанская область"]
["Джамбейты",-39,-36,-33,-30,"—",-42,8.8,145,-9.2,192,-5.9,205,-4.9,82,"—",94,"ЮВ",5.5,5.1]
["Уральск",-38,-36,-33,-30,-19,-43,8.6,148,-9.4,198,-5.9,209,-5.1,"—","—",112,"ЮВ",4.7,3]
["Карагандинская область"]
["Караганда",-39,-37,-35,-32,-21,"—",9.3,161,-10.3,208,-7,222,-6,78,"—",92,"ЮЗ",5.3,4.9]
["Каркаралинск",-38,-36,-34,-31,"—",-45,11.2,165,-9.9,208,-7,238,-5.4,79,"—",60,"Ю",8,"—"]
["Кзыл-Ординская область"]
["Аральское Море",-35,-33,-30,-27,-18,-38,8.4,136,-8.5,181,-5.4,192,-4.6,81,76,59,"СВ",5.6,4.9]
["Казалинск",-32,-30,-28,-25,"—",-40,8.6,128,-7.3,175,-4.3,186,-3.3,79,"—",72,"СВ",3,3.4]
["Кзыл-Орда",-34,-30,-26,-24,"—",-38,8.6,118,-6.2,175,-4.3,181,-2.3,79,"—",73,"СВ",4.5,4.4]
["Кокчетавская область"]
["Кокчетав",-39,-36,-37,-33,"—",-46,8.5,167,-11,215,-7.5,228,-6.5,"—","—",60,"ЮЗ",7.9,5.9]
["Кустанайская область"]
["Кустанай",-40,-36,-37,-34,-24,"—",8.7,161,-12,212,-8.1,224,-7.2,81,78,73,"—","—",4.6]
["Мангистауская область"]
["Форт-Шевченко",-21,-19,-19,-17,"—","—",4.9,79,-2.1,157,0.9,172,1.5,76,"—",61,"—","—","—"]
["Павлодарская область"]
["Баянаул",-39,-37,-35,-32,"—","—",8.9,157,-9.7,208,-6.3,224,-5.2,72,"—",88,"З",8.7,3.9]
["Павлодар",-40,-39,-38,-35,"—",-47,9.8,161,-12.3,206,-8.7,220,-7.6,79,"—",86,"Ю",5.9,4.8]
["Северо-Казахстанская область"]
["Петропавловск",-40,-38,-39,-36,-24,-44,9.1,171,-12.2,218,-8.6,233,-7.5,81,78,74,"ЮЗ",6.4,5.7]
["Семипалатинская область"]
["Аягуз",-42,-41,-40,-39,"—","—",11.6,159,-11.7,205,-8.1,222,-6.8,75,"—",99,"—","—","—"]
["Бахты",-38,-36,-33,-30,"—","—",13.5,135,-9.1,181,-5.6,194,-4.6,76,"—",125,"—","—","—"]
["Кокпекты",-45,-43,-41,-38,"—",-50,12.3,164,-14,209,-10,222,-8.9,77,"—",143,"—","—","—"]
["Семипалатинск",-44,-41,-40,-36,"—","—",9.8,159,-11.2,203,-7.8,216,-6.8,76,"—",109,"—","—","—"]
["Талды-Курганская область"]
["Жаркент",-32,-30,-27,-23,-11,"—",12.6,111,-6,159,-2.9,174,-1.9,"—",74,63,"—","—","—"]
["Талды-Курган",-34,-32,-29,-26,"—","—",12.5,125,-6.6,174,-3.7,187,-2.8,"—","—",169,"—","—","—"]
["Тургайская область"]
["Амангельды",-40,-37,-37,-33,"—",-45,9.2,157,-11.4,200,-8,211,-7.1,81,"—",92,"СВ",7.3,4.8]
["Тургай",-37,-34,-33,-31,-23,"—",9.4,152,-11.2,194,-7.8,207,-6.9,80,78,88,"СВ",6.3,4.9]
["Южно-Казахстанская область"]
["Туркестан",-29,-26,-24,-21,-10,"—",10.1,86,-3.6,151,-0.3,165,0.5,"—",74,134,"В",2.6,2.5]
["Чимкент",-26,-25,-17,-15,"—","—",9.8,61,-1.9,143,1.5,160,2.2,"—","—",368,"В",4.3,2.5]
[]
["КЫРГЫЗСКАЯ РЕСПУБЛИКА"]
["Иссык-Кульская область"]
["Каракол",-18,-16,-15,-13,"—","—",11,"—","—","—","—","—","—",72,64,93,"В",4.4,"—"]
["Чолпон-Ата",-14,-13,-11,-10,"—","—","—","—","—","—","—","—","—",71,61,"—","—","—","—"]
["Нарынская область"]
["Кочкорка",-24,-22,-23,-21,"—",-36,"—","—","—","—","—","—","—",62,42,23,"З",1.7,"—"]
["Нарын",-33,-31,-32,-29,"—",-38,10.7,"—","—","—","—","—","—",80,69,"—","З",2.1,"—"]
["Сусамыр",-42,-40,-40,-36,"—","—",13.1,"—","—","—","—","—","—",82,76,113,"ЮЗ",0.7,"—"]
["Ошская область"]
["Гульча",-24,-22,-20,-20,"—","—","—","—","—","—","—","—","—","—",56,195,"—","—","—"]
["Ош",-20,-17,-16,-13,"—","—",9.9,"—","—","—","—","—","—","—",57,205,"З",1.8,"—"]
["Хайдаркан",-20,-19,-17,-16,"—","—","—","—","—","—","—","—","—","—",52,233,"—","—","—"]
["Таласская область"]
["Талас",-28,-24,-23,-21,"—","—",12.3,"—","—","—","—","—","—",67,57,126,"В",2.5,"—"]
["Чуйская область"]
["Бишкек",-28,-27,-24,-23,"—","—",10.6,"—","—","—","—","—","—",71,63,184,"З",2.4,"—"]
[]
["РЕСПУБЛИКА МОЛДОВА"]
["Кишинев",-24,-22,-20,-17,-8,-32,5.9,82,-2.5,162,0.6,179,1.4,81,75,130,"СЗ",5.7,"—"]
[]
["РЕСПУБЛИКА ТУРКМЕНИСТАН"]
["Ахалская область"]
["Ашхабад",-19,-16,-15,-11,-2,-24,8.8,0,null,108,4,128,4.8,"—",69,139,"В",2.3,"—"]
["Гаудан",-18,-14,-13,-11,-3,-22,9.5,21,-0.1,151,2.7,173,3.4,"—",60,174,"Ю",5.4,"—"]
["Серахс",-18,-14,-14,-11,-3,-26,9.7,0,null,96,4.9,117,5.7,"—",63,150,"СЗ",4.8,"—"]
["Теджен",-20,-16,-15,-12,-5,-27,10.6,0,null,103,3.8,123,4.7,"—",63,110,"В",4.8,"—"]
["Балканская область"]
["Гасанкули",-17,-13,-12,-8,0,-18,10.5,0,null,98,5.3,122,6,"—",64,120,"СВ",3.9,"—"]
["Казанджик",-20,-16,-14,-13,-2,-29,8.2,0,null,114,3.2,131,4,"—",68,109,"В",6.4,"—"]
["Кизиларват",-19,-18,-17,-14,-3,-26,8,0,null,118,3,135,3.8,"—",72,134,"В",6.7,"—"]
["Кизилатрек",-10,-8,-6,-5,3,-15,10.3,0,null,82,6.3,111,6.9,"—",61,125,"СВ",3.7,"—"]
["Небитдаг",-19,-16,-15,-11,-2,-24,8.3,0,null,99,4.7,114,5.3,"—",57,81,"В",7.6]
["Туркменбаши",-18,-14,-13,-11,-3,-22,8.1,0,null,124,4.1,144,4.6,"—",61,82,"ЮВ",6.5,"—"]
["Чагыл",-25,-21,-20,-15,-5,-32,9.3,62,-0.4,137,1.4,153,2.2,"—",60,70,"В",5.6,"—"]
["Марыйская область"]
["Байрамали",-18,-16,-15,-12,-5,-26,10.1,0,null,103,4,121,5,"—",55,146,"В",4.1,"—"]
["Иолотань",-20,-17,-15,-14,-6,-28,10.3,0,null,106,4.1,128,4.9,"—",62,90,"ЮВ",4,"—"]
["Кушка",-20,-17,-16,-12,-2,-33,11.1,0,null,115,4.4,137,5.2,"—",65,239,"ЮЗ",3.1,"—"]
["Мары",-18,-15,-15,-12,-4,-25,10.3,0,null,101,4,122,4.8,"—",62,99,"В",5,"—"]
["Тахтабазар",-20,-16,-15,-12,-5,-27,10,0,null,104,4.3,125,5.1,"—",69,205,"ЮВ",3.3,"—"]
["Ташаузская область"]
["Ташауз",-24,-21,-21,-17,-8,-33,9.6,81,-0.8,147,-0.1,160,0.6,"—",65,60,"В",5.9,"—"]
["Чарджоуская область"]
["Дарганата",-23,-19,-18,-15,-6,-31,10.2,51,-0.6,135,1.4,151,2.2,"—",58,81,"В",4.7,"—"]
["Керки",-19,-16,-16,-12,-3,-25,10,0,null,96,4.6,122,5.5,"—",64,141,"ЮВ",4.9,"—"]
["Репетек",-20,-17,-16,-12,-2,-31,10.5,0,null,111,3.6,130,4.4,"—",58,90,"ЮВ",4.4,"—"]
["Чарджоу",-19,-17,-15,-13,-2,-24,9.6,0,null,114,3.3,134,4.1,"—",63,93,"С",5,"—"]
[]
["РЕСПУБЛИКА УЗБЕКИСТАН"]
["Андижанская область"]
["Андижан",-19,-16,-16,"—",-5,-28,9.1,52,"—",130,1.6,"—","—","—","—","—","—",2.1,"—"]
["Бухарская область"]
["Бухара",-19,-16,-15,"—",-3,-25,10.1,0,null,126,3.1,"—","—","—","—","—","—",4.5,"—"]
["Джизакская область"]
["Галляарал",-26,-23,-22,"—",-6,-37,11,62,"—",144,1.4,"—","—","—","—","—","—",4.7,"—"]
["Джизак",-22,-19,-19,"—",-4,-32,8.5,28,"—",126,2.7,"—","—","—","—","—","—",5.5,"—"]
["Каракалпакстан"]
["Каракалпакия",-32,-29,-30,"—",-13,-40,7.8,119,"—",174,-2.4,"—","—","—","—","—","—",5,"—"]
["Муйнак",-25,-23,-23,"—",-8,"—",6.8,104,"—",167,-1.2,"—","—","—","—","—","—",4.8,"—"]
["Нукус",-27,-24,-23,"—",-9,-34,8.8,90,"—",143,-0.6,"—","—","—","—","—","—",4.2,"—"]
["Чимбай",-27,-24,-23,"—",-10,-34,9.4,100,"—",163,-1.3,"—","—","—","—","—","—",3,"—"]
["Кашкадарьинская область"]
["Гузар",-16,-14,-13,"—",-2,-23,9.4,0,null,100,4.7,"—","—","—","—","—","—",4.7,"—"]
["Мубарек",-19,-16,-16,"—",-3,-27,9.9,0,null,122,3.5,"—","—","—","—","—","—",2.8,"—"]
["Навоийская область"]
["Навои",-18,-16,-16,"—",-2,-28,9,0,null,123,3.5,"—","—","—","—","—","—",3.6,"—"]
["Нурата",-22,-19,-19,"—",-4,-32,10,28,"—",136,2.8,"—","—","—","—","—","—",7.4,"—"]
["Наманганская область"]
["Касансай",-17,-15,-14,"—",-4,-21,8.9,48,"—",138,2,"—","—","—","—","—","—",2.6,"—"]
["Наманган",-20,-17,-17,"—",-6,-26,8.7,52,"—",128,1.5,"—","—","—","—","—","—",2,"—"]
["Самаркандская область"]
["Каттакурган",-19,-16,-16,"—",-3,-30,8.6,23,"—",134,2.8,"—","—","—","—","—","—",3.7,"—"]
["Самарканд",-18,-15,-14,"—",-3,-25,9.8,0,null,133,3.3,"—","—","—","—","—","—",2.7,"—"]
["Сурхандарьинская область"]
["Денау",-14,-12,-11,"—",0,-21,9.3,0,null,89,5.1,"—","—","—","—","—","—",2.4,"—"]
["Термез",-14,-12,-12,"—",-1,-20,10.4,0,null,91,4.5,"—","—","—","—","—","—",4,"—"]
["Шерабад",-13,-10,-10,"—",1,"—",8.4,0,null,80,5.4,"—","—","—","—","—","—",3.6,"—"]
["Сырдарьинская область"]
["Сырдарья",-23,-21,-20,"—",-5,-32,9.4,51,"—",134,1.8,"—","—","—","—","—","—",2.2,"—"]
["Ташкентская область"]
["Ташкент",-19,-16,-16,"—",-4,-30,9.6,30,"—",129,2.7,"—","—","—","—","—","—",2.1,"—"]
["Чарвак",-18,-16,-15,"—",-5,-24,6.9,56,"—",144,1.7,"—","—","—","—","—","—",11.3,"—"]
["Ферганская область"]
["Коканд",-17,-14,-14,"—",-5,-24,7.6,51,"—",131,1.8,"—","—","—","—","—","—",5.4,"—"]
["Фергана",-18,-15,-15,"—",-6,"—",9.1,47,"—",132,1.9,"—","—","—","—","—","—",1.4,"—"]
["Хорезмская область"]
["Ургенч",-23,-21,-21,"—",-8,-28,8.8,79,"—",148,0.8,"—","—","—","—","—","—","—",4.6]
[]
["УКРАИНА"]
["Винницкая область"]
["Винница",-29,-26,-25,-21,-10,-36,"—",107,-3.7,180,-0.7,198,0.2,"—","—",194,"Ю","—","—"]
["Волынская область"]
["Ковель",-28,-25,-23,-21,-9,-35,"—",97,-3.2,180,0,200,0.9,"—","—",176,"З","—","—"]
["Луцк",-27,-24,-22,-20,-8,-34,"—",99,-3.3,179,-0.1,199,0.8,"—","—",162,"ЮВ","—","—"]
["Днепропетровская область"]
["Днепропетровск",-29,-27,-26,-24,-10,-38,"—",100,-3.7,172,-0.6,187,0.2,"—","—",209,"В","—","—"]
["Комиссаровка",-27,-25,-22,-20,-8,-34,"—",100,-3.7,175,-0.6,191,0.2,"—","—",180,"СВ","—","—"]
["Кривой Рог",-21,-18,-18,-17,-7,-28,"—",95,-3.3,170,-0.2,186,0.6,"—","—",177,"В","—","—"]
["Донецкая область"]
["Донецк",-28,-26,-24,-22,-9,-34,"—",105,-4.1,176,-0.9,190,-0.2,"—","—",204,"ЮВ","—","—"]
["Житомирская область"]
["Житомир",-29,-25,-24,-22,-9,-35,"—",109,-3.9,182,-0.8,201,0.1,"—","—",174,"З","—","—"]
["Овруч",-28,-25,-23,-21,-8,-34,"—",111,-4,185,-0.9,202,0,"—","—",205,"З","—","—"]
["Закарпатская область"]
["Ужгород",-25,-23,-21,-18,-7,-32,"—",63,2,154,1.5,176,2.4,"—","—",278,"ЮВ",4.4,"—"]
["Запорожская область"]
["Запорожье",-27,-24,-23,-21,-7,-32,"—",86,-2.9,166,0.3,181,1,"—","—",219,"СВ","—","—"]
["Кирилловка",-28,-25,-23,-22,-8,-33,"—",99,-3.5,174,-0.4,191,0.4,"—","—",236,"В","—","—"]
["Ивано-Франковская область"]
["Ивано-Франковск",-26,-24,-22,-20,-9,-34,"—",96,-3.3,178,0,198,0.9,"—","—",172,"ЮВ","—","—"]
["Киевская область"]
["Киев",-29,-26,-25,-22,-10,-32,"—",103,-3.7,176,-0.6,193,0.3,"—","—",235,"З",4.3,"—"]
["Кировоградская область"]
["Гайворон",-29,-26,-25,-22,-9,-35,"—",95,-3.4,173,-0.2,190,0.6,"—","—",220,"ЮВ","—","—"]
["Знаменка",-29,-27,-25,-22,-10,-35,"—",105,-3.9,177,-0.8,193,0,"—","—",200,"Ю","—","—"]
["Кировоград",-30,-26,-25,-22,-10,-35,"—",102,-3.8,175,-0.7,191,0.1,"—","—",167,"Ю","—","—"]
["Луганская область"]
["Луганск",-32,-29,-27,-25,-10,-42,"—",100,-4.1,172,-0.8,188,0,"—","—",179,"В","—","—"]
["Львовская область"]
["Львов",-25,-24,-20,-19,-9,-34,"—",99,-3,179,0,201,1,"—","—",231,"ЮВ",5.8,"—"]
["Николаевская область"]
["Николаев",-26,-23,-22,-20,-7,-30,"—",76,-2.2,160,0.9,176,1,"—","—",178,"СВ","—","—"]
["Одесская область"]
["Измаил",-22,-19,-17,-15,-2,-25,"—",54,-1.3,153,1.9,172,2.7,"—","—",188,"С",6.4,"—"]
["Любашевка",-24,-21,-21,-19,-7,-30,"—",93,-3.3,171,-0.2,187,0.6,"—","—",194,"ЮВ","—","—"]
["Одесса",-24,-21,-20,-18,-6,-29,"—",61,-1.4,158,1.7,178,2.5,"—","—",204,"С",6.5,"—"]
["Раздельное",-24,-21,-20,-17,-7,-29,"—",83,-2.5,164,0.6,181,1.4,"—","—",178,"СВ","—","—"]
["Сарата",-26,-23,-22,-20,-7,-30,"—",64,-1.5,157,1.6,177,2.4,"—","—",163,"С","—","—"]
["Полтавская область"]
["Лубны",-29,-26,-25,-23,-11,-34,"—",112,-4.2,179,-1.2,195,-0.4,"—","—",247,"ЮВ","—","—"]
["Полтава",-30,-27,-25,-23,-11,-34,"—",112,-4.3,177,-1.3,193,-0.5,"—","—",215,"В","—","—"]
["Ровенская область"]
["Ровно",-27,-25,-22,-21,-9,-35,"—",105,-3.5,181,-0.5,200,0.4,"—","—",157,"З","—","—"]
["Сарны",-27,-25,-23,-21,-10,-35,null,102,-3.5,180,-0.4,199,0.5,"—","—",182,"Ю","—","—"]
["Сумская область"]
["Ромны",-29,-26,-25,-23,-11,-34,"—",118,-4.8,184,-1.7,200,-0.8,"—","—",237,"В","—","—"]
["Сумы",-30,-29,-27,-25,-13,-36,"—",121,-5,185,-1.9,201,-1.1,"—","—",220,"ЮВ","—","—"]
["Тернопольская область"]
["Тернополь",-25,-23,-22,-20,-9,-32,"—",109,-3.8,183,-0.7,203,0.2,"—","—",175,"ЮВ","—","—"]
["Харьковская область"]
["Лозовая",-30,-27,-26,-22,-10,-35,"—",108,-4.3,176,-1.3,192,-0.4,"—","—",230,"В","—","—"]
["Харьков",-31,-28,-26,-23,-11,-36,"—",113,-4.6,179,-1.5,194,-0.7,"—","—",192,"В",6.5,"—"]
["Херсонская область"]
["Аскания-Нова",-26,-23,-22,-20,-7,-31,"—",75,-2.2,165,1,182,1.8,"—","—",154,"В",7.2,"—"]
["Геническ",-27,-24,-23,-19,-7,-32,"—",70,-1.7,161,1.4,178,2.1,"—","—",166,"В",6.6,"—"]
["Херсон",-27,-23,-23,-19,-7,-32,"—",77,-2.1,163,1,180,1.8,"—","—",165,"В","—","—"]
["Хмельницкая область"]
["Хмельницкий",-26,-25,-22,-21,-9,-32,"—",106,-3.6,181,-0.5,200,0.4,"—","—",195,"ЮВ","—","—"]
["Черкасская область"]
["Золотоноша",-29,-26,-24,-21,-8,-36,"—",104,-3.9,177,-0.8,194,0.1,"—","—",205,"ЮВ","—","—"]
["Умань",-29,-25,-23,-20,-8,-35,"—",104,-3.7,178,-0.6,195,0.2,"—","—",220,"СЗ","—","—"]
["Черниговская область"]
["Чернигов",-31,-28,-27,-23,-10,-36,"—",115,-4.5,185,-1.4,202,-0.5,"—","—",210,"Ю","—","—"]
["Черновицкая область"]
["Черновцы",-26,-24,-22,-20,-9,-32,"—",92,-3.2,173,0,191,0.9,"—","—",173,"СЗ",6.3,"—"]
["Автономная Республика Крым"]
["Ай-Петри",-24,-22,-20,-18,-6,-27,"—",105,-2.6,209,0.7,237,1.7,"—","—",638,"СЗ","—","—"]
["Клепинино",-27,-25,-23,-21,-9,-33,"—",55,-1.1,156,2,175,2.8,"—","—",160,"В","—","—"]
["Симферополь",-22,-20,-18,-15,-3,-30,"—",37,-0.5,153,2.6,174,3.4,"—","—",210,"СВ",7.4,"—"]
["Феодосия",-22,-19,-17,-15,-2,-25,"—",0,null,140,3.4,162,4.1,"—","—",185,"СЗ",6.5,"—"]
["Ялта",-10,-8,-7,-6,1,-15,"—",0,null,119,5.1,149,5.9,"—","—",355,"З","—","—"]
[]
["Таблица 2- КЛИМАТИЧЕСКИЕ ПАРАМЕТРЫ ТЕПЛОГО ПЕРИОДА ГОДА"]
[]
["Республика, край, область, пункт","Барометрическое давление, гПа","Температура воздуха, °С, обеспеченностью 0,95","Температура воздуха, °С, обеспеченностью 0,98","Средняя  максимальная температура воздуха наиболее теплого месяца, °С","Абсолютная максимальная температура воздуха, °С","Средняя суточная амплитуда температуры воздуха наиболее теплого месяца, °С","Средняя месячная относительная влажность воздуха наиболее теплого месяца, %","Средняя месячная относительная влажность воздуха в 15 ч наиболее теплого месяца, %","Количество осадков за апрель-октябрь, мм","Суточный максимум осадков, мм","Преобладающее направление ветра за июнь-август","Минимальная из средних скоростей ветра по румбам за июль, м/с"]
[1,2,3,4,5,6,7,8,9,10,11,12,13]
[]
["РОССИЙСКАЯ ФЕДЕРАЦИЯ"]
["Республика Адыгея"]
["Майкоп",990,26.6,30.6,29,41,12.8,67,48,481,88,"Ю",2.1]
["Республика Алтай"]
["Алейск",990,24.5,28.6,26.9,41,12.9,68,51,314,85,"ЮЗ",0]
["Барнаул",990,24.5,27.7,26,38,12.3,70,54,340,61,"СВ",0]
["Беля",960,19.9,24.2,22.3,35,9.5,72,64,463,97,"ЮВ",0]
["Бийск",985,23.4,27.6,25.9,39,13.3,74,55,404,59,"ЮЗ",3.1]
["Змеиногорск",965,23.6,27.7,26,40,13.3,68,52,445,113,"СВ",0]
["Катанда",920,21.4,25.6,23.8,36,16,73,54,361,35,"С",0]
["Кош-Агач",840,18.9,23.2,21.3,33,14.2,54,35,96,54,"З",0]
["Онгудай",930,22.2,26.4,24.6,38,15.3,71,50,334,52,"З",0]
["Родино",990,25.1,29.1,27.5,40,13.8,63,45,243,50,"ЮЗ",3.3]
["Рубцовск",985,25.1,29.1,27.4,41,13.5,65,46,255,"—","СВ",0]
["Славгород",995,24.9,28.9,27.3,40,12.9,62,45,225,70,"СЗ",4.2]
["Тогул",980,22.7,26.8,25.1,37,12.2,75,60,376,42,"СВ","—"]
["Амурская область"]
["Архара",990,24.7,27.5,26.3,36,10.2,80,67,610,104,"ЮВ",0]
["Белогорск",985,24.2,28.3,26.6,40,10.9,75,61,481,105,"Ю",3.1]
["Благовещенск",990,24.7,28.1,27,41,10.6,77,63,528,122,"Ю",0]
["Бомнак",965,21.7,26,24.6,35,12.8,75,61,533,101,"В",3.5]
["Братолюбовка",980,23.2,27.3,25.6,39,11.7,79,63,550,"—","ЮВ","—"]
["Бысса",970,23.5,27.6,25.9,35,14.1,80,60,636,106,"С",0]
["Гош",980,23.3,27.4,25.7,40,13.5,80,63,554,107,"ЮВ",0]
["Дамбуки",975,22.4,26.6,24.8,37,13.8,77,61,482,90,"СЗ",0]
["Ерофей Павлович",950,23.1,27.2,25.5,37,14.7,73,55,429,81,"С","—"]
["Завитинск",980,23.3,27.4,25.7,40,10.7,79,65,577,127,"ЮВ",0]
["Зея",980,23.1,27.2,25.5,36,14.3,78,60,495,75,"—",0]
["Норский Склад",980,23.5,27.6,25.9,35,12.5,79,63,548,135,"СВ",0]
["Огорон",960,21.7,25.9,24.1,35,13.7,78,61,525,96,"С",0]
["Поярково",995,24.2,28.3,26.6,40,11.5,80,64,446,94,"В",0]
["Свободный",985,24.2,28.3,26.6,40,12.5,78,60,578,89,"СЗ","—"]
["Сковородино",960,23,27.1,25.4,36,15.3,76,56,442,97,"В",0]
["Средняя Нюкжа",945,22.6,26.8,25,38,16.7,76,56,546,"—","ЮВ","—"]
["Тыган-Уркан",965,23,27.1,25.4,38,15.1,77,58,524,"—","СЗ",0]
["Тында",950,22.5,26.6,24.9,36,14.9,76,56,518,69,"З",0]
["Унаха",955,22.5,26.6,24.9,36,15.8,77,56,558,86,"СЗ","—"]
["Усть-Нюкжа",955,22.9,27,25.3,37,14,72,52,402,128,"СВ",0]
["Черняево",980,23.5,27.6,25.9,37,12.4,78,59,415,86,"СВ","—"]
["Примечание—Абсолютная максимальная температура воздуха выбрана из ряда наблюдений за период 1881—1985 гг.; в СНиП 2.01.01-82 «Строительная климатология и геофизика» абсолютная максимальная температура воздуха для отдельных пунктов определялась методом приведения."]
["Шимановск",975,23.5,27.6,25.9,40,12.9,"—",58,496,78,"СЗ",0]
["Экимчан",950,22.1,26.3,24.5,40,14.2,78,58,655,96,"В",0]
["Архангельская область"]
["Архангельск",1010,19.6,24,20.9,34,10.9,72,57,402,55,"СЗ",4]
["Борковская",990,17.9,22.3,20.3,35,14.2,74,60,435,76,"СЗ","—"]
["Емецк",1010,19.4,23.7,21.8,35,10.7,72,58,366,53,"С","—"]
["Койнас",1000,19,23.3,21.4,36,12,70,55,423,80,"СЗ",2.4]
["Мезень",1010,16.8,21.2,19.2,35,10.7,75,64,346,51,"С",3.8]
["Онега",1010,19.7,24.5,21.2,36,10.1,71,58,408,72,"СЗ",2.7]
["Астраханская область"]
["Астрахань",1015,28.4,32.1,31,40,11.1,55,36,126,73,"В",3.6]
["Верхний Баскунчак",1010,29,32.8,31.4,45,13.1,45,32,156,58,"З",0]
["Республика Башкортостан"]
["Белорецк",950,20,24.3,22.4,38,11.9,73,50,369,69,"З",0]
["Дуван",970,20.4,24.7,22.8,38,11.5,74,58,386,72,"С","—"]
["Мелеуз",990,23.8,27.9,26.2,41,13.1,66,49,298,78,"С",0]
["Уфа",990,23.3,27.3,24.2,39,10.7,72,54,362,58,"С",0]
["Янаул",1000,22.5,26.6,24.9,38,12.8,70,51,329,63,"СВ",0]
["Белгородская область"]
["Белгород",990,23.3,27.4,25.7,38,11.4,66,52,362,83,"СВ",4.1]
["Брянская область"]
["Брянск",990,20.4,24.7,22.8,38,9.7,73,53,420,"—","СЗ",0]
["Республика Бурятия"]
["Бабушкин",950,16.9,21.3,19.3,33,9,80,75,479,127,"З","—"]
["Баргузин",950,23.2,26.5,25,37,12.6,67,51,238,78,"З","—"]
["Багдарин",910,20.9,25.1,23.3,35,15.6,74,54,343,65,"С","—"]
["Кяхта",920,22.4,26.6,24.8,39,11.9,64,52,317,76,"С",0]
["Монды",870,19.3,23.6,21.7,34,14.5,73,52,343,80,"В",0]
["Нижнеангарск",950,18.6,23,21,35,10.3,77,66,298,58,"Ю",0]
["Сосново-Озерское",905,20.4,24.7,22.8,37,12.8,73,59,302,59,"З","—"]
["Уакит",890,18.8,23.1,21.2,30,13,70,52,362,"—","СЗ","—"]
["Улан-Удэ",950,23.5,28,25.9,40,13.2,65,47,228,92,"СЗ",0]
["Хоринск",930,"—","—",25.9,40,13.9,64,48,243,"—","З","—"]
["Владимирская область"]
["Владимир",995,20.8,25,23.3,37,9.8,72,57,413,109,"С",3.3]
["Муром",1000,22.7,26.8,23.3,37,10.6,70,53,383,69,"ЮЗ","—"]
["Волгоградская область"]
["Волгоград",1000,27.6,31.3,30,44,11.6,51,33,212,82,"СЗ",5.2]
["Котельниково",1005,28.4,32.3,30.8,42,13.8,51,34,261,51,"СЗ",3.1]
["Эльтон",1010,28.9,32.5,31.3,45,13.3,47,33,190,99,"СВ",0]
["Вологодская область"]
["Вологда",995,21.2,25.3,22.3,39,11,76,60,417,74,"З",0]
["Вытегра",1005,20,24.7,21.9,36,10.8,74,59,454,72,"СЗ",0]
["Никольск",995,20.3,24.6,22.7,37,11.8,75,58,425,58,"С","—"]
["Тотьма",995,20,24.3,22.4,37,11.5,75,60,460,69,"ЮЗ",3]
["Воронежская область"]
["Воронеж",1000,24.1,28.6,25.9,38,11.5,66,50,367,100,"С",3.3]
["Республика Дагестан"]
["Дербент",1015,25.8,29.8,28.2,38,7.3,67,65,214,113,"СЗ",0]
["Махачкала",1015,26.2,29,28.6,38,7.8,64,60,246,104,"ЮВ",4.9]
["Ивановская область"]
["Иваново",995,20.9,25.1,23.3,38,11.1,72,56,437,78,"З",2.8]
["Кинешма",1000,21.4,25.6,23.8,38,11.3,71,56,450,60,"ЮЗ","—"]
["Иркутская область"]
["Алыгджер",920,19.9,24.2,22.3,35,14.6,78,55,565,56,"С","—"]
["Бодайбо",975,21.9,27,26.1,40,14.6,74,55,387,62,"—","—"]
["Братск",970,21.1,25.3,23.5,33,10.6,72,56,311,102,"СЗ",0]
["Верхняя Гутара",910,19.5,23.8,21.9,36,15.4,78,54,526,63,"С","—"]
["Дубровское",955,23.1,27.2,25.5,38,14.2,74,52,364,56,"—","—"]
["Ербогачен",975,22,25.8,24.3,35,15,66,50,300,71,"ЮЗ",0]
["Жигалово",970,21.6,26.8,25.6,37,15.2,76,55,293,"—","З","—"]
["Зима",955,22.4,26.6,24.8,35,13.3,73,56,332,66,"СЗ",0]
["Ика",970,21.7,25.9,24.1,35,15.6,75,56,285,"—","З","—"]
["Илимск",975,23.1,27.2,25.5,38,15.3,74,52,336,52,"В","—"]
["Иркутск",955,21.8,25.6,24.7,36,13.4,74,58,402,82,"ЮВ",2.2]
["Ичера",980,22.7,26.8,25.1,36,14.2,74,52,351,"—","С","—"]
["Киренск",975,22.5,26.1,25.1,37,13.4,74,56,325,67,"ЮЗ",0]
["Мама",980,23.4,27.5,25.8,39,14.4,74,53,412,"—","СЗ","—"]
["Маркове",975,23.2,27.3,25.6,37,14.6,74,54,316,"—","З",0]
["Наканню",975,21.5,25.7,23.9,37,15.1,69,50,308,"—","—","—"]
["Невон",980,22.6,26.8,25,37,14.5,73,51,326,56,"ЮЗ","—"]
["Непа",970,21.8,26,24.2,39,14.3,76,56,320,"—","СЗ","—"]
["Орлинга",970,22.7,26.8,25.1,38,14.5,78,58,349,50,"С","—"]
["Перевоз",970,22.5,26.6,24.9,36,15.7,74,54,331,48,"СЗ","—"]
["Преображенка",975,22.1,26.3,24.5,36,14.8,72,53,313,56,"—","—"]
["Слюдянка",960,17.4,21.8,19.8,31,8.2,78,73,476,144,"ЮЗ",0]
["Тайшет",975,22.4,26.6,24.8,36,13.2,71,54,350,71,"З",0]
["Тулун",955,21.6,25.8,24,35,13.8,76,58,359,101,"СЗ",0]
["Усть-Ордынский — Бурятский АО",955,22.8,26.9,25.2,37,13.8,72,56,278,"—","СЗ","—"]
["Кабардино-Балкарская Республика"]
["Нальчик",970,24.6,28.6,27,39,10.4,68,54,505,"—","ЮЗ",0]
["Калининградская область"]
["Калининград",1010,21.2,24.7,22.4,36,9.3,77,63,508,110,"З",4.3]
["Республика Калмыкия — Хальмг Тангч"]
["Элиста",995,28.5,32,31,43,13,48,34,229,71,"З",0]
["Калужская область"]
["Калуга",990,21,25.2,23.4,38,10.7,76,59,441,89,"СЗ",0]
["Камчатская область"]
["Апука — Корякский АО",1010,10.8,15.5,13.2,25,5.5,88,82,254,57,"ЮЗ","—"]
["Ича — Корякский АО",1010,12.5,14.2,14.1,29,5,91,86,578,105,"Ю","—"]
["Ключи",1005,17.2,21,19.5,31,9.5,76,65,368,78,"В",0]
["Козыревск",1005,18.7,23,21.1,32,12.1,75,61,278,40,"С","—"]
["Корф — Корякский АО",1010,13.2,16,15.5,29,6.2,82,75,302,"—","Ю","—"]
["Лопатка, мыс",1005,9,13.8,11.4,20,3.5,97,95,629,72,"СЗ","—"]
["Мильково",995,18.9,23.2,21.3,32,12.3,76,61,329,51,"ЮЗ","—"]
["Начики",980,15.6,20.1,18,30,11,82,66,554,105,"ЮЗ",0]
["о. Беринга",1010,10.1,14.9,12.5,22,3.7,92,88,292,"—","Ю",7]
["Оссора — Корякский АО",1010,13.3,17.9,15.7,30,7.2,82,74,634,"—","ЮЗ","—"]
["Петропавловск-Камчатский",1000,14.4,19.2,16.8,29,6.2,82,75,754,207,"ЮВ",0]
["Семлячики",1010,13.6,18.2,16,31,5.7,85,81,864,"—","Ю",0]
["Соболево",1010,13.9,18.5,16.3,29,7.8,91,81,693,92,"Ю","—"]
["Кроноки",1010,13,17.6,15.4,28,7.5,88,81,548,"—","С","—"]
["Ука",1010,14.6,19.2,17,33,8.5,84,74,360,"—","СВ",0]
["Октябрьская",1010,11.5,16.5,13.9,28,4.4,93,89,389,67,"СЗ",5.2]
["Усть-Воямполка — Корякский АО",1010,11.3,16,13.7,29,6.4,90,85,421,65,"С",4.2]
["Усть-Камчатск",1010,13.2,18,15.6,30,6,86,77,386,58,"Ю",0]
["Усть-Хайрюзово",1010,13.1,18,15.5,30,6.9,89,82,479,61,"С",0]
["Карачаево-Черкесская Республика"]
["Черкесск",955,24.8,28.8,27.2,39,11.5,67,48,453,92,"Ю","—"]
["Республика Карелия"]
["Кемь",1010,16.8,21.9,17.8,32,7.3,77,69,332,40,"С",4.1]
["Лоухи",1000,17.4,21.8,19.8,33,10.6,71,58,383,60,"ЮЗ",3.1]
["Олонец",1010,19.7,24,29.1,36,11.6,74,59,647,97,"ЮЗ",3.1]
["Паданы",995,17.6,22,20,32,8.6,74,67,365,80,"З",3.2]
["Петрозаводск",1000,19,22.8,20.3,33,9,74,60,589,59,"ЮЗ",3.2]
["Реболы",990,18.2,22.6,20.6,33,8.9,70,58,400,25,"ЮЗ","—"]
["Кемеровская область"]
["Кемерово",990,22.7,26.8,25.1,37,12.9,73,56,335,46,"ЮЗ",0]
["Киселевск",975,22.5,26.6,24.9,38,11.9,72,56,338,49,"ЮЗ",0]
["Кондома",970,22.3,26.5,24.7,38,14.4,79,59,636,72,"Ю",0]
["Мариинск",995,22.1,26.2,24.5,37,12.4,74,57,346,69,"ЮЗ",0]
["Тайга",980,21.2,25.4,23.6,36,12.3,74,59,444,82,"ЮЗ",0]
["Тисуль",990,21.9,26.1,24.3,37,13.1,75,59,389,78,"ЮЗ","—"]
["Топки",975,21.4,25.6,23.8,37,10.9,73,58,423,55,"Ю","—"]
["Усть-Кабырза",965,22.2,26.4,24.6,37,14.1,78,56,621,"—","З","—"]
["Кировская область"]
["Вятка",995,21.8,25.7,23.1,37,10.1,70,57,415,137,"З",4]
["Нагорское",985,19.9,24.2,22.2,35,10.3,73,58,433,"—","СЗ","—"]
["Савали",1000,22,26.2,24.4,38,11.5,68,53,381,62,"СЗ","—"]
["Республика Коми"]
["Вендинга",1000,19.6,23.9,22,35,12.9,71,57,423,59,"С",0]
["Воркута",990,15.6,20.3,18,31,10.5,72,63,370,37,"С",4.8]
["Объячево",990,19.9,24.2,22.3,35,11,72,57,440,73,"Ю","—"]
["Петрунь",1000,16.8,21.2,19.2,33,10.8,72,60,349,38,"С","—"]
["Печора",1000,18.3,23.6,21.7,35,10.8,66,52,373,49,"С",3.5]
["Сыктывкар",1000,20,24.3,22.2,35,10.9,71,56,404,65,"С",3.8]
["Троицко-Печорск",1000,19.3,24.6,21.6,35,11.6,70,58,409,58,"СЗ",3]
["Усть-Уса",1000,17.1,21.5,19.5,32,10.1,71,61,344,50,"С","—"]
["Усть-Цильма",1000,18.2,22.9,19.7,34,9.9,71,57,383,66,"—","—"]
["Усть-Щугор",1000,18.6,23,21,35,13.7,70,56,432,52,"С",0]
["Ухта",990,18.9,23.2,21.3,35,10.7,69,52,379,62,"С",3.4]
["Костромская область"]
["Кострома",995,21.2,25.4,23.1,37,9.9,74,58,409,62,"—",4.2]
["Чухлома",990,20.1,24.4,22.5,36,10.6,75,60,456,86,"СЗ","—"]
["Шарья",995,20.7,24.9,23.1,36,11.6,74,59,471,"—","С",3.6]
["Краснодарский край"]
["Краснодар",1010,27.4,31.1,29.8,42,13.2,64,46,393,107,"СВ",0]
["Майкоп — Республика Адыгея",990,26.6,30.6,29,41,12.8,67,48,481,88,"Ю",2.1]
["Сочи",1010,24.8,27.8,26.6,39,7.5,77,68,768,245,"СВ",0]
["Тихорецк",1005,27.6,31.5,30,42,13.2,59,43,360,92,"В",0]
["Красноярский край"]
["Агата",975,18,22.4,20.4,33,13.4,70,58,360,48,"СВ","—"]
["Ачинск",980,21.8,26,24.2,39,12.4,70,55,366,99,"З",3.2]
["Байкит — Эвенкийский АО",980,20.6,25.2,24.5,39,15.1,71,52,355,49,"С",0]
["Боготол",975,21.4,25.6,23.8,34,11.7,73,59,380,99,"ЮЗ","—"]
["Богучаны",990,23.3,26.8,25.7,38,13.5,68,51,292,63,"З",0]
["Ванавара — Эвенкийский АО",980,21,26.3,24.7,35,15.6,70,50,317,64,"ЮЗ",0]
["Вельмо",990,21.9,26,24.3,35,15.3,73,55,469,47,"З","—"]
["Верхнеимбатск",1005,20.3,24.6,22.7,35,11.1,70,59,415,90,"СЗ",0]
["Волочанка",1005,15.6,20.1,18,36,9.2,70,61,256,"—","З",4.5]
["Диксон — Таймырский АО",1005,5.1,10.1,7.5,27,5.5,89,86,"—",31,"СВ",6.7]
["Дудинка — Таймырский АО",1005,15.7,20.4,18.1,32,9,71,64,314,48,"С",4]
["Енисейск",1000,21.8,26,24.5,37,12.9,73,55,360,74,"СЗ",0]
["Ессей — Эвенкийский АО",980,16.4,20.9,18.8,34,10.2,71,60,231,58,"С",0]
["Игарка",1005,17.9,22.4,20.3,33,9.9,69,60,366,55,"СЗ",4.4]
["Канск",985,23.1,27.2,25.5,36,13.3,69,51,279,74,"З",0]
["Кежма",985,22.5,26.6,24.9,36,13.9,69,53,245,64,"ЮЗ",0]
["Ключи",970,22.1,26.2,24.5,36,12.3,72,56,385,63,"З","—"]
["Красноярск",980,22,26.2,24.3,36,11.1,70,58,369,97,"З",0]
["Минусинск",980,24.3,28.2,26.6,39,13.6,68,51,296,54,"ЮЗ",0]
["Таимба",985,22.5,26.6,24.9,37,16.2,72,50,309,54,"З","—"]
["Троицкое",995,23,27.1,25.4,36,16.7,73,54,326,93,"ЮЗ","—"]
["Тура — Эвенкийский АО",990,20.2,25,23.5,38,13.8,68,48,292,50,"В",0]
["Туруханск",1005,18.3,23.5,21.4,36,10.5,69,57,376,61,"СЗ",4]
["Хатанга — Таймырский АО",1010,15.2,19.7,17.6,37,9,69,61,264,"—","СВ",5.2]
["Челюскин, мыс — Таймырский АО",1010,1.5,6.7,3.9,24,4.1,93,91,"—","—","В",5.8]
["Ярцево",1000,21.7,25.9,24.1,36,12.1,71,56,443,77,"ЮВ",0]
["Курганская область"]
["Курган",1000,23.8,28.1,25.2,41,11.9,69,54,286,87,"С","—"]
["Курская область"]
["Курск",985,21.6,25.8,24,37,10,69,56,375,144,"СВ",3.5]
["Липецкая область"]
["Липецк",995,23.5,27.5,25.9,39,11.6,66,51,382,69,"СЗ",4.1]
["Ленинградская область"]
["Тихвин",1005,20.1,24.4,22.5,36,11.9,75,59,467,75,"ЮЗ",0]
["Санкт-Петербург",1010,20.5,24.6,22,34,8.2,72,60,420,76,"З",0]
["Свирица",1010,19.4,23.7,21.8,34,9.7,76,64,405,76,"СЗ",4.4]
["Магаданская область"]
["Аркагала",930,18.3,22.7,20.7,32,15.1,67,51,257,42,"ЮВ",0]
["Брохово",1010,13.3,17.9,15.7,29,6.7,84,77,334,59,"ЮЗ",0]
["Магадан (Нагаева, бухта)",1000,12.8,16.1,14.9,26,6,83,83,412,98,"З",4.3]
["Омсукчан",960,17.1,21.5,19.5,33,12.6,65,51,217,32,"ЮЗ",0]
["Палатка",975,17,21.4,19.4,31,13.1,75,58,324,57,"З",0]
["Среднекан",985,19.8,24.1,22.2,36,13.6,68,52,298,46,"С",0]
["Сусуман",945,18.2,22.6,20.6,32,14.6,68,52,233,36,"СВ",0]
["Республика Марий Эл"]
["Йошкар-Ола",1000,21.8,25.8,24,39,11.6,73,55,387,57,"З",0]
["Республика Мордовия"]
["Саранск",990,22.5,26.6,24.9,39,11.5,69,51,361,128,"С",0]
["Московская область"]
["Дмитров",990,20.3,24.6,22.7,36,10,74,57,447,81,"СЗ",3.1]
["Кашира",995,20.7,24.9,23.1,39,9.6,72,57,393,59,"З","—"]
["Москва",995,22.6,26.3,23.6,37,10.5,70,56,443,61,"СЗ",0]
["Мурманская область"]
["Вайда-Губа",1010,11.6,16.3,14,32,6.5,82,78,323,52,"В","—"]
["Кандалакша",1010,15.8,21.1,19.1,31,8.8,72,61,357,51,"ЮВ",0]
["Ковдор",985,16.3,20.8,18.7,32,12.3,71,57,410,57,"С",0]
["Краснощелье",995,16.4,20.9,18.8,34,10.9,71,57,355,48,"СВ",0]
["Ловозеро",990,15.8,20.3,18.2,34,10.4,72,59,335,51,"ЮВ",0]
["Мончегорск",995,16.3,20.8,18.7,32,8.9,69,58,339,51,"Ю",0]
["Мурманск",1005,15.8,21.5,17.5,33,8.8,73,61,322,58,"С",3.8]
["Ниванкюль",1000,16.3,20.8,18.7,32,10.1,72,59,377,60,"СВ","—"]
["Пулозеро",995,16.1,20.6,18.5,33,10.1,71,60,319,72,"С",0]
["Пялица",1010,11.8,16.5,14.2,28,7.6,85,81,331,70,"СВ","—"]
["Териберка",1010,11.1,15.8,13.5,35,5.3,78,61,323,81,"СЗ","—"]
["Терско-Орловский",1005,11.1,15.8,13.5,34,7.9,85,80,302,62,"С","—"]
["Умба",1010,16.2,20.8,18.7,32,8.2,72,62,334,67,"ЮВ","—"]
["Юкспор",920,10.1,14.9,12.5,26,6.3,78,72,677,80,"С","—"]
["Нижегородская область"]
["Арзамас",990,22.2,26.4,24.6,37,11.4,70,53,384,"—","З",4.2]
["Выкса",1000,22.3,26.5,24.7,39,11.3,72,56,416,"—","ЮЗ","—"]
["Нижний Новгород",995,22.4,26.2,23.5,36,9.3,70,56,410,72,"З",0]
["Новгородская область"]
["Новгород",1010,20.3,24.6,22.7,34,11,76,61,424,72,"ЮЗ",4]
["Новосибирская область"]
["Барабинск",995,23.5,27.6,24.8,38,12.2,72,55,307,75,"СЗ",3.9]
["Болотное",985,22.4,26.6,24.8,36,11.5,72,57,372,64,"ЮЗ",2.9]
["Карасук",995,23.9,28,26.3,40,11.9,65,48,245,"—","З","—"]
["Кочки",990,22.9,27,25.3,39,13.3,73,54,295,68,"ЮЗ","—"]
["Купино",995,23.4,27.5,25.8,40,12.5,67,50,263,93,"З",4]
["Кыштовка",995,21.9,26.1,24.3,39,12.3,75,59,350,"—","С","—"]
["Новосибирск",995,22,26.4,24.6,38,11.4,72,56,338,95,"ЮЗ",0]
["Татарск",995,22.4,26.6,24.8,40,12.5,71,53,286,83,"СЗ",3.9]
["Чулым",990,22.3,26.5,24.7,40,12.4,73,56,310,56,"ЮЗ",3.4]
["Омская область"]
["Исиль-Куль",995,22,26.2,24.4,40,12,68,53,296,"—","СЗ",3.7]
["Омск",995,23.3,27.7,25,40,8,68,52,296,75,"СЗ",3.7]
["Тара",1000,21.1,25.3,23.5,39,11.7,75,62,403,79,"СЗ",3.7]
["Черлак",995,23.7,27.7,26.1,41,11.9,66,49,279,"—","СЗ",3.8]
["Оренбургская область"]
["Оренбург",1000,26.1,30,28.5,42,13.1,57,40,250,60,"С",3.9]
["Орловская область"]
["Орел",990,21.7,25.9,24.1,38,11.1,71,52,393,71,"СЗ",3.9]
["Пензенская область"]
["Земетчино",995,23.2,27.3,25.6,39,12.8,70,52,351,73,"СЗ",0]
["Пенза",985,22.9,27,25.3,39,10.9,67,50,378,"—","СЗ","—"]
["Пермская область"]
["Бисер",955,19,23.2,20.9,35,10.7,73,62,549,82,"З",0]
["Пермь",990,21.5,25.3,23.4,37,10.9,69,57,424,72,"С",0]
["Приморский край"]
["Анучино",985,25.1,29.1,27.5,39,11.8,78,61,574,146,"ЮЗ","—"]
["Астраханка",1000,23.1,27.2,25.5,37,8.7,81,70,508,109,"Ю","—"]
["Богополь",1005,22.7,26.8,25.1,38,10,84,73,594,145,"В","—"]
["Владивосток",1010,21.4,24.5,24.8,35,6.5,84,81,641,210,"ЮВ",4.7]
["Дальнереченск",1000,24.1,26.9,26.6,37,10,81,69,557,113,"ЮЗ",0]
["Мельничное",980,24.1,28.2,26.5,37,12.6,81,62,624,153,"В","—"]
["Партизанск",990,23,27.1,25.4,37,9.2,83,67,666,145,"Ю",0]
["Посьет",1005,22.3,26.5,24.7,36,6.3,87,84,609,198,"В","—"]
["Преображение",1005,20.4,24.7,22.8,34,6.5,87,82,617,161,"В","—"]
["Рудная Пристань",1010,20,24.3,22.4,38,7.2,86,83,664,175,"В",0]
["Чугуевка",985,25.1,29.1,27.5,38,13.1,79,61,593,96,"Ю","—"]
["Псковская область"]
["Великие Луки",1000,20.9,24.5,23.2,35,12,77,61,425,60,"ЮЗ",0]
["Псков",1005,21.4,24.7,22.9,36,10.7,74,57,424,75,"З",3.5]
["Ростовская область"]
["Миллерово",995,26,30,28.4,40,13,57,40,304,64,"СВ",0]
["Ростов-на-Дону",1005,26.1,30,29.1,40,12.2,58,45,336,100,"В",3.6]
["Таганрог",1010,25.8,29.8,28.2,40,9.1,61,51,308,140,"В","—"]
["Рязанская область"]
["Рязань",1000,21.7,25.9,24.1,38,10.5,71,54,349,91,"З",4.1]
["Самарская область"]
["Самара",995,24.6,28.5,25.9,39,12.8,63,49,307,72,"З",3.2]
["Саратовская область"]
["Саратов",1005,25.1,29.1,27.5,41,11.5,56,41,292,65,"СЗ",4.3]
["Сахалинская область"]
["Александровск-Сахалинский",1010,17.9,20.9,20.5,31,8,81,76,455,77,"ЮВ",3.7]
["Долинск",1005,19.8,24.1,22.2,35,9.3,85,73,654,222,"Ю",0]
["Кировское",1000,19.1,23.4,21.5,35,10.5,84,68,472,70,"Ю",0]
["Корсаков",1010,18.4,22.8,20.8,30,7.2,88,80,546,86,"СВ",0]
["Курильск",1010,16.9,21.3,19.3,31,7.2,89,84,642,170,"В",0]
["Макаров",1010,16.8,21.2,19.2,33,6.4,85,81,736,148,"Ю","—"]
["Невельск",995,18.5,22.8,20.9,30,6.2,85,81,579,135,"В",3.1]
["Ноглики",1010,17,21.4,19.4,37,9.2,85,72,481,87,"ЮВ","—"]
["Оха",1010,15.9,20.4,18.3,38,7.8,86,74,426,73,"ЮВ",4.9]
["Погиби",1010,16.1,20.6,18.5,27,5.8,88,81,425,87,"Ю","—"]
["Поронайск",1010,16.3,20.3,19.4,36,7,87,83,598,135,"Ю",0]
["Рыбновск",1010,16.4,20.9,18.8,29,6.9,86,80,390,74,"Ю","—"]
["Холмск",1000,18.6,23,21,30,6.6,83,77,559,137,"ЮВ",0]
["Южно-Курильск",1005,16.6,20,18.7,31,7.9,93,92,909,144,"СВ",0]
["Южно-Сахалинск",1010,19.7,24,22.1,34,9.2,86,72,559,116,"С",0]
["Свердловская область"]
["Верхотурье",995,21,25.2,23.4,36,12.1,71,56,381,58,"З","—"]
["Екатеринбург",980,22,25.6,23.1,38,10.6,68,56,383,94,"З",4]
["Ивдель",1000,20.7,24.7,22.7,35,11.9,70,57,381,91,"С","—"]
["Республика Северная Осетия"]
["Владикавказ",940,23,27.1,25.4,38,10.4,75,61,721,131,"Ю",0]
["Смоленская область"]
["Вязьма",985,19.4,23.7,21.8,36,10.1,76,60,454,69,"З","—"]
["Смоленск",985,20.8,24.3,22.3,35,10.2,77,62,457,67,"СЗ",3.2]
["Ставропольский край"]
["Арзгир",1000,29.1,32.9,31.5,43,13.5,52,35,264,67,"В",0]
["Ставрополь",965,25,29,27.4,40,9.8,59,47,457,"—","З",0]
["Тамбовская область"]
["Тамбов",995,23.2,27.3,25.6,38,11.2,67,49,366,60,"С",2.8]
["Республика Татарстан"]
["Бугульма",975,21.5,25.7,23.9,38,11.1,69,55,289,"—","СЗ",0]
["Елабуга",1000,29.9,27,25.3,40,11.3,67,51,354,68,"СЗ",3.7]
["Казань",1000,23.5,27.2,24.7,38,10.8,69,56,373,75,"СЗ",3.8]
["Тверская область"]
["Бежецк",995,19.8,24.1,22.2,35,10.4,76,60,416,78,"З",3.1]
["Тверь",995,20.6,24.8,23,36,11.1,75,59,444,68,"З",0]
["Ржев",990,20.1,24.4,22.5,36,10.5,77,61,439,70,"З","-"]
["Томская область"]
["Александровское  ",1000,20.3,24.6,22.7,35,10,73,60,402,61,"СЗ",0]
["Колпашево",1000,21.5,25.3,23.6,35,11.1,72,58,392,64,"СЗ",0]
["Средний Васюган",1000,21.3,25.5,23.7,37,11.4,73,58,431,56,"СЗ",2.7]
["Томск",990,21.7,26,23.7,36,11,74,59,406,76,"Ю",0]
["Усть-Озерное",995,22,26.2,24.4,36,12.4,72,55,421,96,"ЮЗ",0]
["Республика Тыва"]
["Кызыл",935,24.5,28.6,26.9,38,13.7,58,44,195,51,"С",0]
["Тульская область"]
["Тула",995,21.9,26.1,24.3,38,11,70,54,411,68,"СЗ",3.4]
["Тюменская область"]
["Березово — Ханты-Мансийский АО",1005,18.6,23.2,20.4,33,8.6,73,63,352,70,"С",4.2]
["Демьянское",1000,20.2,24.5,22.6,35,9.6,72,59,386,64,"С",0]
["Кондинское — Ханты Мансийский АО",1005,21.6,25.8,24,36,10.3,69,54,359,"—","СЗ",4]
["Леуши",1000,20.8,25.4,22.8,35,9.8,70,58,389,"—","ЮЗ","—"]
["Марресаля",1010,8.8,13.6,11.2,28,7.6,87,85,"—","—","СЗ","—"]
["Надым",1010,18.5,22.8,20.9,35,10.5,70,55,366,"—","С","—"]
["Октябрьское",1005,19.9,24.2,22.3,35,10,70,59,442,104,"С",3.4]
["Салехард",1010,16.3,20.8,18.7,31,10.7,71,62,310,52,"СВ",5.3]
["Сосьва",1005,19.9,24.2,22.3,35,12.9,68,53,376,"—","СВ","—"]
["Сургут — Ханты-Мансийский АО",1005,19.8,23.6,21.7,34,9.7,70,59,467,68,"С",4.5]
["Тарко-Сале — Ямало-Ненецкий АО",1000,18.8,23.1,21.2,36,10.5,69,56,375,86,"СЗ",0]
["Тобольск",1000,21.5,25.6,23.6,35,10.3,71,58,349,65,"СЗ",4.1]
["Тюмень",1000,21.6,25.8,24,38,11.3,74,58,342,111,"СЗ",0]
["Угут",1005,20.9,25.1,23.3,36,11.6,72,57,460,"—","С",0]
["Уренгой — Ямало-Ненецкий АО",1010,18.3,22.7,20.7,34,10.4,69,56,397,"—","С","—"]
["Ханты-Мансийск — Ханты Мансийский АО",1005,20.2,24.5,22.6,34,9.2,70,60,428,52,"СВ",4.9]
["Удмуртская Республика"]
["Глазов",995,21.2,25.4,23.6,37,11.8,71,55,437,62,"З",0]
["Ижевск",995,22.4,27,24.1,37,10.6,69,56,342,61,"З",0]
["Сарапул",995,22.2,26.4,24.6,38,11,67,53,371,73,"СЗ","—"]
["Ульяновская область"]
["Сурское",1000,22.7,26.8,25.1,38,12.7,71,53,344,86,"З","—"]
["Ульяновск",990,23.3,27.4,25.7,40,11.8,66,49,328,"—","—","—"]
["Хабаровский край"]
["Аян",1010,13.9,18,16.5,33,6.4,88,79,790,235,"СВ","—"]
["Байдуков",1010,16.3,20.8,18.7,29,6.2,87,82,480,"—","Ю","—"]
["Бикин",1000,24.8,28.8,27.2,38,11,80,66,597,130,"ЮВ",0]
["Бира",990,23.7,27.8,26.1,40,11.1,82,66,733,153,"В","—"]
["Биробиджан",995,23.6,27.7,26,39,11.2,84,69,746,"—","СВ","—"]
["Вяземский",1000,24,28.1,26.4,40,11.7,82,67,602,95,"ЮЗ",0]
["Гвасюги",985,24.3,28.4,26.7,41,13.3,84,64,850,95,"С","—"]
["Гроссевичи",1005,16.8,21.2,19.2,36,6.2,94,86,601,"—","ЮЗ","—"]
["Де-Кастри",1005,17.1,21.5,19.5,30,7.5,89,79,608,90,"В","—"]
["Джаорэ",1005,16.8,21.2,19.2,32,6.1,85,80,427,"—","—","—"]
["Екатерино-Никольское",1000,24.1,28.2,26.5,40,9.8,82,67,619,163,"СВ",0]
["Комсомольск-на-Амуре",1005,22.8,26.9,25.2,35,9.9,78,67,484,95,"Ю",0]
["Нижнетамбовское",1005,22.8,26.9,25.2,36,11.3,78,64,586,"—","СВ","—"]
["Николаевск-на-Амуре",1005,19.2,23,21.5,35,9.5,80,70,447,82,"В",3.4]
["Облучье",980,23.4,27.5,25.8,40,11.5,80,66,687,113,"ЮВ","—"]
["Охотск",1010,13.8,16.4,16.4,32,6.5,89,80,395,80,"ЮВ","—"]
["Им. Полины Осипенко",1000,22.2,26.4,24.6,37,12.8,78,63,410,102,"С","—"]
["Сизиман",1010,17,21.4,19.4,36,9.7,90,80,718,92,"В","—"]
["Советская Гавань",1010,19.2,23.5,21.6,39,9.2,86,71,641,140,"СВ","—"]
["Софийский прииск",905,20.2,24.5,22.6,32,14.3,77,58,657,89,"В",0]
["Средний Ургал",965,23.6,27.7,26,40,14.1,78,61,625,"—","—","—"]
["Троицкое",1005,22.9,27,25.3,39,9.5,80,70,549,78,"СВ","—"]
["Хабаровск",1000,23.5,26.9,25.7,40,8.6,78,67,556,99,"ЮЗ",4.6]
["Чумикан",1010,15.9,20.4,18.3,35,8.8,88,77,635,128,"СВ",0]
["Энкэн",1010,14.9,19.4,17.3,34,8,86,74,551,"—","ЮЗ","—"]
["Республика Хакассия"]
["Абакан",980,23.8,28.1,26.2,38,12.9,68,51,282,76,"—","—"]
["Шира",955,21.7,25.9,24.1,36,12.5,68,55,291,147,"ЮЗ",0]
["Челябинская область"]
["Челябинск",985,21.7,25.9,24.1,40,10.7,69,54,435,88,"СЗ",3.2]
["Чеченская Республика"]
["Грозный",995,29,31.9,30.7,41,12.7,66,44,367,90,"В",0]
["Читинская область"]
["Агинское",930,22.9,27,25.3,37,13.6,71,55,322,78,3,"—"]
["Акша",930,23.2,27.3,25.6,39,14.1,72,55,356,66,"СЗ",0]
["Александровский Завод",920,21.5,25.7,23.9,36,14.4,78,60,366,"—","ЮЗ","—"]
["Борзя",930,23.2,27.2,26,41,12.9,68,65,276,73,"СВ","—"]
["Дарасун",920,22,26.2,24.4,37,14.6,74,56,377,"—","СЗ","—"]
["Калакан",940,22.9,27,25.3,37,16.2,75,51,362,63,"СВ","—"]
["Красный Чикой",920,22.4,26.6,24.8,38,14.3,74,56,307,76,"СЗ","—"]
["Могоча",940,22,25.5,24.1,36,14.5,75,70,409,99,"СЗ",0]
["Нерчинск",950,24.3,28.4,26.7,40,13.5,69,52,289,64,"СВ",0]
["Нерчинский Завод",935,22.8,26.9,25.2,40,13.1,75,59,375,78,"СЗ",0]
["Средний Калар",925,21.6,25.8,24,36,16.6,76,53,351,64,"СВ","—"]
["Тунгокочен",920,21.5,25.7,23.9,35,13.5,76,54,354,66,"ЮЗ","—"]
["Тупик",935,22,26.2,24.4,36,15.6,76,55,460,"—","Ю","—"]
["Чара",940,20.2,25.1,23.6,35,14.8,72,67,325,54,"СВ","—"]
["Чита",935,22.8,26.9,25.2,38,14.2,71,53,316,51,"С",0]
["Чувашская Республика — Чаваш республики"]
["Порецкое",995,23.3,26.5,24.7,38,11.2,72,56,383,108,"ЮЗ",0]
["Чебоксары",1000,21.7,25.9,24.1,39,10.1,70,57,371,93,"З","—"]
["Чукотский АО (Магаданская область)"]
["Анадырь",1000,12.6,16.5,14.7,28,7,81,81,191,45,"ЮВ",5.7]
["Марково",1010,17,21.7,19.2,33,11.1,73,70,229,44,"СВ",0]
["Островное",1000,16.8,21.2,19.2,34,12.7,65,53,156,38,"СЗ",0]
["Усть-Олой",995,17,21.4,19.4,34,13.1,70,54,182,47,"СВ","—"]
["Эньмувеем",1000,16,20.5,18.4,33,11.7,70,60,203,34,"СЗ","—"]
["Республика Саха (Якутия)"]
["Алдан",925,19.7,24.2,22.6,35,11.5,67,66,503,75,"Ю",0]
["Аллах-Юнь",935,19.8,24.1,22.2,33,16.2,69,51,280,52,"Ю",0]
["Амга",990,23,27.1,25.4,39,16,66,48,198,66,"З",0]
["Батамай",1000,20.9,25.1,23.3,38,13,68,55,240,68,"З","—"]
["Бердигястях",980,21.5,25.7,23.9,36,16.7,66,49,207,36,"СЗ","—"]
["Буяга",975,22.7,26.8,25.1,38,16.9,72,50,255,34,"—","—"]
["Верхоянск",995,20.7,25,22.1,36,13.8,63,56,137,33,"СВ",0]
["Вилюйск",995,22.8,26.5,24.5,37,12.8,61,51,207,71,"С",0]
["Витим",985,22.2,26.3,25.1,37,14,72,63,306,57,"С",0]
["Воронцово",1010,14.9,19.4,17.3,34,9.8,70,60,196,41,"СЗ","—"]
["Джалинда",1000,17.3,21.7,19.7,35,12.1,67,56,227,48,"СЗ","—"]
["Джарджан",1005,17.9,22.2,20.3,37,10.3,66,57,268,40,"С",0]
["Джикимда",985,24,28.1,26.4,38,17.8,72,50,297,55,"—","—"]
["Дружина",1005,16.5,21,18.9,36,9.5,72,62,204,45,"С",0]
["Екючю",985,19.9,24.2,22.3,36,15.7,64,50,158,50,"С","—"]
["Жиганск",995,19.4,23.6,21.4,35,10.9,65,55,250,55,"С",4.2]
["Зырянка",1005,18.4,22.8,20.8,36,10.6,69,58,202,40,"С",0]
["Исить",995,21.2,25.2,24.7,37,13.3,69,67,238,63,"З",0]
["Иэма",925,17.2,21.6,19.6,32,13.9,69,56,236,69,"СЗ","—"]
["Крест-Хальджай",995,22.2,26.4,24.6,38,13.1,64,49,228,53,"З","—"]
["Кюсюр",1005,15.2,19.7,17.6,34,9.8,68,59,337,42,"СВ",0]
["Ленск",980,22.3,26.5,24.7,36,14.2,68,53,283,106,"З","—"]
["Нагорный",910,19.7,24,22.1,37,14.1,74,57,542,67,"С",0]
["Нера",945,20.1,24.4,22.5,34,13.3,60,46,208,36,"ЮЗ","—"]
["Нюрба",995,21.7,25.9,24.1,36,14.1,66,49,210,88,"СВ",0]
["Нюя",985,22.5,26.6,24.9,38,13.7,68,52,273,61,"З",0]
["Оймякон",920,17.9,23,21.6,33,16.7,61,47,185,39,"З",0]
["Олекминск",980,21.9,26,25.1,37,13.5,67,63,239,80,"СВ",0]
["Оленек",980,18.8,23.4,21.1,36,13.4,63,53,244,60,"СВ",0]
["Охотский Перевоз",990,21.8,26,24.2,37,14.3,71,54,275,45,"Ю",0]
["Сангар",995,21,25.2,23.4,35,10.8,64,55,261,58,"СЗ",0]
["Саскылах",1010,14.9,19.4,17.3,36,10.4,70,59,178,34,"СЗ","—"]
["Среднеколымск",1010,16.6,21,19,36,10.4,69,57,151,45,"СВ",0]
["Сунтар",990,21.5,26,24.7,36,14.5,65,52,215,81,"С",0]
["Сухана",1000,18.7,23,21.1,34,13.1,63,50,216,56,"С",0]
["Сюльдюкар",990,21.8,26,24.2,35,16.2,66,48,249,"—","СВ","—"]
["Сюрен-Кюель",920,16.8,21.2,19.2,32,12.3,67,54,303,56,"ЮЗ",0]
["Токо",910,20,24.3,22.4,33,17,75,54,420,55,"В","—"]
["Томмот",975,23.1,27.2,25.5,38,16.3,73,52,343,64,"С","—"]
["Томпо",965,19.8,25,23.2,36,15.5,67,49,252,55,"Ю",0]
["Туой-Хая",980,21.1,25.3,23.5,36,14.6,68,50,260,56,"С",0]
["Тяня",985,23.8,27.9,26.2,38,17.9,74,51,289,57,"СЗ","—"]
["Усть-Мая",990,21.3,25.9,24.6,36,13.7,67,51,237,55,"Ю",0]
["Усть-Миль",985,22.6,26.8,25,38,16.4,73,56,257,"—","В","—"]
["Усть-Мома",985,19.4,23.7,21.8,36,14.3,66,53,166,37,"СЗ",0]
["Чульман",910,19,23.4,23.7,35,15.7,70,64,471,83,"СЗ",0]
["Чурапча",985,22.5,26.6,24.9,37,14.5,65,46,208,48,"З","—"]
["Шелагонцы",980,19.5,23.8,21.9,35,15.9,66,52,244,70,"С",0]
["Эйик",975,18.4,22.8,20.8,33,11.7,66,54,211,52,"С","—"]
["Якутск",995,22.8,26.9,25.2,38,13.5,60,57,186,78,"СЗ",0]
["Ненецкий АО (Архангельская область)"]
["Варандей",1010,10.6,15.4,13,32,7.1,86,80,277,46,"СВ","—"]
["Индига",1010,11.8,16.5,14.2,31,7.6,84,78,302,48,"СЗ",5.4]
["Канин Нос",1005,9.6,14.4,11.4,31,4.9,88,83,248,85,"Ю",6.2]
["Коткино",1010,16.4,20.9,18.8,34,11.3,75,62,340,40,"СВ","—"]
["Нарьян-Мар",1010,15.2,19.7,17.6,33,9.2,75,61,307,54,"С",5.2]
["Ходовариха",1010,9.3,14.1,11.1,29,5.7,89,83,275,42,"СВ","—"]
["Хоседа-Хард",1000,16.4,20.9,18.8,34,12,73,57,318,51,"СЗ",4.4]
["Ярославская область"]
["Ярославль",1000,20.8,25,23.2,37,10.8,74,58,404,76,"С",3.9]
[]
["АЗЕРБАЙДЖАНСКАЯ РЕСПУБЛИКА"]
["Баку",1015,28,32,33,40,12.2,58,54,97,73,"С",4.9]
[]
["РЕСПУБЛИКА АРМЕНИЯ"]
["Ванадзор",865,"—","—",23.9,36,"—",74,58,475,53,"Ю",0]
["Горис",865,"—","—",24.1,35,"—",70,52,528,70,"СЗ",0]
["Ереван",910,"—","—",33.2,42,"—",45,"—",184,"—","СВ",0]
["Ехегнадзор",870,"—","—",31.3,39,"—",45,30,251,32,"ЮВ",0]
["Камо",805,"—","—",22.3,32,"—",73,52,375,69,"С",0]
["Кафан",935,"—","—",29.7,42,"—",60,41,397,76,"ЮВ",0]
["Севан",805,"—","—",21.9,35,"—",71,57,427,"—","СВ",0]
["Сисиан",840,"—","—",25.3,36,"—",64,44,272,54,"В",0]
["Спитак",845,"—","—",27.3,35,"—",70,50,369,53,"В",0]
["Степанаван",860,"—","—",23.3,35,"—",77,60,545,53,"З",0]
[]
["РЕСПУБЛИКА БЕЛАРУСЬ"]
["Брестская область"]
["Брест",1000,22.5,27,24,37,10.8,70,56,423,86,"З",2.9]
["Витебская область"]
["Витебск",995,21,25,23,35,10.3,74,61,463,107,"З",3.1]
["Полоцк",1000,21,26,23,34,10.6,"—",60,460,64,"З",2.9]
["Гомельская область"]
["Василевичи",1000,22.5,27,25,38,11.8,72,57,456,99,"З",0]
["Гомель",1000,22.5,27,24,38,10.5,69,55,436,90,"СЗ",3.4]
["Гродненская область"]
["Гродно",1000,22,26.5,24,36,10.6,73,57,410,110,"З",0]
["Минская область"]
["Минск",990,21,25.5,23,35,10.3,70,58,470,74,"СЗ",2]
["Могилевская область"]
["Горки",990,21.5,25,23,36,10,75,59,462,97,"З;СЗ",3.1]
["Могилев",990,21.5,26,23,36,10.8,73,58,459,74,"З",3.7]
[]
["ГРУЗИЯ"]
["Ахалкалаки",825,20,25,21.7,37,14.6,72,47,"—",63,"С",1.5]
["Казбеги",645,"—","—",6.8,17,6.2,77,82,"—",113,"З",1.8]
["Крестовый перевал",760,14,20,15.4,25,8.1,85,77,"—",117,"СВ",0.8]
["Мамисонский перевал",720,11,18,12.2,25,7.9,83,75,"—",114,"З",2.5]
["Местиа",855,21,26,23,38,15.2,72,46,"—",145,"ЮЗ",0.2]
["Мта-Сабуети",875,20,25,22,32,10.6,87,75,"—",84,"З",2.4]
["Поти","—",25,32,30.1,39,7.1,84,74,"—",223,"ЮЗ",1]
["Сакара",1000,26,33,30.7,42,11.1,74,58,"—",94,"З",0.3]
["Самтредиа","—",26,33,30.4,41,9.7,80,"—","—",164,"З",0.9]
["Тбилиси",970,27,34,32.6,41,12,58,41,"—",139,"СЗ",0.9]
["Телави","—",26,33,30.9,38,11.4,65,50,"—",100,"З",1]
["Цхинвали","—",23,30,27.5,36,11.6,69,53,"—",89,"ЮВ",0.5]
["Шираки",950,26,32,30.3,39,15,66,46,"—",134,"В",1]
["Абхазская Республика"]
["Гудаута","—",32,26,30.4,39,8.5,78,67,"—",168,"СВ",1.1]
["Псху",935,29,23,26.3,41,13.6,80,60,"—",155,"ЮВ",0.1]
["Сухуми",1000,32,25,30.1,40,7.5,77,67,"—",169,"З",1]
["Аджарская Республика"]
["Батуми",1015,32,26,30.2,38,6.6,79,71,"—",276,"ЮЗ",1.1]
["Хуло","—",28,21,24.9,39,10.6,78,62,"—",133,"Ю",1]
[]
["РЕСПУБЛИКА КАЗАХСТАН"]
["Акмолинская область",null,null,null,"|"]
["Астана",980,25.5,29.5,27,39,13.6,57,40,238,"—","СВ",3.7]
["Атбасар","—",25.9,29.9,26.9,40,14.1,59,40,218,"—","СЗ",4.7]
["Актюбинская область"]
["Актюбинск","—",27.3,31.7,29.2,42,13.9,51,"—",192,"—","СЗ",2.6]
["Караулкельды","—","—","—",31.1,42,13.3,"—","—",143,"—","З,СЗ",3.2]
["Уил",1005,29.8,33.5,31.3,43,14.1,42,"—",146,"—","СЗ",63]
["Челкар","—","—",null,32.1,43,14.6,41,"—",113,"—","С",4.3]
["Алматинская область"]
["Алматы",920,28.2,31.5,29.7,43,12.1,45,38,403,"—","Ю",1.6]
["Баканас","—","—","—",33.4,44,16.1,39,"—","—","—","СВ",2.8]
["Атырауская область"]
["Атырау",1020,31.2,34.2,32.1,43,13.1,46,29,113,"—","ЮЗ,",4.7]
[{"$nulls":11},"СЗ"]
["Ганюшкино","—","—","—",31.2,40,13,57,"—",112,"—","ЮЗ",4.1]
["Восточно-Казахстанская область"]
["Зайсан","—",26.8,30.7,28.4,40,11,44,38,237,"—","—","—"]
["Зыряновск","—","—","—",26.9,40,15.9,"—","—",387,"—","—","—"]
["Катон-Карагай","—","-","—",23.1,36,12.8,67,"—",360,"—","—","—"]
["Лениногорск","—","—","—",23.9,37,14,69,"—",549,"—","В",1.6]
["Усть-Каменогорск","—","—","—",28.2,43,14.6,64,"—",332,"—","СЗ",3.5]
["Шемонаиха","—","-","—",27.3,42,14.1,64,"—",308,"—","С",4.1]
["Джамбулская область"]
["Джамбул","—","—","—",31.9,44,15.8,40,"—",169,"—","С",2.5]
["Фурмановка","—","—","—",33.1,46,17.3,44,"—",104,"—","СВ",3.6]
["Джезказганская область"]
["Балхаш",980,26.6,29.8,28.7,41,10.7,"—",46,76,"—","СВ",4.4]
["Карсакпай","—",27.4,31.8,29.8,41,14.2,42,30,115,"—","—","—"]
["Западно-Казахстанская область"]
["Джамбейты","—","—","—",30.8,44,15,47,"—",172,"—","СЗ",4]
["Уральск","—",27.8,31.7,29.5,42,14.4,"—",38,195,"—","СЗ",2.6]
["Карагандинская область"]
["Караганда","—",25.8,29.5,26.8,39,13.2,53,"—",223,"—","С",3.8]
["Каркаралинск","—","—","—",25,37,14.7,52,"—",262,"—","СЗ",4.6]
["Кзыл-Ординская область"]
["Аральское море","—",30.4,34,32,45,12.1,40,"—",78,"—","С",5]
["Казалинск",1010,"—","—",32.9,44,14,44,"—",73,"—","СЗ",2.5]
["Кзыл-Орда","—","—","—",34.1,46,15.7,37,"—",56,"—","С;СВ",3.1]
["Кокчетавская область"]
["Кокчетав","—","—","—",25.8,38,14.4,"—","—",250,"—","З",4.5]
["Кустанайская область"]
["Кустанай",1000,25.2,29.6,26.7,42,13.2,62,44,237,"—","—","—"]
["Мангистауская область"]
["Форт-Шевченко",1020,"—","—",29.5,41,7.7,63,"—",111,"—","—","—"]
["Павлодарская область"]
["Баянаул","—","—","—",26.2,38,11.6,54,"—",273,"—","З",4.5]
["Павлодар","—","—","—",27.7,41,13.1,58,"—",192,"—","С",4.4]
["Северо-Казахстанская область"]
["Петропавловск",1000,24.4,28.4,24.9,40,11.9,68,53,277,null,"СЗ",4.6]
["Семипалатинская область"]
["Аягуз","—","—","—",28.2,40,15.7,50,"—",192,"—","—","—"]
["Бахты","—","—","—",30.9,42,17.3,52,"—",153,"—","—","—"]
["Кокпекты","—","—","—",28,42,15.4,56,"—",187,"—","—","—"]
["Семипалатинск","—","—","—",28.9,42,14.2,58,"—",197,"—","—","—"]
["Талды-Курганская область"]
["Жаркемт",935,24.7,31.5,31.7,42,15.7,"—",35,116,"—","—","—"]
["Талды-Курган",null,null,null,30.8,44,15.5,"—","—",224,"—","—","—"]
["Тургайская область"]
["Амангельды","—","—","—",30.3,42,14.9,50,"—",149,"—","СВ",4.4]
["Тургай",1005,29.7,33.5,31,43,13.6,44,30,134,"—","СВ",4.9]
["Южно-Казахстанская область"]
["Туркестан","—",33.6,37.1,36.4,49,17.7,"—",17,72,"—","СВ",3.2]
["Чимкент","—","—","—",33,44,14.9,"—","—",208,"—","В",2.4]
[]
["КЫРГЫЗСКАЯ РЕСПУБЛИКА"]
["Иссык-Кульская область"]
["Каракол","—","—","—","—",34,13.9,61,45,352,61,"СВ",1.1]
["Чолпон-Ата","—","—","—","—",31,"—",66,56,231,40,"З",0.9]
["Нарынская область"]
["Кочкорка","—","—","—","—",35,"—",60,36,209,30,"В",0.8]
["Нарын","—","—","—","—",35,14.7,50,34,254,42,"Ю",1.6]
["Сусамыр","—","—","—","—",33,20.7,63,35,290,38,"ЮЗ",1.1]
["Ошская область"]
["Гульча","—","—","—","—",37,"—",55,31,325,70,"—","—"]
["Ош","—","—","—","—",39,"—",44,29,191,63,"З",1.7]
["Хайдаркан","—","—","—","—",33,"—",42,32,323,54,"—","—"]
["Таласская область"]
["Талас","—","—","—","—",40,"—",51,34,216,"—","СЗ",1.9]
["Чуйская область"]
["Бишкек","—","—","—","—",42,14.2,44,31,287,70,"З",1.7]
[]
["РЕСПУБЛИКА МОЛДОВА"]
["Кишинев",995,31,26,28.1,39,12,63,49,346,218,"СЗ",2.7]
[]
["РЕСПУБЛИКА ТАДЖИКИСТАН"]
["Душанбе",795,38,34,33.9,43,"—",17.8,24,247,24,"З",1.3]
[]
["ТУРКМЕНИСТАН"]
["Ахалская область"]
["Ашхабад",990,40,35,38.2,48,15.1,35,22,104,80,"СЗ",1.2]
["Гаудан",850,30,24,27.6,38,11.8,38,30,183,85,"С",1.8]
["Серахс",980,41,35,38.4,47,15.5,24,14,58,53,"СЗ",2.6]
["Теджен",990,41,35,38.4,48,16.1,30,17,57,49,"СЗ",2.7]
["Балканская область"]
["Гасанкули",1020,33,28,31.9,46,8.3,71,58,85,79,"З",2.6]
["Казанджик",1010,41,35,38.5,48,13.1,33,21,76,62,"В",1.9]
["Кизиларват",1005,40,35,38.4,47,13.5,38,28,103,77,"В",2.8]
["Кизилатрек",1020,38,32,36.3,48,13,58,34,76,91,"З",1.9]
["Небитдаг",1015,41,35,38.5,48,12.4,36,22,70,55,"В",3.2]
["Туркменбаши",1005,37,30,34.9,45,12.7,45,31,62,68,"СЗ",2.6]
["Чагыл",1005,40,33,38.2,48,15.1,33,23,60,38,"В",2.4]
["Марыйская область"]
["Байрамали",985,40,35,38.5,48,15.8,27,18,55,51,"С",2.1]
["Иолотань",985,40,34,37.2,46,17.7,37,20,48,40,"СЗ",1.8]
["Кушка",945,38,32,36.5,46,17.9,26,14,67,71,"СВ",2.4]
["Мары",990,41,36,38.8,46,16.8,29,15,47,65,"С",2.3]
["Тахтабазар",975,42,36,39.4,48,17.5,23,14,60,63,"С",2.9]
["Ташаузская область"]
["Ташауз",1005,38,32,36.2,46,14.9,41,25,49,74,"С",1.9]
["Чарджоуская область"]
["Дарганата",1000,38,33,36.6,47,16.1,41,28,60,60,"С",1.9]
["Керки",985,40,34,38.4,46,16.7,37,24,46,39,"СЗ",1.7]
["Репетек",990,42,36,39.9,50,18.6,23,11,38,49,"С",2.9]
["Чарджоу",995,38,33,36.8,45,15.2,36,22,39,63,"С",3.1]
[]
["РЕСПУБЛИКА УЗБЕКИСТАН"]
["Андижанская область"]
["Андижан",970,32.5,36.4,35.1,42,15.5,"—","—","—",64,"—",0]
["Бухарская область"]
["Бухара",990,34.1,38.4,36.7,46,16.4,"—","—","—",35,"—",0]
["Джизакская область"]
["Галляарал",950,33.3,37.5,35.4,43,20,"—","—","—",62,"—",0]
["Джизак",970,33.6,37,35.8,45,15.1,"—",null,"—",69,"—",0]
["Каракалпакстан"]
["Каракалпакия",1010,33.2,33.7,34.2,46,16.5,"—","—","—",51,"—",0]
["Муйнак",1010,30.2,35.1,31.8,44,9.7,"—","—","—",66,"-",3.4]
["Нукус",1010,33.4,37.3,35.5,45,15.7,"—","—","—",48,"—",4.4]
["Чимбай",1010,34.7,39.2,34.2,44,15.1,"—","—","—",33,"—",0]
["Кашкадарьинская область"]
["Гузар",950,35.8,40.1,38.1,48,16.8,"—","—","—","—","—",0]
["Мубарек",990,37.2,41,39.5,49,17.3,"—","—","—","—","—",4.3]
["Навоийская область"]
["Навои",970,33.9,38.2,36,46,17.1,"—","—","—",38,"—",0]
["Нурата",950,33.8,37.8,35.3,47,16.1,"—","—","—",47,"—",0]
["Наманганская область"]
["Касансай",910,32.9,36.7,32.8,41,13.5,"—","—","—",76,"—",0]
["Наманган",970,32.1,35.7,34.9,42,14.6,"—","—","—","—","—",0]
["Самаркандская область"]
["Каттакурган",950,33.1,37.2,35.8,44,15.6,"—","—","—","—","—",0]
["Самарканд",930,31.7,36,33.7,42,16.5,"—","—","—","—","—",0]
["Сурхандарьинская область"]
["Денау",950,33.7,37.4,36.9,45,16.7,"—","—","—","—","—",0]
["Термез",970,38.2,42.2,39.4,47,18.7,"—",null,"—",37,"—",0]
["Шерабад",970,36.2,40,39.1,47,14.9,"—","—","—","—","—",3.1]
["Сырдарьинская область"]
["Сырдарья",990,33.1,37.1,36,45,18.7,"—","—","—",53,"—",0]
["Ташкентская область"]
["Ташкент",950,33,37.5,35.4,45,16.8,"—","—","—",50,null,1.4]
["Чарвак",910,29.8,34.3,31.9,42,14.8,"—",null,null,99,null,0]
["Ферганская область"]
["Коканд",970,32.3,35.8,34.8,42,15.3,"—",null,"—","—","—",0]
["Фергана",950,32,35.9,34.3,42,15.4,"—","—","—",85,"—",0]
["Хорезмская область"]
["Ургенч",1010,33.5,37.6,35.4,45,14.6,"—","—","—",42,"—",0]
[]
["УКРАИНА"]
["Винницкая область"]
["Винница",980,27,23,24,38,"—","—","—","—",112,"СЗ",1.3]
["Волынская область"]
["Ковель",995,27,23,23.7,37,"—","—","—","—",122,"З",1.4]
["Луцк",990,26,22,23.6,36,"—","—","—","—",114,"З",1.9]
["Днепропетровская область"]
["Днепропетровск",1000,31,27,27.4,40,"—","—","—","—",82,"С",2.6]
["Комиссаровка",1005,30,26,26.5,39,"—","—","—","—",91,"С",1.8]
["Кривой Рог","—",31,26,27.2,38,"—","—","—","—",75,"С",2.6]
["Донецкая область"]
["Донецк",990,30,26,26.9,39,"—","—","—","—",125,"СВ",2.3]
["Житомирская область"]
["Житомир",990,26,22,23.7,38,"—","—","—","—",180,"—",1.7]
["Овруч",995,26,21,23.8,38,"—","—","—","—",158,"СЗ",0.9]
["Закарпатская область"]
["Ужгород",1000,27,24,25.9,39,"—","—","—","—",75,"В",1.5]
["Запорожская область"]
["Запорожье",1010,31,27,28.1,40,"—","—","—","—",120,"С",1.1]
["Кирилловка",990,29,26,26.8,38,"—","—","—","—",114,"С",1.9]
["Ивано-Франковская область"]
["Ивано-Франковск",985,26,21,23.6,37,"—","—","—","—",93,"З",1.4]
["Киевская область"]
["Киев",995,29,24,25.2,39,"—","—","—","—",103,"С",1.6]
["Кировоградская область"]
["Гайворон","—",27,24,25.4,39,"—","—","—","—",95,"СЗ",1.2]
["Знаменка",995,28,24,25.8,38,"—","—","—","—",136,"С",1.5]
["Кировоград",995,29,25,25.9,39,"—","—","—","—",122,"СЗ",2.8]
["Луганская область"]
["Луганск",1010,30,26,27.8,41,"—","—","—","—",80,"З",1.4]
["Львовская область"]
["Львов",975,26,22,22.9,37,"—","—","—","—",92,"З",2]
["Николаевская область"]
["Николаев",1010,31,26,28.5,39,"—","—","—","—",144,"С",2.1]
["Одесская область"]
["Измаил",1015,27,24,25.8,38,"—","—","—","—",76,"С",2.3]
["Любашевка",995,29,24,25.9,37,"—","—","—","—",102,"С",2.1]
["Одесса",1010,28,24,25.4,38,"—","—","—","—",103,"С",2.1]
["Раздельное",1000,30,26,27,37,"—","—","—","—",106,"СЗ",1.8]
["Сарата","—",31,27,27.7,41,"—","—","—","—",100,"С",1.5]
["Полтавская область"]
["Лубны",1000,27,24,25.7,38,"—","—","—","—",84,"СЗ",1.5]
["Полтава",995,29,25,26,38,"—","—","—","—",178,"З",1.7]
["Ровенская область"]
["Ровно",1000,26,22,23.5,37,"—","—","—","—",66,"З",2.2]
["Сарны",1000,26,23,24,38,"—","—","—","—",106,"З",1.1]
["Сумская область"]
["Ромны",995,27,23,24.9,39,"—","—","—","—",86,"СЗ",1.2]
["Сумы",995,27,23,25.1,40,"—","—","—","—",89,"СЗ",2]
["Тернопольская область"]
["Тернополь",975,25,21,23,37,"—","—","—","—",106,"СЗ",1.3]
["Харьковская область"]
["Лозовая",995,30,26,26.8,38,"—","—","—","—",75,"СВ",0.7]
["Харьков",1000,29,25,26.4,39,"—","—","—","—",83,"С",1.2]
["Херсонская область"]
["Аскания-Нова",1010,31,27,28.6,40,"—","—","—","—",123,"С",2.4]
["Геническ",1015,29,25,27.1,38,"—","—","—","—",114,"С",2.6]
["Херсон",1010,30,26,28,39,"—","—","—","—",86,"С",2.3]
["Хмельницкая область"]
["Хмельницкий",980,26,20,23.7,37,"—","—","—",null,106,"СЗ",1.4]
["Черкасская область"]
["Золотоноша",1005,29,24,25.6,39,"—","—","—","—",89,"СЗ",1.8]
["Умань",990,29,23,24.8,38,"—","—","—","—",155,"СЗ",1.5]
["Черниговская область"]
["Чернигов",1000,28,23,24.5,39,"—","—","—","—",78,"С",2.1]
["Черновицкая область"]
["Черновцы",990,26,23,24.5,38,"—","—","—","—",117,"СЗ",2]
["Автономная Республика Крым"]
["Ай-Петри",880,23,19,20.4,30,"—","—","—","—",215,"СЗ",3.3]
["Клепинино",1010,30,27,28.3,41,"—","—","—","—",114,"СЗ",1.9]
["Симферополь",990,29,26,27.6,39,"—","—","—","—",122,"В",2.7]
["Феодосия",1015,29,25,27.5,38,"—","—","—","—",109,"СЗ",2.4]
["Ялта",1010,31,26,27.3,37,"—","—","—","—",189,"З",1.1]
[]
[]
[]
[]
["Таблица 3— СРЕДНЯЯ МЕСЯЧНАЯ И ГОДОВАЯ ТЕМПЕРАТУРА ВОЗДУХА, °С"]
[]
["Республика, край, область, пункт","I","II","III","IV","V","VI","VII","VIII","IX","X","XI","XII","Год"]
[1,2,3,4,5,6,7,8,9,10,11,12,13,14]
[]
["РОССИЙСКАЯ ФЕДЕРАЦИЯ"]
["Республика Адыгея"]
["Майкоп",-1.4,0.3,4.1,11.3,16.5,19.7,22.2,21.9,17.1,11.2,6.2,1.4,10.9]
["Республика Алтай"]
["Алейск",-17.6,-16.3,-8.7,3.3,12.2,18.4,20.3,17.2,11.3,3.2,-7.5,-15.1,1.7]
["Барнаул",-17.5,-16.1,-9.1,2.1,11.4,17.7,19.8,16.9,10.8,2.5,-7.9,-15,1.3]
["Беля",-9.2,-8.1,-3.2,3.2,9.5,14.6,16.9,15.5,10.7,4.1,-3.2,-7.9,3.6]
["Бийск",-17.7,-16.5,-9.2,2.3,11.3,17.2,19.2,16.3,10.5,2.6,-8.1,-15.1,1.1]
["Змеиногорск",-15.1,-14.4,-7.9,2.9,11.7,17.3,19.2,16.6,11.3,3.5,-6.6,-13.2,2.1]
["Катанда",-22.8,-18.8,-9.2,2.3,9.5,14.2,15.5,13.3,7.9,0.2,-11.4,-19.9,-1.6]
["Кош-Агач",-30.5,-26.8,-15,-1.4,6.2,12.3,14,12,5.8,-3.8,-17.1,-26.9,-5.9]
["Онгудай",-21.1,-17.5,-7.2,3.5,10,14.9,16.3,13.9,8.5,1.1,-10.1,-18.3,-0.5]
["Родино",-17.7,-16.9,-9.8,3.3,12.5,18.6,20.5,17.4,11.6,3,-7.4,-15.1,1.7]
["Рубцовск",-17.5,-16.4,-8.9,3.6,12.6,18.7,20.5,17.7,11.8,3.7,-7.1,-14.9,2]
["Славгород",-18.9,-18.2,-10.6,3,12.5,18.9,20.8,17.6,11.8,3,-7.8,-15.9,1.4]
["Тогул",-16.5,-15.3,-8.7,1.7,10.5,16.7,18.8,15.8,10.3,2.4,-8.1,-15,1.1]
["Амурская область"]
["Архара",-26.7,-21.8,-10.7,2.5,11,17.2,20.9,18.8,11.9,2.4,-12,-23.6,-0.8]
["Белогорск",-27.1,-20.7,-10.9,1.8,10.3,17.4,21.1,18.7,11.7,1.3,-13.5,-24,-1.2]
["Благовещенск",-24.1,-18.7,-9.1,2.7,11.1,17.9,21.4,19.1,12.2,2.2,-11.5,-21.8,0.1]
["Бомнак",-32.2,-24.8,-13.1,-1.6,7.9,14.7,17.8,15.3,8.5,-2.8,-20,-30.7,-5.1]
["Братолюбовка",-28,-21.8,-12.1,0.8,9.5,16.3,19.9,17.6,10.8,0.5,-14.3,-25.3,-2.2]
["Бысса",-30.7,-24.3,-12.8,-0.4,8.8,15.2,18.7,16.2,9.1,-1,-16.8,-28.1,-3.8]
["Гош",-31.2,-24.6,-14,0.3,9.1,15.9,19.3,16.9,9.9,-0.6,-16.3,-28.2,-3.6]
["Дамбуки",-31.1,-24.9,-15.1,-1.9,7.5,14.4,17.9,15.3,8.2,-3.3,-18.8,-28.9,-5.1]
["Ерофей Павлович",-27.6,-22,-13,-1.2,7.5,15,18.3,15,7.9,-3.4,-17.6,-26.3,-4]
["Завитинск",-26.9,-20.9,-11.6,1.3,9.7,16.7,20.3,18.1,11.3,1.1,-13.4,-24,-1.5]
["Зея",-30.1,-23.8,-13.6,-0.6,8.4,15.3,18.6,15.7,9,-2.4,-17.8,-28,-4.1]
["Норск",-31.8,-25.1,-13.3,0.2,9.4,16,19.3,17,9.9,-0.3,-16.8,-29,-3.7]
["Огорон",-29.3,-23.1,-13.9,2.3,7,13.8,17.1,14.5,8,-3.3,-18,-27.3,-4.7]
["Поярково",-26.9,-21.6,-11.5,2.1,10.4,17.1,20.9,18.8,11.9,1.8,-12.4,-23.7,-1.1]
["Свободный",-27.7,-21.6,-12.1,1,9.6,16.6,20.2,17.7,10.6,0,-14.9,-25.4,-2.2]
["Сковородино",-29.1,-23.4,-14.1,-1.8,7.2,14.5,18,15,7.7,-3.8,-18.4,-27.7,-4.7]
["Средняя Нюкжа",-34.7,-28.9,-18.4,-5.4,5.3,13.2,16.8,13.4,5.7,-6.6,-22.9,-32.9,-8]
["Тыган-Уркан",-26.4,-21.6,-13.4,-1.5,7.5,14.6,18.1,15.1,7.9,-3.4,-17.2,-25.2,-3.8]
["Тында",-31.7,-25.9,-16.2,-3.8,6,13.4,17.1,13.9,6.3,-5.7,-21.5,-30.2,-6.5]
["Унаха",-30,-24.5,-15.9,-3.5,6.2,13.6,17.2,14.1,6.9,-5.1,-20.2,-28.3,-5.8]
["Усть-Нюкжа",-32.3,-26.4,-15.2,-3.1,6.5,14.3,17.6,14.3,6.8,-4.9,-21.2,-31.1,-6.2]
["Черняево",-27.9,-22.4,-12.5,0.2,8.8,16.1,19.6,16.8,9.7,-1.2,-16,-25.9,-2.9]
["Шимановск",-27.7,-21.9,-12.2,0.6,9.1,16.1,19.7,16.9,10,-0.8,-15.7,-25.3,-2.6]
["Экимчан",-33.1,-24.8,-14.9,-3.2,6,13,16.8,14.5,7.7,-3.5,-19.3,-30.5,-5.9]
["Архангельская область"]
["Архангельск",-12.9,-12.5,-8,-0.9,6,12.4,15.6,13.6,7.9,1.5,-4.1,-9.5,0.8]
["Борковская",-17.8,-16.4,-11.2,-2.9,3.1,10.2,13.5,11,5.5,-1.7,-8.1,-13.9,-2.4]
["Емецк",-14.1,-12.8,-7.3,-0.1,6.6,13.4,16.1,13.9,8,1.2,-4.5,-10.2,0.9]
["Койнас",-16.5,-15,-9.6,-1.3,4.6,11.8,15.2,12.7,6.6,-0.3,-6.8,-12.9,-1]
["Мезень",-14.3,-13.7,-9.5,-2.6,3.4,9.9,13.6,11.9,6.6,-0.2,-6.2,-11.4,-1.1]
["Онега",-12,-11.6,-7.2,0.1,6.4,12.7,15.9,13.9,8.4,1.9,-3.6,9,1.3]
["Астраханская область"]
["Астрахань",-6.7,-5.6,0.4,9.9,18,22.8,25.3,23.6,17.3,9.6,2.4,-3.2,9.5]
["Верхний Баскунчак",-9.5,-9.1,-2.1,9.6,17.4,22.3,25.6,23.5,16.6,7.6,0.5,-5.7,8]
["Республика Башкортостан"]
["Белорецк",-16.2,-14.4,-7.8,2.7,10.2,14.5,16,14.2,8.7,0.7,-7.4,-13.8,0.6]
["Дуван",-15.7,-14.3,-7.5,2.8,10.6,15.3,17,14.8,9.3,1.1,-6.7,-12.6,1.2]
["Мелеуз",-15.5,-14.4,-7.5,4.6,13.6,17.8,19.6,17.9,11.7,3.2,-5.1,-11.8,2.8]
["Уфа",-14.9,-13.7,-6.7,4.4,13.3,17.3,18.9,16.8,11.1,2.8,-5.1,-11.2,2.8]
["Янаул",-15.5,-13.7,-7.1,2.9,11.2,15.1,17.1,14.5,9.2,0.8,-6.1,-11.7,1.5]
["Белгородская область"]
["Белгород",-8.5,-6.4,-2.5,7.5,14.6,17.9,19.9,18.7,12.9,6.4,0.3,-4.5,6.4]
["Брянская область"]
["Брянск",-9.1,-8.4,-3.2,5.9,12.8,16.7,18.1,16.9,11.5,5,-0.4,-5.2,5.1]
["Республика Бурятия"]
["Бабушкин",-16.4,-16.6,-9.7,-0.7,5.2,10.7,14.2,14.2,8.9,2.5,-5.1,-10.5,-0.3]
["Баргузин",-27.4,-23.7,-12.1,-0.3,7.8,15.1,18.4,15.9,8.6,-0.6,-12.8,-23.2,-2.9]
["Багдарин",-29.4,-25.2,-15.4,-3.5,5.2,12.5,15.3,12.2,5.1,-5,-19,-28,-6.3]
["Кяхта",-21.9,-18.2,-8.6,2,9.5,16.6,18.9,16.4,9.2,0.6,-10.5,-19.2,-0.4]
["Монды",-19.9,-17.6,-10.1,-1.8,5.6,12.1,14.2,12,5.5,-2.2,-11.8,-18.2,-2.7]
["Нижнеангарск",-22.6,-21.3,-13.4,-3.2,4.3,11.2,15.5,14.6,8.3,-0.6,-11.8,-18.4,-3.1]
["Сосново-Озерское",-24.7,-21.8,-13.2,-2.9,4.7,13.5,16.4,13.6,6.4,-2.6,-14.2,-21.7,-3.9]
["Уакит",-28.3,-24.5,-15.7,-5.2,3.5,11.6,14.8,11.8,4.7,-6,-18.7,-26.5,-6.5]
["Улан-Удэ",-24.8,-21,-10.2,1.1,8.7,16,19.3,16.4,8.7,-0.2,-12.4,-21.4,-1.7]
["Хоринск",-25.6,-22,-10.7,0.4,8.4,16.2,18.8,15.8,8,-1.1,-13.4,-21.9,-2.3]
["Владимирская область"]
["Владимир",-11.1,-10,-4.3,4.9,12.2,16.6,17.9,16.4,10.7,3.7,-2.7,-7.5,3.9]
["Муром",-11.5,-10.9,-4.9,4.7,12.5,16.7,18.7,17.2,11.3,4.1,-2.3,-8.2,4]
["Волгоградская область"]
["Волгоград",-9.1,-7.6,-1.4,10,17,21,23.4,22,16.2,7.5,1.4,-4.2,8]
["Котельниково",-7.4,-6.8,-0.8,9.5,17,21.2,24,22.7,16.2,8.3,1.9,-3.7,8.5]
["Эльтон",-10.2,-10.1,-3,9.1,17.3,22.2,24.6,23.1,16.1,7.4,-0.1,-6.7,7.5]
["Вологодская область"]
["Вологда",-12.6,-11.6,-5.9,2.3,9.6,14.9,16.8,15,9.1,2.5,-3.5,-8.9,2.3]
["Вытегра",-10.9,-10.4,-5.9,1.8,8.4,13.8,16.7,14.7,9.2,3,-2.8,-8,2.5]
["Никольск",-13.8,-12.9,-6.6,2,9,14.5,16.8,14.5,8.5,1.6,-4.6,-10.8,1.5]
["Тотьма",-13.1,-11.9,-6.2,2.1,9.1,14.3,17,14.5,8.5,1.9,-4.5,-10.4,1.8]
["Воронежская область"]
["Воронеж",-9.8,-9.6,-3.7,6.6,14.6,17.9,19.9,18.6,13,5.9,-0.6,-6.2,5.6]
["Республика Дагестан"]
["Дербент",1.5,1.7,4.1,9.4,16.1,21.4,24.7,24.5,20.1,14.4,8.7,4.3,12.5]
["Махачкала",-0.5,0.2,3.5,9.4,16.3,21.5,24.6,24.1,19.4,13.4,7.2,2.6,11.8]
["Ивановская область"]
["Иваново",-11.9,-10.9,-5.1,4.1,11.4,15.8,17.6,15.8,10.1,3.5,-3.1,-8.1,3.3]
["Кинешма",-11.7,-11.3,-5.6,3.4,11.1,15.9,18.2,15.9,10,3.3,-3.5,-9.1,3]
["Иркутская область"]
["Алыгджер",-16.7,-14.6,-7.8,-0.2,6.2,12.2,13.8,12,6.4,0.1,-8.9,-15.1,-1.1]
["Бодайбо",-30.8,-26.8,-15.4,-2.7,6.1,14.2,17.6,14.5,6.9,-3.1,-18.6,-28.9,-5.6]
["Братск",-20.7,-19.4,-10.2,-1.2,6.2,14,17.8,14.8,8.1,-0.5,-9.8,-18.4,-1.6]
["Верхняя Гутара",-19.8,-17.2,-10.6,-2.1,4.8,11.3,13.7,11,4.9,-2.1,-11.5,-18,-3]
["Дубровское",-28.6,-23.2,-13.6,-2.9,5.7,14.3,17.7,14,6.4,-2.3,-17.4,-25.8,-4.6]
["Ербогачен",-31,-28.2,-17.2,-5,4.7,14,17.1,13,5.3,-5.6,-21.9,-30.1,-7.1]
["Жигалово",-28.4,-25.1,-13.8,-1,7.2,14.6,17.4,14.1,6.5,-2.4,-15.7,-25.4,-4.3]
["Зима",-23,-20,-10.1,1.1,8.7,15.8,18,14.9,8.1,-0.1,-12.2,-20.5,-1.6]
["Ика",-29.4,-24.3,-15.4,-3.9,5.3,13.7,16.7,13,5.7,-3.6,-18.2,-28.1,-5.7]
["Илимск",-25.4,-22,-12.6,-1.6,6.3,14.2,17.6,14.2,6.6,-2,-14.8,-23.8,-3.6]
["Иркутск",-20.6,-18.1,-9.4,1,8.5,14.8,17.6,15,8.2,0.5,-10.4,-18.4,-0.9]
["Ичера",-28.2,-25.4,-14.6,-2.7,6.4,14.6,17.6,14,6.6,-3,-17.6,-26.7,-4.9]
["Киренск",-27.4,-23.8,-13.8,-2.2,6.7,15,18.3,14.8,7,-2.4,-15.9,-25.8,-4.1]
["Мама",-28.9,-23.9,-14.3,-2.8,5.9,14.1,17.9,14.4,6.8,-2.1,-17.4,-26.1,-4.7]
["Марково",-27.8,-23.3,-13.7,-1.8,7.1,15.2,18,14.7,7.1,-2,-15.8,-26,-4]
["Наканно",-35.1,-31.3,-18.4,-6.5,3.8,13.3,16.7,12.6,4.8,-6.5,-24.8,-33.7,-8.8]
["Невон",-24.9,-23.2,-13.3,-1.8,6.5,14.6,17.6,14.1,6.9,-1.4,-14.4,-23.4,-3.6]
["Непа",-27.9,-25.4,-14.6,-3.5,5.6,13.9,16.8,12.9,5.7,-4,-18.5,-27.2,-5.5]
["Орлинга",-26.7,-23.3,-13.2,-1.9,6.8,14.3,17.1,13.9,6.6,-2,-15,-24.7,-4]
["Перевоз",-26.5,-25,-15.4,-3.5,5.5,13.4,16.8,13.2,5.7,-3.9,-17.6,-25.6,-5.2]
["Преображенка",-29.2,-24.2,-15.4,-3.9,5.6,14.7,17.7,13.5,5.8,-4.1,-18.6,-28.4,-5.5]
["Слюдянка",-17.4,-17,-9.9,-0.3,6,11.8,15.3,14.2,7.8,-1.7,-7.3,-13.5,-0.7]
["Тайшет",-19.5,-17.2,-9.1,0.7,8.4,15.8,18.3,15,8.3,0.2,-10.6,-18.4,-0.7]
["Тулун",-21.5,-18.3,-10.2,0,7.7,14.4,17.2,14.1,7.3,-0.6,-11.8,-20.1,-1.8]
["Усть-Ордынский — Бурятский АО",-24.8,-22.3,-12.5,0.6,8.2,15.6,18,15.1,7.7,-0.8,-14.2,-21.9,-2.6]
["Кабардино-Балкарская Республика"]
["Нальчик",-4,-2.8,1.8,9.5,15.4,19.1,21.6,21,16,9.4,3.8,-1.3,9.1]
["Калининградская область"]
["Калининград",-3.1,-2.5,0.6,6.2,11.6,15.2,17.3,16.7,13,7.8,2.9,-0.9,7.1]
["Республика Калмыкия — Хальмг Тангч"]
["Элиста",-6.8,-6.2,-0.3,9.5,16.9,21.5,24.4,23.2,16.8,8.9,2.1,-2.9,8.9]
["Калужская область"]
["Калуга",-10.1,-8.9,-3.9,4.8,12.3,16.2,18,16.5,11,4.7,-1.5,-6.5,4.4]
["Камчатская область"]
["Апука — Корякский АО",-10.9,-13.1,-11.9,-6.5,0.7,6.1,9.8,10.4,6.5,-1.7,-8.5,-12.1,-2.6]
["Ича — Корякский АО",-12,-12.6,-9.3,-3.2,2.1,6.3,10.3,11.4,8.7,3.1,-4,-9,-0.7]
["Ключи",-16.1,-14,-9.7,-2.7,4.2,10.8,14.6,13.6,8.7,1.5,-7.5,-14.1,-0.9]
["Козыревск",-17.9,-15.1,-10.2,-2.1,5.1,11.5,14.9,13.6,8.1,0.4,-9.8,-16.7,-1.5]
["Корф — Корякский АО",-13.6,-16.1,-12.7,-6.5,0.5,7.4,12.1,12,7.4,-2,-9.5,-14,-2.9]
["Лопатка, мыс",-5.1,-5.9,-4.4,-1.5,1.1,4.1,7.5,9.4,8.7,5.2,0.3,-3.1,1.3]
["Мильково",-19.9,-17,-11.9,-2.5,5.2,11.6,15,13.6,8,0.3,-10.9,-17.6,-2.1]
["Начики",-18.3,-16.5,-11.8,-4.4,1.9,7.7,12,11.8,7.3,0.5,-9.4,-16.4,-3]
["О.Беринга",-3.5,-3.8,-3,-0.8,2,5.2,8.6,10.5,8.9,4.5,0.1,-2.5,2.2]
["Оссора — Корякский АО",-13.3,-13.9,-12.2,-6.4,0.6,6.9,11.8,12,7.8,0.1,-7.6,-12.5,-2.2]
["Петропавловск-Камчатский",-7.5,-7.5,-4.8,-0.5,3.8,8.3,12.2,13.2,10.1,4.8,-1.7,-5.5,2.1]
["Семлячики",-6.3,-6.2,-4.7,-1,3.2,7.3,11.4,12.8,9.9,4.7,-1.8,-5.2,2]
["Соболево",-14,-14.1,-10,-3.3,2.6,7.4,11.2,11.9,8.5,2.7,-5.6,-10.9,-1.1]
["Кроноки",-8.5,-8.2,-6.2,-1.6,2.6,6.6,10.7,11.7,8.6,2.8,-3.3,-7.4,0.6]
["Ука",-15.8,-16.3,-13.5,-6.2,-0.1,6.3,12.2,12.6,8.1,0.7,-7.1,-13.2,-2.7]
["Октябрьская",-12.1,-12.6,-8.7,-2.5,2.1,6.1,9.8,11.4,9.3,4.1,-3,-9,-0.4]
["Усть-Воямполка — Корякский АО",-16.8,-16.8,-13.3,-5.8,1.3,6.4,10,10.5,7.1,0.5,-7.7,-13.7,-3.2]
["Усть-Камчатск",-11.4,-11.2,-9,-3.6,1.6,6.8,11.2,12.2,9,2.6,-4.7,-9.7,-0.5]
["Усть-Хайрюзово",-14.2,-14.4,-11.3,-4.5,2.2,7.3,11.2,11.7,8,1.6,-5.7,-11.1,-1.6]
["Карачаево-Черкесская Республика"]
["Черкесск",-4.4,-2.3,1.5,9,14.8,18.3,21.1,20.6,15.7,9.6,3.7,-1.1,8.8]
["Республика Карелия"]
["Кемь",-10.6,-10.8,-6.9,-1,4.5,10.5,13.8,13.1,8.4,2.2,-2.8,-7.1,1.1]
["Лоухи",-12.1,-12.4,-8.3,-1.7,4.7,11.6,14.8,12.8,7.2,1,-4.4,-8.5,0.4]
["Олонец",-10.3,-10.5,-6.3,1.3,8.6,13.6,16.4,14.7,9.3,3.4,-1.8,-7.1,2.6]
["Паданы",-11,-11.2,-7.1,-0.1,5.8,12.2,15.5,13.5,8.4,2.4,-3.1,-8,1.4]
["Петрозаводск",-11.1,-10.4,-5.4,1.3,7.6,13.6,15.7,14.1,8.9,2.9,-2.6,-7.2,2.3]
["Реболы",-11.9,-11.8,-7.6,-0.5,6.1,12.9,16,13.7,8,1.6,-3.5,-8.6,1.2]
["Кемеровская область"]
["Кемерово",-18.8,-16.9,-9.8,1,9.7,16.3,18.8,15.4,9.5,1.3,-9.6,-16.9,0]
["Киселевск",-17.2,-15.5,-8.1,2,10,16.6,18.8,15.8,10,2.2,-8.3,-15.4,0.9]
["Кондома",-19.1,-16.3,-8.6,0.9,9.1,15.2,17.4,14.5,8.6,1.4,-9.4,-17,-0.3]
["Мариинск",-17.8,-16.2,-9.3,0.8,9,15.9,18.3,15.2,9.1,1,-9.1,-16.2,0.1]
["Тайга",-18.8,-16.7,-10.4,-0.3,8.2,14.9,17.5,14.4,8.4,0.1,-10.3,-17.4,-0.9]
["Тисуль",-17.4,-15.9,-8.5,0.7,8.8,15.7,17.9,14.8,9,1.2,-9,-15.5,0.2]
["Топки",-18.2,-16.1,-10.2,-0.2,8.9,15.8,18.2,15.4,9.2,0.7,-10.2,-16.5,-0.3]
["Усть-Кабырза",-22.1,-18,-10,-0.4,8.1,14.6,16.9,14.5,8.4,0.4,-10.5,-19,-1.4]
["Кировская область"]
["Вятка",-14.4,-12.9,-6.7,2.2,10,15.4,17.9,15.3,9,1.5,-5.7,-11.8,1.6]
["Нагорск",-14.9,-13.7,-7.1,1.6,9,14.6,16.9,14.8,8.5,0.8,-6,-12.5,1]
["Савали",-14,-13.2,-7.4,2.8,11.6,16.8,18.8,16.8,10.4,2.8,-5.2,-11.5,2.4]
["Республика Коми"]
["Вендинга",-15.8,-15.1,-9.1,-0.4,6.2,12.4,15.5,13,6.8,0,-6.7,-13.2,-0.5]
["Воркута",-20.3,-20.6,-16.5,-9,-2.8,5.8,12.4,9.5,3.8,-5.1,-13.6,-15.7,-6]
["Объячево",-14.9,-13,-6.6,1.7,8.5,14.4,16.6,14.3,8.2,0.7,-5.7,-11.6,1]
["Петрунь",-19.7,-18.8,-15.2,-6.5,-0.2,8.4,13.8,11,5.3,-3,-11.3,-16.6,-4.4]
["Печора",-19.5,-17.7,-11.6,-3.4,3.4,11.1,16,12.3,6.1,-2.5,-10.6,-15.6,-2.7]
["Сыктывкар",-15.6,-14.1,-7.7,1,7.6,14,16.7,14,7.8,0.3,-6.7,-12.9,0.4]
["Троицко-Печорск",-18,-16,-9.4,-0.3,5.7,12.8,15.9,13,7,-1,-9,-15.5,-1.2]
["Усть-Уса",-18.4,-17.6,-12.9,-4.3,1.4,9.5,14.1,11.6,5.7,-2.1,-9.6,-15.6,-3.2]
["Усть-Цильма",-17.3,-15.8,-10.7,-2.6,3.1,10.6,14.5,12,6.2,-1.3,-8.5,-14.2,-2]
["Усть-Щугор",-19.7,-17.7,-12,-2.4,3.7,11.4,15.2,12.3,6.4,-1.8,-10.2,-16.9,-2.6]
["Ухта",-17.3,-15.8,-8.9,-0.5,5.4,12.1,15.7,12.7,6.6,-1.4,-8.5,-13.6,-1.1]
["Костромская область"]
["Кострома",-11.8,-11.1,-5.3,3.2,10.9,15.5,17.8,16.1,10,3.2,-2.9,-8.7,3.1]
["Чухлома",-12.8,-11.6,-5.7,2.5,9.7,14.8,17,15.1,9.2,2.4,-3.6,-9.8,2.3]
["Шарья",-13,-12.1,-6,2.9,10.2,15.1,17.4,15.1,9.3,2.3,-4.7,-10.6,2.2]
["Краснодарский край"]
["Краснодар",-1.6,-0.6,4.3,11.3,17,20.7,23.3,22.7,17.6,11.4,5.6,1.1,11.1]
["Сочи",5.9,6.1,8.2,11.7,16.1,19.9,22.8,23.1,19.9,15.7,11.7,8.2,14.1]
["Тихорецк",-3.5,-2.1,2.8,11.1,16.6,20.8,23.2,22.6,17.3,10.1,4.8,-0.1,10.3]
["Красноярский край"]
["Агата",-34.6,-33.1,-23.1,-11.4,-1.6,7.7,13.7,10.6,3.9,-7.2,-24.9,-31.9,-11]
["Ачинск",-17.7,-15.6,-9.1,0.4,8.6,15.6,17.9,15,9,0.6,-9.3,-16.3,-0.1]
["Байкит — Эвенкийский АО",-30.9,-27,-15.4,-3.9,4.1,12.9,16.8,12.5,5.4,-5,-21.2,-29.8,-6.8]
["Боготол",-17.4,-16,-9.1,0.2,8.1,15.3,17.8,14.6,8.7,0.8,-9.7,-16.4,-0.3]
["Богучаны",-24.4,-22.4,-12.1,-0.5,7.2,15.7,18.8,14.9,8,-0.5,-13.4,-22.8,-2.6]
["Ванавара —",-29.8,-26.5,-15.7,-3.7,5.1,14,17.2,13,5.6,-4.4,-19.9,-28.5,-6.1]
["Эвенкийский АО"]
["Вельмо",-27.6,-24.8,-14.8,-3.7,4.3,13.1,16.8,12.7,6.1,-3.7,-18.1,-26.5,-5.5]
["Верхнеимбатск",-24.7,-22.4,-14.3,-5.1,2.4,11.8,16.8,13.1,6.8,-3.5,-16.9,-24,-5]
["Волочанка",-31.2,-29.7,-25.7,-15.8,-6.1,5.9,13,9.4,2.4,-1.6,-25.2,-27.8,-11.9]
["Диксон — Таймырский АО",-25.6,-25.7,-24.3,-17.2,-8.1,0.2,4.6,5,1.6,-7.3,-17.6,-22.3,-11.4]
["Дудинка — Таймырский АО",-28,-26.9,-22.8,-15,-5.9,5.1,13.2,10.5,3.8,-8.2,-21.1,-25.6,-10.1]
["Енисейск",-22,-19.5,-10.7,-0.9,7.1,15.1,18.5,14.9,8.2,-0.5,-12.3,-20.7,-1.9]
["Ессей — Эвенкийский АО",-36,-34.1,-24.7,-13.8,-3.3,7.4,13.5,10.2,2.6,-11.3,-27.9,-33.1,-12.5]
["Игарка",-28.1,-26.3,-20,-10.8,-2,8.5,15.1,11.5,5.1,-6.5,-20.8,-26.2,-8.4]
["Канск",-20.2,-18.7,-10.3,0.7,8.6,16,18.8,15.6,8.8,0.4,-10.2,-18.6,-0.8]
["Кежма",-27.4,-25.1,-14.1,-2.2,6.3,14.9,18.1,14.2,7.1,-1.9,-15.8,-25.7,-4.3]
["Ключи",-17.7,-15.6,-8,0.8,8.2,15.6,18.1,14.8,8.5,0.7,-10.1,-16.9,-0.1]
["Красноярск",-18.2,-16.8,-7.8,2.6,9.4,16.6,19.1,15.7,9.4,1.5,-8.8,-16.3,0.5]
["Минусинск",-20.8,-19,-8.9,3,10.5,17.2,19.8,16.9,10,1.9,-8.9,-17.8,0.3]
["Таимба",-30.1,-26.6,-15.6,-3.4,5.1,13.4,16.8,12.7,5.3,-4.2,-20.1,-29.1,-6.3]
["Троицкое",-22.8,-20.3,-11.5,-0.8,6.9,14.5,17.5,14,7,-1,-12.5,-21.9,-2.6]
["Тура — Эвенкийский АО",-36.5,-32.4,-19.5,-7,3,12.4,16.3,12.3,5,-6.8,-25.8,-33.5,-9.4]
["Туруханск",-27.2,-23.8,-16.9,-8.6,-0.3,9.5,16,12.5,5.6,-5.7,-19.8,-26,-7.1]
["Хатанга",-33.1,-31.7,-27.8,-18,-7,5.2,12.7,9,1.7,-12,-26.4,-29.6,-13.1]
["Челюскин-2, мыс — Таймырский АО",-28.5,-28.6,-28.2,-21,-10.5,-1.4,1.5,0.7,-2.4,-11.5,-21.4,-25.3,-14.7]
["Ярцево",-23.6,-21.5,-12.9,-2.7,5.1,14.3,18.2,14,7.6,-1.8,-14.7,-22.3,-3.4]
["Курганская область"]
["Курган",-17.7,-16.6,-8.6,4.1,12.6,17.2,19.1,16.3,10.9,2.4,-7.2,-14.3,1.5]
["Курская область"]
["Курск",-9.3,-7.8,-3,6.6,13.9,17.2,18.7,17.6,12.2,5.6,-0.4,-5.2,5.5]
["Липецкая область"]
["Липецк",-10.3,-9.5,-4.4,5.5,13.8,18,20.2,18.5,12.5,5.5,-1.5,-7.1,5.1]
["Ленинградская область"]
["Свирица",-9.8,-9.7,-5.7,1.9,8.9,14.1,16.9,15.2,10,4,-1.6,-6.7,3.1]
["Тихвин",-10.5,-9.3,-4.7,2.8,9.7,14.7,16.6,14.8,9.5,3.6,-1.8,-6.6,3.2]
["Санкт-Петербург",-7.8,-7.8,-3.9,3.1,9.8,15,17.8,16,10.9,4.9,-0.3,-5,4.4]
["Магаданская область"]
["Брохово",-19.6,-19.2,-16.7,-8.7,-0.5,5.8,11.9,12.2,7.8,-1.1,-10.7,-15.8,-4.6]
["Аркагала",-36.8,-32.8,-25.6,-13.1,0.8,10.2,13,9.9,1.6,-15.1,-30.3,-36.5,-12.4]
["Магадан (Нагаева бухта)",-17,-16,-12.6,-5.7,1.3,6.6,11.2,11.5,7.1,-2.4,-11.4,-15,-3.5]
["Омсукчан",-33.4,-31,-24.3,-12.4,0.8,10.1,13.2,10.6,3.1,-11.3,-26.5,-32.5,-11.1]
["Палатка",-22.1,-20.2,-16.3,-7.7,2.3,9.4,12.8,11.6,5.2,-6.7,-16.7,-20.3,-5.7]
["Среднекан",-36.6,-33.4,-25.8,-12,2.8,13,15.1,11.9,4,-11.3,-28.6,-35.8,-11.4]
["Сусуман",-38.2,-34.5,-27.2,-13.3,1.6,10.8,13.3,10.2,2.1,-14.9,-31.2,-37.5,-13.2]
["Республика Марий Эл"]
["Йошкар-Ола",-14,-12.9,-6.4,3.6,11.6,16.2,18,16.2,10.2,2.7,-4.3,-9.8,2.6]
["Республика Мордовия"]
["Саранск",-12.3,-11.7,-5.9,4.8,13.1,17.3,19.2,17.7,11.6,4.1,-3,-8.7,3.9]
["Московская область"]
["Дмитров",-10.4,-9.5,-4.4,4.3,11.5,15.7,17.5,15.7,10.3,4,-2.4,-7.2,3.8]
["Кашира",-10.9,-9.8,-4.6,4.6,12.2,16.3,17.8,16.5,11,4.1,-2.3,-7,4]
["Москва",-10.2,-9.2,-4.3,4.4,11.9,16,18.1,16.3,10.7,4.3,-1.9,-7.3,4.1]
["Мурманская область"]
["Вайда-Губа",-5.6,-6.4,-4.8,-1.7,2.5,7,10.2,10.1,6.8,2,-1.5,-3.8,1.2]
["Кандалакша",-11.8,-12.1,-7.8,-1.6,4.1,10.6,14.8,12.7,7.1,1.1,-4.2,-8.5,0.4]
["Ковдор",-13.5,-14.1,-9.2,-3.1,3.8,10.6,13.4,11,5.2,-1.2,-7.1,-11.3,-1.3]
["Краснощелье",-13.2,-13.8,-10.5,-3.9,2.4,9.7,13.2,11.1,5.8,-0.6,-5.6,-9.8,-1.3]
["Ловозеро",-13.2,-13.8,-10.2,-3.8,2.4,9.1,13,11.1,5.6,-0.9,-6.2,-10.4,-1.4]
["Мончегорск",-12.8,-12.7,-8.6,-2.5,3.4,10.2,13.8,12,6.6,0.2,-5.4,-9.7,-0.5]
["Мурманск",-10.5,-10.8,-6.9,-1.6,3.4,9.3,12.6,11.3,6.6,0.7,-4.2,-7.8,0.2]
["Ниванкюль",-13.1,-13,-8.1,-1.7,4.2,10.5,13.5,11.6,6.3,-0.1,-6.1,-10.2,-0.5]
["Пулозеро",-13.4,-13.6,-9.4,-3,3.1,9.6,13.4,11.4,6,-0.3,-5.8,-10.1,-1]
["Пялица",-10,-11.2,-8.9,-3.7,1.4,6.8,10.1,9.8,6.4,1.3,-2.8,-6.4,-0.6]
["Териберка",-7.8,-8.5,-6.3,-2.1,2.4,7.5,11.2,10.8,6.9,1.5,-2.8,-5.8,0.6]
["Терско-Орловский",-9.9,-11.1,-8.8,-3.6,0.7,5.4,9,9.3,6.4,0.9,-3.3,-6.2,-0.9]
["Умба",-11,-11.9,-8,-1.9,3.9,10.5,14.3,12.6,7.4,1.3,-3.6,-7.8,0.5]
["Юкспор",-12.2,-12.6,-10.9,-6.9,-1.9,4.9,9,7.2,1.5,-4.1,-7.7,-10.4,-3.7]
["Нижегородская область"]
["Арзамас",-12.4,-11.9,-6.5,3.5,12,16.9,18.8,17.2,10.8,3.5,-3.6,-9.4,3.2]
["Выкса",-11.3,-10.8,-5.1,4.4,12.5,16.8,18.9,17,11.1,4,-2.8,-8.5,3.8]
["Нижний Новгород",-11.8,-11.1,-5,4.2,12,16.4,18.4,16.9,11,3.6,-2.8,-8.9,3.6]
["Новгородская область"]
["Новгород",-8.7,-8.7,-4.3,3.3,10.4,15.2,17.3,15.4,10.3,4.2,-0.9,-5.9,4]
["Новосибирская область"]
["Барабинск",-19.9,-18.3,-11.8,0.5,10.1,16.4,18.5,15.5,9.8,1.1,-9.2,-17,-0.4]
["Болотное",-18.5,-16.8,-9.4,1.1,9.6,16.4,18.9,15.5,9.6,1.1,-9.7,-16.9,0.1]
["Карасук",-19.4,-18.4,-10.6,2.9,12.1,18.2,20.2,16.9,11.2,2.2,-8.5,-16.2,0.9]
["Кочки",-19.6,-18.2,-11.5,1.2,10.7,16.7,18.6,15.4,9.7,1.4,-9.5,-16.9,-0.2]
["Купино",-19.6,-18.6,-11.7,1.3,11.2,17.4,19.5,16.3,10.5,1.9,-8.6,-16.7,0.2]
["Кыштовка",-20.3,-18.3,-10.7,1.3,9.8,15.7,18,14.6,9.3,0.8,-9.8,-17.4,-0.6]
["Новосибирск",-18.8,-17.3,-10.1,1.5,10.3,16.7,19,15.8,10.1,1.9,-9.2,-16.5,0.2]
["Татарск",-19.6,-18,-11.1,1.2,10.7,16,18.7,15.6,10.1,1.4,-8.8,-16.4,0]
["Чулым",-19.5,-17.9,-11.3,0.3,10.1,16.4,18.5,15.5,9.7,1.3,-9.3,-17,-0.2]
["Омская область"]
["Омск",-19,-17.6,-10.1,2.8,11.4,17.1,18.9,15.8,10.6,1.9,-8.5,-16,0.6]
["Тара",-19.9,-18,-11.4,-0.1,9.1,15.5,17.7,14.8,9.2,0.8,-9.8,-17.2,-0.8]
["Черлак ",-19.2,-17.9,-10.3,3.2,12.1,18,19.8,16.5,11.3,2.2,-8.4,-15.8,1]
["Оренбургская область"]
["Оренбург",-14.8,-14.2,-7.3,5.2,15,19.7,21.9,20,13.4,4.5,-4,-11.2,4]
["Орловская область"]
["Орел",-9.7,-8.8,-4,5.6,13,16.9,18.5,17.1,11.7,5.1,-0.9,-5.6,4.9]
["Пензенская область"]
["Земетчино",-11.6,-11.1,-5.6,4.8,13.4,17.5,19.4,17.7,11.7,4.4,-2.4,-8.2,4.2]
["Пенза",-12.2,-11.3,-5.6,4.9,13.5,17.6,19.6,18,11.9,4.4,-2.9,-9.1,4.2]
["Пермская область"]
["Бисер",-17.5,-15.4,-8.9,0.5,6.9,12.7,15.2,12.7,6.9,-1.3,-9.2,-15.4,-1.1]
["Пермь",-15.3,-13.4,-6.9,2.6,10.2,15.7,18,15.4,9.3,1.4,-6.3,-12.7,1.5]
["Приморский край"]
["Анучино",-20.3,-16,-5.9,5,12.1,17,21.1,20.6,13.7,5.7,-5.7,-16.7,2.6]
["Астраханка",-17.7,-13.6,-4.8,4.4,11.6,16.5,20.6,20.9,14.9,6.7,-4.3,-13.9,3.4]
["Богополь",-13.3,-10.1,-3.1,4.2,9.5,13.2,17.7,19.2,14.1,6.9,-2.6,-10.8,3.7]
["Владивосток",-13.1,-9.8,-2.4,4.8,9.9,13.8,18.5,21,16.8,9.7,-0.3,-9.2,5]
["Дальнереченск",-20.5,-16.7,-6.7,4.5,12.1,17.4,21.1,20.2,13.7,5.4,-6.5,-17.2,2.2]
["Мельничное",-22.9,-18.3,-8.7,2.1,9.4,15,19.2,18.2,11.3,2.6,-9.2,-19.9,-0.1]
["Партизанок",-13.4,-10.3,-3.1,5.1,11.3,15.1,19.4,20.1,14.6,7.5,-2.2,-10.7,4.5]
["Посьет",-10.6,-8,-1.6,5.3,10.5,14.3,18.8,20.9,16.6,9.6,0.3,-7.8,5.7]
["Преображение",-8.7,-6.7,-1.4,4.2,8.4,11.8,16.6,19.2,15.6,9.2,1.1,-6.3,5.3]
["Рудная Пристань",-11.9,-9,-2.8,3.3,7.5,11.1,15.9,18.3,14.3,7.3,-1.8,-9.6,3.6]
["Чугуевка",-21.3,-17.3,-6.7,4.3,11.5,16.3,20.4,19.5,12.5,4.4,-7.2,-17.9,1.5]
["Псковская область"]
["Великие Луки",-8.6,-7.7,-3.2,4.9,11.5,15.7,17.1,15.8,10.7,5.1,-0.1,-5.2,4.7]
["Псков",-7.5,-7.5,-3.4,4.2,11.3,15.5,17.4,15.7,10.9,5.3,0,-4.5,4.8]
["Ростовская область"]
["Миллерово ",-8.1,-7.4,-2,8.4,15.8,19.6,22,21,14.9,7.2,0.9,-4.6,7.3]
["Ростов-на-Дону",-5.7,-4.8,0.6,9.4,16.2,20.2,23,22.1,16.3,9.2,2.5,-2.6,8.9]
["Таганрог",-5.2,-4.5,0.5,9.4,16.8,21,23.7,22.6,17.1,9.8,3,-2.1,9.3]
["Рязанская область"]
["Рязань",-11,-10,-4.7,5.2,12.9,17.3,18.5,17.2,11.6,4.4,-2.2,-7,4.3]
["Самарская область"]
["Самара",-13.5,-12.6,-5.8,5.8,14.3,18.6,20.4,19,12.8,4.2,-3.4,-9.6,4.2]
["Саратовская область"]
["Саратов",-11,-11.4,-4.8,6.6,15,19.4,21.4,19.9,14,5.4,-2,-8.3,5.3]
["Сахалинская область"]
["Александровск Сахалинский",-18,-15.4,-8.9,-0.2,5.5,10.8,15.3,16.4,12.2,4.6,-4.9,-13.3,0.3]
["Долинск",-13.5,-12.4,-6.5,0.9,6.2,10.9,15.3,16.9,13.1,6.4,-1.9,-8.6,2.2]
["Кировское",-23.6,-19.7,-12,-1.7,5.6,11.7,15.6,15.5,10.4,2.1,-9.1,-19.3,-2]
["Корсаков",-10.7,-10.1,-5.3,1.2,5.6,10,14.5,16.9,13.7,7.4,-0.4,-6.8,3]
["Курильск",-5.2,-6.7,-4,1.5,5.9,9.2,13.5,15.3,13.1,8.8,3.2,-1.5,4.4]
["Макаров",-14.3,-12.3,-6.7,0.9,5.3,9.5,13.8,15.7,12.8,6,-3,-10.2,1.6]
["Невельск",-8.6,-8,-3.7,2.4,7,11.2,15.7,17.7,14.5,8.2,0.6,-5.2,4.3]
["Ноглики",-19.7,-17,-10.9,-2.4,3,8.5,13.2,14.2,10.5,2.9,-7.6,-16.3,-1.8]
["Оха",-19.7,-17.7,-12.5,-4,1.5,7.7,12.7,13.9,10.2,2.7,-6.3,-15.1,-2.2]
["Погиби",-20.7,-18.7,-12.6,-3.6,1.9,9,13.8,15.4,11.7,3.6,-7.3,-16.7,-2]
["Поронайск",-17.3,-14.4,-8,-0.3,4.4,8.9,13.6,15.7,12.2,5.1,-4.8,-13.5,0.1]
["Рыбновск",-22.3,-20.1,-14.3,-4.6,1.8,9.4,14.4,15.1,11.1,3.4,-6.9,-17.4,-2.5]
["Холмск",-9.7,-8.7,-4.2,2.3,6.9,11.4,15.7,17.7,14.2,7.8,0,-6.1,3.9]
["Южно-Курильск",-5,-6,-3.2,1.6,5.4,8.3,12.6,15.8,14.7,10.3,4,-1.3,4.8]
["Южно-Сахалинск",-13.7,-12.8,-6.6,1.3,6.7,11.2,15.6,16.9,12.9,6,-2.3,-9.1,2.2]
["Свердловская область"]
["Верхотурье",-17.3,-15.1,-7.7,2.3,8.9,14.7,17,14.4,8.7,0.7,-7.9,-15.1,0.3]
["Екатеринбург",-15.5,-13.6,-6.9,2.7,10,15.1,17.2,14.9,9.2,1.2,-6.8,-13.1,1.2]
["Ивдель",-19.1,-16.7,-8.4,1.4,7.6,13.9,16.6,13.9,7.8,-0.6,-8.8,-16.3,-0.7]
["Республика Северная Осетия"]
["Владикавказ",-4.4,-3,1.4,9,14.2,17.6,19.9,19.3,14.8,8.7,3.1,-1.6,8.1]
["Смоленская область"]
["Вязьма",-9.8,-9,-4.3,4.3,11.3,15.4,16.6,15.4,10.2,4.1,-1.9,-6.4,3.8]
["Смоленск",-9.4,-8.4,-4,4.4,11.6,15.7,17.1,15.9,10.4,4.5,-1,-5.8,4.3]
["Ставропольский край"]
["Арзгир",-4.9,-3.6,1.6,10.3,17.4,22,25,23.7,17.8,10.1,4,-1.3,10.2]
["Ставрополь",-3.2,-2.3,1.3,9.3,15.3,19.3,21.9,21.2,16.1,9.6,4.1,-0.5,9.1]
["Тамбовская область"]
["Тамбов",-10.9,-10.3,-4.6,6,14.1,18.1,19.8,18.6,12.5,5.2,-1.4,-7.3,5]
["Республика Татарстан"]
["Бугульма",-14.3,-13.7,-8,2.4,11.4,16.3,18.1,16.4,10.2,2.1,-5.8,-11.6,2]
["Елабуга",-13.9,-13.2,-6.6,3.8,12.4,17.4,19.5,17.5,11.2,3.2,-4.4,-11.1,3]
["Казань",-13.5,-13.1,-6.5,3.7,12.4,17,19.1,17.5,11.2,3.4,-3.8,-10.4,3.1]
["Тверская область"]
["Бежецк",-10.7,-10.2,-5.2,3.2,10.8,15.2,17.1,15.4,9.8,3.6,-2.3,-7.7,3.2]
["Тверь",-10.5,-9.4,-4.6,4.1,11.2,15.7,17.3,15.8,10.2,4,-1.8,-6.6,3.8]
["Ржев",-10,-8.9,-4.2,4.1,11.2,15.6,17.1,15.8,10.3,4.1,-1.4,-6.3,4]
["Томская область"]
["Александровское",-21.5,-19.6,-12.1,-1.7,5.5,13.7,17.5,13.7,8,-1.4,-12.7,-19.6,-2.5]
["Колпашево",-20.7,-18.7,-10.8,-0.7,7.3,15.2,18,14.4,8.7,0.1,-11.4,-19.4,-1.5]
["Средний Васюган",-20.4,-18.2,-10.2,-0.4,7.2,14.7,17.7,14,8.6,-0.3,-11.3,-18.9,-1.5]
["Томск",-19.1,-16.9,-9.9,0,8.7,15.4,18.3,15.1,9.3,0.8,-10.1,-17.3,-0.5]
["Усть-Озерное",-21.5,-19.3,-11,-0.9,6.7,15,18.1,14.1,7.9,-0.9,-12.9,-20.1,-2.1]
["Республика Тыва"]
["Кызыл",-32.1,-28,-15.2,2.2,11.4,17.9,19.8,17,10,0,-15.6,-28.4,-3.4]
["Тульская область"]
["Тула",-19.9,-9.5,-4.1,5,12.9,16.7,18.6,17.2,11.6,5,-1.1,-6.7,4.7]
["Тюменская область"]
["Березово — Ханты-Мансийский АО",-22.3,-19.8,-13.4,-4.3,2.9,11.2,15.9,13,6.8,-2.8,-13.3,-19.7,-3.8]
["Демьянское — Ханты-Мансийский АО",-19.2,-16.9,-9.4,0.7,7.7,14.7,17.6,14.5,8.9,0.2,-9.8,-17,-0.7]
["Кондинское",-19.8,-18.4,-10.1,0.1,8.4,14.9,18.7,14.7,8.9,-0.6,-10.2,-16.3,-0.8]
["Леуши",-18.1,-16.2,-8.5,1.6,8.4,14.9,17.8,14.9,8.9,0.3,-8.8,-15.9,-0.1]
["Марресаля",-21.8,-21.4,-20.3,-13,-5.5,1.2,6.6,6.7,3.2,-4,-13.1,-18.4,-8.3]
["Надым",-24.5,-24,-16.8,-8.8,-1,8.8,15.5,11.4,5.6,-5.4,-16.1,-21.9,-6.4]
["Октябрьское",-22.8,-20.1,-10.2,-2.2,4.7,12,16.9,12.6,7.2,-2.9,-11.7,-18.1,-2.9]
["Салехард",-24.5,-23.4,-18.6,-10.2,-1.9,7.3,13.3,10.9,4.9,-4.6,-15.6,-21.5,-7]
["Сосьва",-22.7,-20.4,-12,-1.8,5.2,12.3,16.1,12.8,6.6,-2.5,-12.8,-20.2,-3.3]
["Сургут — Ханты-Мансийский АО",-22,-19.6,-13.3,-3.5,4.1,13,16.9,14,7.8,-1.4,-13.2,-20.3,-3.4]
["Тарко-Сале — Ямало-Ненецкий АО",-25.1,-24.4,-18,-8.1,-0.7,9.8,15.8,12,6,-5,-16.8,-23.1,-6.5]
["Тобольск",-19.7,-17.5,-9.1,1.6,9.6,15.2,18.3,14.6,9.3,0,-8.4,-15.6,"-0.1"]
["Тюмень",-17.4,-16.1,-7.7,3.2,11,15.7,18.2,14.8,9.7,1,-7.9,-13.7,0.9]
["Угут",-21,-19.4,-10.9,-1.1,6,13.4,17.4,13.6,7.9,-1.4,-12.6,-18.8,-2.2]
["Уренгой — Ямало-Ненецкий АО",-26.4,-26.4,-19.2,-10.3,-2.6,8.4,15.4,11.3,5.2,-6.3,-18.2,-24,-7.8]
["Ханты-Мансийск — Ханты-Мансийский АО",-21.7,-19.4,-9.8,-1.3,6.4,13.1,17.8,13.3,8,-1.9,-10.7,-17.1,-1.9]
["Удмуртская Республика "]
["Глазов",-14.9,-14,-8,2,9.9,15.8,17.8,15.4,9.1,1.8,-6.2,-12.6,1.3]
["Ижевск",-14.6,-13.3,-6.7,3.3,11.3,16.4,18.5,16.4,10.1,2.1,-5.1,-11.6,2.3]
["Сарапул",-14.3,-13.5,-7.3,3,11.5,17.1,18.9,16.8,10.4,2.7,-5.5,-12.2,2.3]
["Ульяновская область"]
["Сурское",-13.2,-12.5,-6.1,4.8,13,17.1,18.7,17.2,11.3,3.6,-3.1,-8.9,3.5]
["Ульяновск",-13.8,-13.2,-6.8,4.1,12.6,17.6,19.6,17.6,11.4,3.8,-4.1,-10.4,3.2]
["Хабаровский край"]
["Аян",-19.7,-17.6,-11.6,-3.8,0.8,5.6,11.4,13.2,9.6,0.4,-11,-17.4,-3.3]
["Байдуков",-21.7,-20.2,-14.5,-5.2,0.9,9.1,14.5,15.5,12,3.4,-7.1,-16.6,-2.5]
["Бикин",-22.4,-17.4,-8.1,4.1,11.7,17.4,21,19.9,13.3,4.5,-7.6,-18.3,1.5]
["Бира",-22,-16.6,-8.2,2.7,10.2,16.5,20.1,18.5,12,2.6,-10.1,-19.5,0.5]
["Биробиджан",-22.6,-17.5,-9,3,10.7,16.7,20.3,19,12.4,3,-9.8,-19.6,0.6]
["Вяземский",-22.3,-17.8,-9,3.4,11.3,17.1,20.6,19.6,13,3.9,-8.2,-18.1,1.1]
["Гвасюги",-24.9,-20.1,-10.6,1.3,9.1,15.6,19.6,18.4,11.4,1.5,-10.8,-20.8,-0.9]
["Гроссевичи",-14.8,-11.9,-6,0.4,4.3,8.4,13,15.9,13.1,5.9,-4,-11.8,1]
["Де-Кастри",-19.4,-15.8,-9.3,-1.5,3.2,8.5,13.2,15.3,12,3.2,-8.1,-16.2,-1.2]
["Джаорэ",-20.2,-17.2,-11.4,-2.9,1.9,9.7,15.1,16.2,12,3.2,-7.7,-16.5,-1.5]
["Екатерино-Никольское",-21.2,-16.3,-7.7,3.5,11,17.1,21,19.6,13.1,3.9,-8.3,-18.3,1.4]
["Комсомольск-на-Амуре",-25.6,-20.3,-10.1,1.3,8.7,15.6,19.9,18.7,12.6,3,-10.7,-22,-0.7]
["Нижнетамбовское",-26.4,-21.1,-11,0.3,8.2,15.1,19.3,18.2,12.1,2.6,-10.8,-21.8,-1.3]
["Николаевск-на-Амуре",-23.9,-20,-12.7,-2.9,3.7,11.5,16.5,16.2,11.1,2,-9.9,-19.8,-2.4]
["Облучье",-26.5,-21.1,-11.4,1.4,9.6,16.2,19.8,17.9,11,1.1,-12.6,-23.6,-1.5]
["Охотск",-23,-20,-14.3,-5.8,1.1,6.2,11.8,13,8.4,-2.3,-14.1,-20.5,-5]
["Им. Полины Осипенко",-29.3,-22.8,-12.7,-0.8,6.9,13.3,17.8,16.6,10.7,0.7,-13.8,-25.6,-3.2]
["Сизиман",-18.2,-15.3,-9.3,-1.2,2.9,7.5,12.6,14.7,11.4,3.2,-7.5,-14.9,-1.2]
["Советская Гавань",-18,-14.7,-8,0.2,5.1,9.9,14.3,16.4,12.6,4.8,-5.4,-13.8,0.3]
["Софийский прииск",-33.3,-26.4,-17.1,-5.2,3.8,11,15.1,12.8,6.2,-5.1,-20.6,-30.7,-7.5]
["Средний Ургал",-31.1,-23,-12.1,0.2,8.1,14.8,18.8,16.5,9.5,-0.8,-16.6,-28.6,-3.7]
["Троицкое",-23.3,-18.2,-9.4,2.1,10.3,16.7,20.5,19.2,13.1,3.9,-8.7,-19.2,0.6]
["Хабаровск",-22.3,-17.2,-8.5,3.1,11.1,17.4,21.1,20,13.9,4.7,-8.1,-18.5,1.4]
["Чумикан",-23.7,-18.9,-11.6,-2.7,1.9,6.6,12,13.5,10,0.7,-12.9,-21.3,-3.9]
["Энкэн",-20.2,-17.3,-11.3,-4,1.4,6.1,11.5,13.3,8.9,-0.5,-11.4,-17.5,-3.4]
["Республика Хакассия"]
["Абакан",-25.5,-18.5,-8.5,2.9,10.5,17.3,19.5,16.4,9.9,1.6,-9.5,-17.9,0.3]
["Шира",-18.5,-17.2,-8.9,1.3,8.9,15.6,17.7,14.9,8.8,1.2,-9.1,-16.4,-0.1]
["Челябинская область"]
["Челябинск",-15.8,-14.3,-7.4,3.9,11.9,16.8,18.4,16.2,10.7,2.4,-6.2,-12.9,2]
["Чеченская Республика"]
["Грозный",-3.8,-2,2.8,10.3,16.9,21.2,23.9,23.2,17.8,10.4,4.5,-0.7,10.4]
["Читинская область"]
["Агинское",-23.3,-20.4,-11.5,0.4,8.8,15.6,18.4,15.5,8.4,-0.6,-13,-21.3,-1.9]
["Акша",-22.6,-19.1,-9.4,1,9,15.4,18.1,15.5,8.4,-0.1,-12.1,-20.3,-1.4]
["Александровский Завод",-26.8,-23.5,-13.9,-1.4,7.4,14.1,16.7,14.1,7,-2.4,-15.5,-24.6,-4.1]
["Борзя",-26.9,-23.5,-12.1,0.4,9.2,16.3,18.7,16.3,8.9,-0.8,-13.9,-23.8,-2.6]
["Дарасун",-22,-19.6,-10.4,-0.4,8,14.4,16.9,14.2,7,-1.4,-12.6,-19.9,-2.2]
["Калакан",-35.5,-28.7,-17.1,-3.7,6,13.6,16.6,13.3,5.8,-6,-22.6,-33.6,-7.7]
["Красный Чикой",-26.2,-22.4,-11.4,0.6,8.3,14.7,17.1,14.3,7.4,-1.2,-13.1,-22.8,-2.9]
["Могоча",-29.6,-24.5,-14.5,-2.4,6.6,13.8,16.8,13.7,6.7,-3.8,-18.9,-28.5,-5.4]
["Нерчинск",-30.8,-26.3,-13.6,0.8,9.8,17,19.7,16.6,9,-1,-16.7,-28.2,-3.6]
["Нерчинский Завод",-28.6,-23.5,-12.9,0,8.9,15.5,18.8,15.9,8.9,-0.9,-15.2,-25.8,-3.2]
["Средний Калар",-36.3,-30.7,-19.1,-5.7,4.5,12.1,15.1,12.1,4.5,-7.5,-23.7,-34.4,-9.1]
["Тунгокочен",-31,-26.5,-16,-3,6,13.1,15.8,12.8,5.5,-4.5,-19.2,-29.3,-6.4]
["Тупик",-32.7,-27.8,-16.8,-3.6,6,13.4,16.3,13.1,5.9,-5.1,-20.5,-30.8,-6.9]
["Чара",-33.8,-29.7,-18.3,-4.9,4.4,12.7,16.2,13,5.2,-6.4,-22,-31.9,-8]
["Чита",-26.2,-22.2,-11.1,-0.4,8.4,15.7,17.8,15.2,7.7,-1.8,-14.3,-23.5,-2.9]
["Чувашская Республика — Чаваш республики"]
["Порецкое",-12.4,-11.7,-5.8,4.4,12.9,17.2,19,17.2,11.2,3.6,-3.3,-9.4,3.6]
["Чебоксары",-13,-12.4,-6,3.6,12,16.5,18.6,16.9,10.8,3.3,-3.7,-10,3]
["Чукотский АО (Магаданская область)"]
["Анадырь",-19.7,-22.3,-20.6,-12.9,-3,5.4,10.6,9.5,3.9,-5.9,-14.6,-21,-7.6]
["Марково",-25.8,-25.4,-23,-14.3,-1.5,10.5,13.7,10.5,3.5,-8.9,-19.5,-25.6,-8.8]
["Островное",-33.6,-33.1,-26.4,-14.1,0.5,11.7,13.1,9.2,1.8,-12.1,-26.4,-32.2,-11.8]
["Усть-Олой",-35.6,-34.1,-26.5,-13.7,1.7,11.8,12.8,9.3,2.3,-11.7,-27.3,-34.8,-12.2]
["Эньмувеем",-23.9,-26.5,-24.1,-16,-2,9.8,12.5,9.2,2.2,-10.3,-20.5,-26.2,-9.6]
["Республика Саха (Якутия)"]
["Алдан",-27.5,-25.2,-16.4,-5.6,3.9,13,16.7,13.4,5.2,-6.3,-19.7,-26.5,-6.3]
["Аллах-Юнь",-44.1,-39.2,-26.6,-11.4,2.3,10.9,14.7,11.4,3.5,-12.2,-32.2,-42.7,-13.8]
["Амга",-42.9,-38,-24,-7.5,6.1,14.5,17.7,14.1,5.3,-8.9,-29.6,-40.6,-11.2]
["Батамай",-41.8,-37.4,-23.8,-8.8,4.2,13.7,17.1,13.6,5,-9.6,-30.6,-40.1,-11.5]
["Бердигястях",-40.5,-35.7,-22.9,-8.3,4.7,13.5,16.3,12.6,3.9,-8.7,-28.2,-38.9,-11]
["Буяга",-37.6,-33.6,-21.6,-6.9,5.1,13.2,16.5,13,4.7,-7.5,-26,-36.4,-9.8]
["Верхоянск",-48.2,-43.6,-30.2,-13.3,2.1,12.8,15.2,10.9,2.5,-14.5,-36.4,-45.1,-15.6]
["Вилюйск",-37.8,-32.1,-20.2,-7.5,4.3,14.4,17.9,14.1,5.5,-7.7,-26.3,-35.9,-9.3]
["Витим",-29.2,-26.9,-16.1,-3.9,5.7,14.3,17.8,14.2,6.4,-3.4,-18.6,-27.6,-5.6]
["Воронцово",-37.9,-36.2,-28.8,-16.8,-2.6,9.3,11.9,8.7,1.5,-13.2,-29.7,-35.9,-14.2]
["Джалинда",-39.4,-35.9,-27.2,-14.8,-3,8.8,13.7,9.3,1.6,-12.7,-31,-35.4,-13.9]
["Джарджан",-38.6,-34.7,-23.7,-12.4,-0.8,10.7,14.7,11.1,3.1,-11,-29.6,-36.1,-12.3]
["Джикимда",-34.7,-31.4,-19.1,-4.4,6.1,13.9,17.5,13.7,5.6,-5.4,-22.9,-33.1,-7.9]
["Дружина",-39.4,-37,-28,-14.5,0.4,11.5,13.7,10.5,2.9,-12.4,-29.6,-37,-13.2]
["Екючю",-45.9,-41.8,-29.2,-13.1,2.2,12.5,14.6,10.5,2.1,-13.9,-35.5,-43.2,-15.1]
["Жиганск",-39.3,-35.2,-23.6,-10.9,1.1,12,15.9,12,3.5,-10.1,-29.5,-37.1,-11.8]
["Зырянка",-36.8,-33.9,-25.9,-12.4,2.7,13.1,15.1,11.8,3.8,-11.1,-28.1,-35.4,-11.4]
["Исить",-35.8,-31.9,-20.6,-5.9,5.8,14.3,17.9,14.6,6.5,-5.3,-23.8,-33.5,-8.1]
["Иэма",-45.5,-42.3,-31.8,-16.6,-1,8.9,12.7,10.3,2,-14.8,-35.4,-42.7,-16.4]
["Крест-Хальджай",-45.1,-39,-23.3,-7.1,6.2,14.9,18.2,14.7,5.8,-9,-30.9,-42.5,-11.4]
["Кюсюр",-38,-34.9,-26.3,-15.7,-3.5,7.9,12.4,9.4,2,-11.2,-29,-35,-13.5]
["Ленск",-29.8,-27.6,-16.5,-4.2,5.5,14.2,17.6,13.8,5.9,-4.5,-20.4,-28.9,-6.2]
["Нагорный",-29.6,-26.4,-18,-7,3.2,11.5,14.9,11.8,4.3,-7.7,-22.1,-29,-7.8]
["Нера",-46.3,-41.6,-29.1,-11.3,3.8,13.2,15.7,12.1,3.4,-14.7,-35.9,-44.4,-14.6]
["Нюрба",-36,-31.9,-20.6,-7.2,5,14.2,17.3,13.5,5.2,-7.3,-26,-34.2,-9]
["Нюя",-30,-26.8,-15.9,-3.5,6.3,14.9,18.1,14.5,6.8,-3.5,-20.1,-28.6,-5.7]
["Оймякон",-47.5,-43.3,-32.8,-15.2,1.2,11.1,13.6,10.3,1.6,-16.3,-37.3,-45.6,-16.7]
["Олекминск",-32.2,-28.8,-16.8,-4.2,6.2,14.6,18,14.5,5.9,-5,-21.6,-30.8,-6.7]
["Оленек",-41.3,37.4,-26.5,-13.1,-1.1,10.2,14.6,10,2.4,-12.1,-31.8,-36.9,-13.6]
["Охотский Перевоз",-44.2,-39.4,-24.7,-7.8,5.7,14.2,17.4,14,5.5,-8.7,-30.3,-41.1,-11.6]
["Сангар",-39.1,-34.5,-21.6,-8.5,4.1,14.3,18.1,14.5,6,-8.7,-28.5,-37.3,-10.1]
["Саскылах",-35.1,-33.3,-28.8,-18.7,-7.3,5.5,11.9,8.3,1.1,-12.6,-27.7,-31.4,-14]
["Среднеколымск",-37.3,-34.7,-26.9,-14.6,-0.3,11.1,13.5,9.9,2.8,-11.3,-27.5,-35.1,-12.5]
["Сунтар",-33.7,-30.1,-19.3,-6,5.6,14.6,17.7,13.9,5.6,-6.1,-24.1,-32.2,-7.8]
["Сухана",-42.5,-38.3,-26.5,-13,-0.5,11.1,14.7,10.3,2.4,-11.6,-32.2,-38.8,-13.7]
["Сюльдюкар",-37.6,-33.8,-21.2,-8.5,3.6,13.2,16.4,12.6,4.5,-7.4,-26.9,-35.1,-10]
["Сюрен-Кюель",-34.6,-32.4,-23.6,-12.7,-0.2,9.3,12.7,9.9,1.7,-12.1,-27.4,-33.1,-11.9]
["Токо",-39.8,-34.5,-22.9,-8.9,3.1,10.8,14.4,11.5,3.6,-9.3,-27,-37.8,-11.4]
["Томмот",-35.5,-31.6,-20,-5.8,5.4,13.7,17.2,13.5,5.5,-6.7,-24.4,-33.9,-8.6]
["Томпо",-44.3,-39.2,-27.3,-11.8,3.2,12.3,15.3,11.7,3.1,-13.3,-34.3,-42.2,-13.9]
["Туой-Хая",-33.2,-29.3,-18.8,-6.4,4.3,13.3,16.5,13,5.4,-6.3,-23.6,-31.2,-8]
["Тяня",-33.1,-29.9,-18.2,-4.5,5.7,13.6,17,13.2,5.1,-5.9,-22.6,-32.2,-7.7]
["Усть-Мая",-42.2,-36,-21.5,-6,6,14.4,18,14.5,6.3,-7.1,-27.2,-39.5,-10]
["Усть-Миль",-39.6,-34.2,-21,-5.2,6.1,13.9,17.2,13.9,5.5,-7.3,-27,-37.7,-9.6]
["Усть-Мома",-44.9,-41,-29,-13.2,3.1,12.9,14.8,11.1,2.5,-15,-34.9,-43,-14.7]
["Чульман",-36.7,-31.9,-20,-7,4,12.3,15.8,12.6,4.5,-7.6,-24.7,-34.9,-9.5]
["Чурапча",-44,-38.4,-24,-7.8,5.8,14.7,18.1,14.3,5.2,-9.4,-30.8,-41.8,-11.5]
["Шелагонцы",-41.9,-37.6,-25.6,-12.5,0.5,11.4,14.5,10.2,2.4,-10.8,-31,-38.9,-13.3]
["Эйик",-37.7,-34.2,-23.8,-11.8,0,10.9,15.1,10.9,2.8,-10.5,-28.4,-35.5,-11.9]
["Якутск",-42.6,-35.9,-22.2,-7.2,5.8,15.4,18.7,14.9,6.2,-8,-28.3,-39.5,-10.2]
["Ненецкий АО (Архангельская область)"]
["Варандей",-17.8,-19.2,-16.6,-9.5,-3.4,2.8,8.9,8.8,4.9,-2.2,-9.5,-13.9,-5.6]
["Индига",-13.9,-14.9,-12.4,-6.3,-0.7,5.4,9.9,10,6.2,0.1,-5.5,-10.7,-2.7]
["Канин Нос",-8.2,-9.6,-8.7,-4.8,-0.8,4.2,8.4,8.6,5.8,1.6,-1.9,-5.6,-0.9]
["Коткино",-17.3,-17.8,-12.6,-5.4,0.9,8.4,12.9,10.9,5.6,-1.8,-9,-13.5,-3.2]
["Нарьян-Мар",-16.9,-17.3,-14.3,-6.7,-0.3,7.4,12.7,11,5.6,-1.6,-8.4,-13.7,-3.5]
["Ходовариха",-15.5,-16.9,-14.6,-8.6,-2.9,-2.5,8.3,8.4,5.1,-1,-6.9,-11.7,-4.5]
["Хоседа-Хард",-19.6,-19.5,-15.8,-7.6,-1.1,7.4,12.6,10.1,4.8,-3.5,-11.2,-16.7,-5]
["Ярославская область"]
["Ярославль",-11.9,-10.7,-5.1,3.7,10.9,15.7,17.6,16,10,3.4,-2.7,-8.1,3.2]
[]
["АЗЕРБАЙДЖАНСКАЯ РЕСПУБЛИКА"]
["Баку",3.9,4.1,6.3,11.2,17.7,22.6,25.7,25.7,21.8,16.6,11.1,6.8,null,14.5]
[]
["РЕСПУБЛИКА АРМЕНИЯ"]
["Ванадзор",-3.7,-2.3,1.4,7.5,12.1,15,17.6,17.7,14.2,8.9,3.9,-1.1,7.6]
["Горис",-0.5,-0.2,2.3,8.1,12.5,15.9,18.5,17.9,14.2,9.4,5.3,1.7,8.8]
["Ереван",-3.4,-0.9,5.3,12.4,17.4,21.6,25.5,25.2,20.5,13.5,6.5,-0.2,12]
["Ехегнадзор",-3.8,-1.8,3.6,10.3,15.3,19.8,24.1,24.2,20.1,12.9,6,-0.8,10.8]
["Камо",-7.5,-6.3,-2.5,3.9,8.9,12.5,15.7,15.8,12,6.7,0.6,-4.8,4.6]
["Кафан",0.8,2,5.2,11.4,16.2,20,23.3,22.8,18.6,12.8,7.2,2.4,11.9]
["Севан",-8.2,-7.4,-3.3,3.5,8.8,12.1,15.7,15.7,12.2,6.4,0.6,-5.5,4.2]
["Сисиан",-4.8,-3.2,0.5,6.5,11.3,14.8,17.9,17.6,13.8,8.3,2.6,-2.7,6.9]
["Спитак",-4.4,-3.4,0.4,6.7,11.5,14.6,17.6,17.9,14.2,9,3.3,-1.9,7.1]
["Степанаван",-3.6,-2.8,0.6,6.7,11.3,14.2,17.1,16.8,13.3,8.2,3.1,-1.8,6.9]
[]
["РЕСПУБЛИКА БЕЛАРУСЬ"]
["Брестская область"]
["Брест",-4.5,-3.5,0.7,7.3,13.6,16.7,18.4,17.4,13.3,7.7,2.6,-1.8,7.3]
["Витебская область"]
["Витебск",-7.9,-7.2,-2.7,5.1,12.6,16,17.8,16.2,11.1,5.3,-0.3,-5.1,5.1]
["Полоцк",-7.3,-6.8,-2.5,5,12.3,15.8,17.5,16.1,11.1,5.5,0,-4.6,5.2]
["Гомельская область"]
["Василевичи",-6.6,-5.6,-1,6.8,13.9,17,18.4,17.2,12.4,6.6,1,-3.7,6.4]
["Гомель",-7,-6.1,-1.5,6.6,13.9,17,18.5,17.4,12.5,6.5,0.7,-4.1,6.2]
["Гродненская область"]
["Гродно",-5.1,-4.4,-0.5,6.3,12.9,16.1,17.8,16.7,12.5,7,1.7,-2.7,6.5]
["Минская область"]
["Минск",-6.9,-6.2,-2,5.5,12.7,16,17.7,16.3,11.6,5.8,0.2,-4.3,5.5]
["Могилевская область"]
["Горки",-8.3,-7.8,-3.3,4.8,12.4,15.9,17.6,16.1,11,5.1,-0.6,-5.4,4.8]
["Могилев",-7.6,-6.9,-2.3,5.5,12.9,16.3,18,16.5,11.6,5.4,-0.1,-4.9,5.4]
[]
["ГРУЗИЯ"]
["Ахалкалаки",-6.6,-5.5,-1.4,5.2,9.7,12.6,15.8,15.5,12,6.8,1.6,-3.7,5.2]
["Казбеги",-14.7,-14.5,-12.3,-7.6,-3.1,0,3.5,3.6,0.2,-4.4,-8.2,-12.1,-5.8]
["Крестовый перевал",-10.5,-10,-6.9,-1,3.4,7.2,10.6,10,6.7,1.4,-3.1,-8,0]
["Мамисонский перевал",-11.6,-11.1,-8.7,-3.4,0.8,4.2,7.9,7.6,4.3,-1,-5.3,-9.4,-2.1]
["Местиа",-5.8,-3.9,0,5.8,10.6,13.6,16.9,15.9,11.9,6.7,1.5,-3.7,5.8]
["Мта-Сабуети",-3.4,-2.8,0.3,6.1,10.4,13.5,16,15.9,12.7,7.7,3.3,0.9,6.6]
["Поти",5.8,6.7,8.8,12.6,16.4,20.3,22.7,22.8,19.8,15.5,11.5,7.9,14.2]
["Сакара",4.2,5.2,8.7,13.8,17.9,21.1,23.2,23.7,20.3,15.3,10.6,6.3,14.2]
["Самтредиа",5.1,6.2,9.1,13.7,17.7,21,23,23,21.1,15.5,11.1,7.1,14.5]
["Тбилиси",2.1,3.3,7.4,13.2,17.8,21.6,24.8,24.1,20,13.8,8.5,4.2,13.4]
["Телави",1,2.1,6.1,12.1,16.6,20.2,23.4,22.4,18.4,12.4,7.8,3.3,12.2]
["Цхинвали",-1,0.1,4,9,14.3,17.7,20.6,20.3,16.5,10.8,5.8,1.3,10]
["Шираки",-1.8,-0.4,4.1,10.3,15.3,19.4,22.9,22.1,17.8,11.1,5.7,0.8,10.6]
["Абхазская Республика"]
["Гудаута",6.1,6.8,8.8,12.9,16.7,20.5,23,23.1,20,15.6,11.8,8.2,14.5]
["Псху",-1.3,0.4,3.9,9.3,13.7,16.7,19.6,18.8,14.7,9.4,4.8,0.4,9.2]
["Сухуми",5.9,6.7,8.8,12.9,16.7,20.7,22.7,22.8,19.9,15.6,11.8,8,14.4]
["Аджарская Республика"]
["Батуми",7.1,7.3,8.4,11.9,16.4,20.4,22.8,23,20.2,16,12.3,9.3,14.6]
["Хуло",1.1,1.9,4.8,9.9,13.9,16.6,18.4,18.5,15.9,11.8,7.6,3.1,10.3]
[]
["РЕСПУБЛИКА КАЗАХСТАН"]
["Акмолинская область"]
["Астана",-16.8,-16.5,-10.1,3,12.7,18.2,20.4,17.8,11.5,2.6,-7,-14,1.8]
["Атбасар",-17.9,-17.5,-11.1,2.6,12.4,18.1,20.2,17.6,11.4,2.3,-7.5,-14.9,1.3]
["Актюбинская область"]
["Актюбинск",-14.9,-14.4,-7.3,5.9,15,20.2,22.5,20.4,13.7,4.6,-3.9,-11.3,4.2]
["Караулкельды",-13,-12.3,-15.4,8,16.3,21.8,24.2,22.4,15.3,5.6,-2.3,-9,6]
["Уил",-13,-12.1,-4.9,8.3,16.8,22.1,24.6,22.7,15.7,6.3,-2.1,-8.8,6.3]
["Челкар",-14.6,-14,-6,8.2,17,22.7,25.1,22.9,15.8,6.2,-2.6,-10.3,5.9]
["Алматинская область"]
["Алматы",-6.5,-5.1,2,10.8,16.2,20.7,23.5,22.3,17,9.5,0.9,-4.5,8.9]
["Баканас",-11.4,-9.6,0.1,11,17.8,23.3,25.8,23.3,16.8,8.4,-1,-8,8]
["Атырауская область"]
["Атырау",-9.6,-8.7,-1.5,9.6,18.2,23.4,25.7,23.7,16.8,8.2,0.4,-5.6,8.4]
["Ганюшкино",-7.2,-6.6,-0.2,10.2,18.1,23.1,25.2,23.4,16.8,8.6,1.7,-3.7,9.1]
["Восточно-Казахстанская область"]
["Зайсан",-17,-15,-6.5,6.9,15.3,20.7,22.9,21.2,15.3,6.2,-5.8,-14.6,4.1]
["Зыряновск",-22.6,-20.8,-11.7,1.9,12.2,17.1,18.9,16.5,10.6,2.4,-10.8,-19.5,-0.5]
["Катон-Карагай",-13.7,-12.2,-6.8,2.7,10.1,14.8,16.5,14.9,9.9,2,-7.6,-12.4,1.5]
["Лениногорск",-12.5,-12.1,-6.3,3,10.4,15.3,17.1,14.9,9.9,2.7,-6.7,-11.2,2]
["Усть-Каменогорск",-16.5,-16,-7.8,4.8,13.4,18.7,20.7,18.3,12.4,5,-6.1,-13.8,2.8]
["Шемонаиха",-17,-16.5,-8.9,3.8,12.7,18.1,20.1,17.5,11.9,3.8,-7.1,-14.3,2]
["Джамбулская область"]
["Джамбул",-5,-3.3,3.3,11.3,16.8,22.1,24.9,22.8,17.1,9.9,2,-3.4,9.9]
["Фурмановка",-8.7,-6.6,2,11.9,18.2,22.9,24.9,22.6,16.6,9.1,0.1,-6.3,8.9]
["Джезказганская область"]
["Балхаш",-14.4,-13.7,-4.9,7.7,16,21.9,24.2,21.8,15.3,6.5,-3.4,-11.1,5.5]
["Карсакпай",-15.2,-14.5,-7.4,6.2,14.7,20.7,23,20.5,13.8,4.4,-4.9,-11.9,4.1]
["Западно-Казахстанская область"]
["Джамбейты",-13.4,-12.9,-6.4,7.4,15.9,21.3,23.7,21.8,14.8,5.6,-2.5,-9,5.5]
["Уральск",-13.5,-13.2,-6.7,6.2,15.4,20.3,22.6,20.6,13.8,5.1,-2.9,-9.8,4.8]
["Карагандинская область"]
["Караганда",-14.5,-14.2,-7.7,4.6,12.8,18.4,20.4,17.8,12,3.2,-6.3,-12.3,2.9]
["Каркаралинск",-13.8,-13.6,-7.8,3.1,10.8,16,18.1,15.7,10.1,2.2,-6.6,-12,1.9]
["Кзыл-Ординская область"]
["Аральское Море",-12.6,-11.9,-3.7,9.3,17.9,23.8,26.5,24.2,17.3,7.6,-1.3,-8.7,7.4]
["Казалинск",-10.8,-9.9,-1.5,10.5,18.9,24.1,26.3,23.9,17.1,8.2,-0.4,-7.2,8.2]
["Кзыл-Орда",-9.1,-7.3,0.9,12,19.5,24.5,26.4,23.9,17.2,8.6,0.3,-6.2,9.2]
["Кокчетавская область"]
["Кокчетав",-15.8,-15.3,-9.2,3.3,12.1,17.8,19.8,17.1,11.5,2.8,-6.7,-13.4,2]
["Кустанайская область"]
["Кустанай",-17,-16.6,-9.8,3.8,13,18.6,20.4,17.9,12,3,-6.2,-14.1,2.1]
["Мангистауская область"]
["Форт-Шевченко",-2.9,-2.3,2.5,10.4,17.7,22.8,25.6,24.6,19.5,12.3,5.5,0.2,11.3]
["Павлодарская область"]
["Баянаул",-13.2,-13.1,-7,4.7,12.7,18.6,20.5,17.7,12.1,3.5,-5.7,-11.4,3.3]
["Павлодар",-17.6,-17.3,-9.4,4.2,13.2,19.5,21.4,18.5,12.3,3.5,-7,-14.4,2.2]
["Северо-Казахстанская область"]
["Петропавловск",-18.1,-16.9,-10.3,2.4,11.6,17,18.9,16.2,10.7,1.9,-7.8,-15.2,0.9]
["Семипалатинская область"]
["Аягуз",-16.5,-15.8,-8,5,12.7,18.3,20.7,18.5,12.1,3.6,-7.2,-14.1,2.4]
["Бахты",-13.2,-11.4,-1.9,9.4,15.8,20.7,23,21.5,15.4,7.3,-2.8,-10.5,6.1]
["Кокпекты",-20.5,-18.6,-10.4,3.7,12.8,18.3,20.7,18.6,12.4,3.2,-8.7,-17.6,1.2]
["Семипалатинск",-16,-15.6,-8.4,4.7,14.1,19.8,21.9,19.3,13,4.5,-5.9,-13.3,3.2]
["Талды-Курганская область"]
["Жаркент",-9.1,-6.1,3.2,12.6,18.1,22.1,24,22.7,17.2,9.8,0.7,-6,9.1]
["Талды-Курган",-9.7,-8,0,10.2,16.3,21.1,23.5,21.7,16,8.3,-0.9,-7.3,7.6]
["Тургайская область"]
["Амангельды",-16.5,-16.3,-8.8,6.1,15.1,20.7,23,20.3,13.6,4.1,-5.2,-12.8,3.6]
["Тургай",-16.2,-15.9,-8.1,6.4,16,22,24.4,21.7,15,5.2,-4.1,-12.2,4.5]
["Южно-Казахстанская область"]
["Туркестан",-5.4,-2.2,5.4,14.1,20.6,25.9,28.4,26.3,19.8,11,3.1,-2.3,12.1]
["Чимкент",-2,0,5.6,13.1,18.4,23.5,26.3,24.8,19.3,12.3,5.2,0.2,12.2]
[]
["КЫРГЫЗСКАЯ РЕСПУБЛИКА"]
["Иссык-Кульская область"]
["Каракол",-7.1,-5.5,-0.1,7,11.8,14.6,16.9,16.2,12.3,6.2,-1.1,-5.3,5.5]
["Чолпон-Ата",-3.4,-2.1,1.7,7.1,11.3,14.6,17,16.7,13.1,7.8,1.9,-1.6,7]
["Нарынская область"]
["Кочкорка",-9.9,-6,0.5,6.5,11,13.8,16.3,15,10.9,4.8,-3.2,-8.8,4.2]
["Нарын",-17.3,-14.4,-4.5,6.3,11.4,14.4,17,16.8,12.4,5.3,-4.5,-13.4,2.5]
["Сусамыр",-21.5,-19.4,-11.7,-0.9,8,10.7,13.1,12.7,8.2,1.3,-10.5,-19.2,-2.4]
["Ошская область"]
["Гульча",-7.6,-4.5,2.5,9.5,13.6,16.3,19.2,19.2,14.5,7.9,1.4,-4,7.3]
["Ош",-3.5,-0.9,5.7,12.8,18,22.3,24.7,23.1,18.1,11.2,4.3,-0.7,11.2]
["Хайдаркан",-6.8,-5.1,0.3,7,12.2,15.8,18.5,18,13.3,6.6,0.8,-3.2,6.4]
["Таласская область"]
["Талас",-6.6,-4.3,1.6,8.7,14.1,18,20.2,18.6,13.5,7.5,0.6,-3.8,7.3]
["Чуйская область"]
["Бишкек",-5.6,-3.2,3.8,11.4,16.9,21.3,24.1,22.6,17.3,10.1,2.2,-2.9,9.8]
[]
["РЕСПУБЛИКА МОЛДОВА"]
["Кишинев",-3.5,-2.2,2.6,9.7,15.9,19.4,21.4,20.7,16,10.1,4.1,-0.8,9.4]
[]
["РЕСПУБЛИКА ТАДЖИКИСТАН"]
["Районы республиканского подчинения"]
["Душанбе",2,4.1,9.1,15.4,19.7,24.7,26.8,24.6,19.8,13.9,8.3,4,14.4]
["Гарм",-3.9,-2,3.7,11.4,15.6,19.7,23.6,23.9,19.4,12.4,5.8,0.2,10.8]
["Горно-Бадахшанская автономная область"]
["Мургаб",-17.3,-13.5,-6.6,0.4,5.4,9.4,13.2,12.8,7.2,-0.4,-8.6,-15.3,-1.1]
["Хорог",-7.7,-5.3,1.2,9.7,14.8,19.2,22.7,22.8,18.2,10.8,3.4,-3.4,8.9]
["Ленинабадская область"]
["Исфара",-1.5,1.2,7.1,14.6,20,24.4,26.6,24.9,19.6,12.5,5.4,0.6,13]
["Пенджикент",-0.4,1.5,6.6,12.9,17.7,22.6,25.1,23.5,18.6,12.4,6.1,1.9,12.4]
["Ура-Тюбе",-1.8,0.1,4.9,11.8,17.2,22.1,24.8,22.9,17.6,11.1,4.6,0.2,11.3]
["Худжанд",-0.8,2,9.7,16.1,21.9,26.8,28.6,26.6,21.1,13.5,6.8,1.5,14.5]
["Хатлонская область"]
["Куляб",2.3,5.4,10.4,16.7,21.5,27.2,30.2,28.5,23.4,16.9,10,4.8,16.4]
["Курган-Тюбе",1.8,5.4,10.8,17.4,22.5,27.1,28.6,26.4,21.2,15.4,9,4.1,15.8]
["Шаартуз",2.9,6,11.2,18.3,24.1,28.6,30.7,28.6,22.9,16.5,9.7,4.8,17]
[]
["РЕСПУБЛИКА УЗБЕКИСТАН"]
["Андижанская область"]
["Андижан",-2.2,1.2,8.1,16.1,21.4,25.7,27.2,25,19.8,13.1,5.6,0.5,13.5]
["Бухарская область"]
["Бухара",0.4,2.7,8.4,16.5,22.3,26.7,28.4,25.7,20.1,13.1,6.7,2.3,14.4]
["Джизакская область"]
["Галляарал",-2.3,0.5,6.2,13.1,18.5,24,26.9,24.6,18.3,11.1,4.2,-0.3,12.1]
["Джизак",-0.4,2,"2009-09-07",15.1,21.2,26.4,28.6,26.6,20.9,13.7,6.8,2.2,14.3]
["Каракалпакстан"]
["Каракалпакия",-8.2,-7.9,-0.5,10.3,18.6,24,27,24.6,17.3,8,0.7,-4.4,9.1]
["Муйнак",-5.9,-5.5,0.1,9.4,18.1,23.7,26.6,25,19.1,10.8,3.2,-2.4,10.2]
["Нукус",-4.9,-3.3,3.8,13.4,21.1,25.9,28,25.4,19.1,10.7,2.9,-2.9,11.6]
["Чимбай",-6.1,-4.5,2.4,12.4,19.9,24.4,26.4,24.1,17.9,9.8,2.1,-3.8,10.4]
["Кашкадарьинская область"]
["Гузар",2.9,5.3,9.8,16.6,22.6,27.7,29.9,28.2,22.9,16.2,9.6,5,16.4]
["Мубарек",1.5,4,9.1,16.7,23.5,28.9,31.8,29.4,22.7,14.6,7.3,2.6,16]
["Навоийская область"]
["Навои",0.9,3.6,8.4,15.8,21.7,26.3,28.3,25.9,19.9,13.3,7.1,2.7,14.5]
["Нурата",-0.1,2.2,7,14.3,20.4,25.8,28.1,25.8,19.7,12.4,6,1.5,13.6]
["Наманганская область"]
["Касансай",-1.4,0.9,6.6,13.9,18.8,22.9,25.4,24,19,12.6,5.7,0.8,12.4]
["Наманган",-2,1.1,8.5,16.2,21.5,25.7,27.2,25.2,20.2,13.5,5.9,0.2,13.7]
["Самаркандская область"]
["Каттакурган",-0.2,2.3,7.5,14.4,20.4,25.5,27.9,25.8,20,12.7,6.2,1.8,13.7]
["Самарканд",0.5,2.8,7.4,14.2,19.3,23.9,25.9,24,19,12.7,6.6,2.6,13.3]
["Сурхандарьинская область"]
["Денау",3.6,6.1,10.7,17.1,22.3,27,28.4,26.1,21.3,15.5,9.9,5.6,16.2]
["Термез",2.6,6,11.4,18.4,24.3,28.2,30.4,28.1,22.4,15.8,9.9,5.1,16.9]
["Шерабад",4,6.9,11.6,18.7,24.9,29.9,31.8,29.7,24.5,18,11.2,6.3,18.1]
["Сырдарьинская область"]
["Сырдарья",-1.5,1,7.7,15.2,21,25.4,26.8,24.3,18.8,12.3,5.3,0.2,13.1]
["Ташкентская область"]
["Ташкент",-0.4,2,7.9,14.7,20.2,24.9,27.1,25.1,19.6,12.8,6.7,2,13.6]
["Чарвак",-1.6,0.1,5.2,12.5,17.1,21.7,24.8,23.6,18.5,12.1,5.7,0.7,11.7]
["Ферганская область"]
["Коканд",-1.8,1.6,8.4,16.4,21.6,25.6,27.4,25.5,20.1,13.1,5.5,0.4,13.7]
["Фергана",-1.7,1.5,7.9,15.6,20.8,25,26.9,25,19.7,13.1,5.7,0.7,13.3]
["Хорезмская область"]
["Ургенч",-3.7,-2.3,4.9,14.4,21.6,26.4,28.2,25.7,19.4,11.4,3.8,-1.6,12.4]
[]
["УКРАИНА"]
["Винницкая область"]
["Винница",-5.8,-4.3,0.2,8,14.1,17.1,18.3,17.7,13.4,7.6,1.9,-2.5,7.1]
["Волынская область"]
["Ковель",-4.7,-3.4,1,7.9,13.7,16.8,18,17.2,13,7.8,2.6,-1.8,7.3]
["Луцк",-4.9,-3.5,0.9,8,13.5,16.8,18,17.4,13.3,7.9,2.6,-2,7.3]
["Днепропетровская область"]
["Днепропетровск",-5.5,-4.1,0.8,9.4,16,19.6,21.3,20.6,15.4,8.4,2.5,-2.1,8.5]
["Комиссаровка",-5.6,-4.2,0.7,9.1,15.5,18.9,20.5,19.8,14.7,8,2.4,-2.1,8.1]
["Кривой Рог",-5,-3.6,1.3,9.5,15.9,19.5,21.1,20.5,15.6,8.8,3,-1.6,8.8]
["Донецкая область"]
["Донецк",-6.1,-4.8,0.4,9.3,15.5,19,20.9,20.1,14.9,7.8,2,-2.6,8]
["Житомирская область"]
["Житомир",-6,-4.6,-0.1,7.7,13.9,17,18,17.4,13,7.4,1.8,-2.7,6.9]
["Овруч",-6.2,-4.8,-0.1,7.6,14.2,17.2,18.1,17.3,12.8,7.1,1.5,-2.9,6.8]
["Закарпатская область"]
["Ужгород",-2.8,-0.2,4.7,10.7,15.6,18.5,19.9,19.4,15.5,10,4.9,-0.4,9.7]
["Запорожская область"]
["Запорожье",-4.2,-2.9,1.7,9.9,16.4,20.2,22,21.2,16.2,9.5,3.8,-0.8,9.4]
["Кирилловка",-5.2,-4,0.7,9,15,18.7,20.7,19.8,14.8,8.1,2.5,-1.9,8.2]
["Ивано-Франковская область"]
["Ивано-Франковск",-5.1,-3.2,1.4,8.1,13.5,16.6,17.9,17.3,13.5,8,2.6,-2.1,7.4]
["Киевская область"]
["Киев",-5.6,-4.2,0.7,8.7,15.1,18.2,19.3,18.6,13.9,8.1,2.1,-2.3,7.7]
["Кировоградская область"]
["Гайворон",-5.1,-3.6,1.2,9.1,15.2,18.2,19.5,18.9,14.4,8.3,2.8,-1.6,8.1]
["Знаменка",-5.9,-4.6,0.3,8.7,15.1,18.5,19.9,19.3,14.4,7.9,2.1,-2.5,7.8]
["Кировоград",-5.7,-4.4,0.5,8.9,15.3,18.6,20,19.4,14.7,8.1,2.3,-2.3,8]
["Луганская область"]
["Луганск",-5.9,-4.8,0.8,10,16.3,19.9,21.7,20.6,15,7.9,2.4,-2.2,8.5]
["Львовская область"]
["Львов",-4.6,-3.1,1.1,7.7,13.2,16.1,17.3,16.8,13,8,2.5,-2.1,7.2]
["Николаевская область"]
["Николаев",-3.1,-1.8,2.6,10.2,16.5,20.4,22.3,21.8,16.9,10.3,4.4,-0.1,10]
["Одесская область"]
["Измаил",-1.7,-0.1,4,10.5,16.2,20.1,21.8,21.2,17,11,5.7,1,10.6]
["Любашевка",-5,-3.5,1.1,9.1,15.2,18.5,20,19.5,15.2,8.8,2.9,-1.3,8.4]
["Одесса",-1.7,-1,2.6,9,15.5,19.4,21.4,21.2,17.1,11.1,5.9,1.4,10.2]
["Раздельное",-3.6,-2.3,2.2,9.6,15.7,19.3,21,20.7,16.2,9.9,4,-0.6,9.3]
["Сарата",-2,-0.8,3.3,9.9,15.9,19.8,21.6,21.2,16.4,10.4,5.2,0.6,10.1]
["Полтавская область"]
["Лубны",-6.4,-5.2,-0.1,8.6,15.5,18.6,19.8,18.9,13.9,7.5,1.4,-3.1,7.5]
["Полтава",-6.6,-5.3,-0.1,8.8,15.4,18.7,20.1,19.4,14.3,7.6,1.5,-3.1,7.6]
["Ровенская область"]
["Ровно",-5.4,-4,0.3,7.7,13.7,16.6,17.8,17.2,13.1,7.7,2.2,-2.4,7]
["Сарны",-5.4,-4,0.6,8,14.1,17,18.2,17.4,13.1,7.7,2.3,-2.2,7.2]
["Сумская область"]
["Ромны",-7.3,-6,-0.8,8,14.7,17.8,19,18.1,13.1,6.8,0.8,-3.8,6.7]
["Сумы",-7.7,-6.4,-1.1,7.9,14.9,18,19.2,18.2,13,6.6,0.6,-4.1,6.6]
["Тернопольская область"]
["Тернополь",-5.8,-4.2,0,7.4,13.3,16.2,17.4,16.8,12.9,7.4,1.8,-2.9,6.7]
["Харьковская область"]
["Лозовая",-6.5,-5.2,0,9.1,15.7,19.2,20.8,19.9,14.6,7.6,1.7,-2.9,7.8]
["Харьков",-7,-5.7,-0.3,8.9,15.6,19,20.4,19.5,14.1,7.3,1.3,-3.3,7.5]
["Херсонская область"]
["Аскания-Нова",-3.1,-2,2.2,9.6,15.6,20,22.4,21.6,16.4,9.7,4.4,0.3,9.8]
["Геническ",-2.3,-1.6,2,9.3,16.1,20.6,22.9,22.1,17.3,10.7,5.4,1.1,10.3]
["Херсон",-3,-1.8,2.3,10,16,19.9,21.9,21.3,16.4,9.8,4.5,0.1,9.8]
["Хмельницкая область"]
["Хмельницкий",-5.5,-4,0.3,7.8,13.9,16.8,18,17.4,13.2,7.6,2,-2.6,7.1]
["Черкасская область"]
["Золотоноша",-5.9,-4.6,0.5,8.9,15.4,18.5,19.7,18.8,13.9,7.7,2.1,-2.5,7.7]
["Умань",-5.7,-4.2,0.4,8.5,14.6,17.6,19,18.2,13.6,7.6,2.1,-2.4,7.4]
["Черниговская область"]
["Чернигов",-7.1,-5.6,-0.6,7.8,14.5,17.6,18.7,17.7,12.8,6.8,1.2,-3.3,6.7]
["Черновицкая область"]
["Черновцы",-4.9,-2.9,1.7,8.7,14.3,17.4,18.7,18,14.3,8.6,2.9,-1.9,7.9]
["Автономная республика Крым"]
["Ай-Петри",-3.6,-3.1,-0.6,4.9,9.5,12.9,15.1,14.7,10.9,6.5,2.6,-1.5,5.7]
["Клепинино",-1.5,-0.5,3.1,10.4,15.7,19.9,22.2,21.5,16.6,10.4,5.9,1.9,10.5]
["Симферополь",-0.5,0.4,3.6,10.2,15.2,19.2,21.5,21,16.6,10.7,6.3,2.4,10.6]
["Феодосия",0.8,1.4,4.4,10.6,16.1,20.8,23.4,22.8,18.4,12.4,7.8,4.1,11.9]
["Ялта",3.9,4.2,6,10.8,15.6,20.2,23.2,23,19,13.6,9.5,6.3,12.9]

{"sheet":"Лист1","index":2,"n_rows":70,"n_cols":1,"rows_kept":70,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["Версия для печати"]
[]
["СООТНОШЕНИЯ МЕЖДУ ЕДИНИЦАМИ ФИЗИЧЕСКИХ ВЕЛИЧИН"]
["                    В РАЗЛИЧНЫХ СИСТЕМАХ ИЗМЕРЕНИЯ"]
[]
["---------------------------------------------------------------------------------------"]
["|                                       МОЩНОСТЬ                                      |"]
["|-------------------------------------------------------------------------------------|"]
["|Единица |   1 кВт    |   1 МВт    |  1 ккал/ч  | 1 Гкал/ч  |            |            |"]
["|        |            |            |            |           |            |            |"]
["|--------|------------|------------|------------|-----------|------------|------------|"]
["|        |            |  -3        |            |         -3|            |            |"]
["|1 кВт   |1           |10          |860         |0,86 x 10  |            |            |"]
["|--------|------------|------------|------------|-----------|------------|------------|"]
["|        |  3         |            |        3   |           |            |            |"]
["|1 МВт   |10          |1           |860 х 10    |0,86       |            |            |"]
["|--------|------------|------------|------------|-----------|------------|------------|"]
["|        |          -3|          -6|            |  -6       |            |            |"]
["|1       |1,163 x 10  |1,163 x 10  |1           |10         |            |            |"]
["|ккал/ч  |            |            |            |           |            |            |"]
["|--------|------------|------------|------------|-----------|------------|------------|"]
["|        |          3 |            |  6         |           |            |            |"]
["|1       |1,163 x 10  |1,163       |10          |1          |            |            |"]
["|Гкал/ч  |            |            |            |           |            |            |"]
["|-------------------------------------------------------------------------------------|"]
["|                                       ДАВЛЕНИЕ                                      |"]
["|-------------------------------------------------------------------------------------|"]
["|Единица |1 кгс/кв. м |1 кгс/кв. см|    1 ат    |   1 Па    |   1 бар    |            |"]
["|        |            |            |            |           |            |            |"]
["|--------|------------|------------|------------|-----------|------------|------------|"]
["|        |            |  -4        |         -4 |           |         -5 |            |"]
["|1 кгс/  |1           |10          |1,02 x 10   |9,81       |9,81 х 10   |            |"]
["|кв. м   |            |            |            |           |            |            |"]
["|--------|------------|------------|------------|-----------|------------|------------|"]
["|        |  4         |            |            |           |            |            |"]
["|1 кгс/  |10          |1           |1           |0,981      |0,968       |            |"]
["|кв. см  |            |            |            |           |            |            |"]
["|--------|------------|------------|------------|-----------|------------|------------|"]
["|        |  4         |            |            |         -5|            |            |"]
["|1 ат    |10          |1           |1           |1,01 х 10  |1,01        |            |"]
["|--------|------------|------------|------------|-----------|------------|------------|"]
["|        |            |         4  |         -6 |           |  -5        |            |"]
["|1 Па    |0,802       |9,81 х 10   |9,87 х 10   |1          |10          |            |"]
["|--------|------------|------------|------------|-----------|------------|------------|"]
["|        |         4  |            |            |  5        |            |            |"]
["|1 бар   |1,02 x 10   |1,02        |0,987       |10         |1           |            |"]
["|-------------------------------------------------------------------------------------|"]
["|                                  КОЛИЧЕСТВО ТЕПЛОТЫ                                 |"]
["|-------------------------------------------------------------------------------------|"]
["|Единица |   1 кал    |   1 ккал   |   1 Гкал   |   1 Дж    |   1 кДж    |   1 ГДж    |"]
["|        |            |            |            |           |            |            |"]
["|--------|------------|------------|------------|-----------|------------|------------|"]
["|        |            |  3         |  -9        |           |          -3|          -9|"]
["|1 кал   |1           |10          |10          |4,187      |4,187 x 10  |4,187 x 10  |"]
["|--------|------------|------------|------------|-----------|------------|------------|"]
["|        |  3         |            |  -6        |          3|            |          -6|"]
["|1 ккал  |10          |1           |10          |4,187 х 10 |4,187       |4,187 х 10  |"]
["|--------|------------|------------|------------|-----------|------------|------------|"]
["|        |  9         |  6         |            |          9|          -6|            |"]
["|1 Гкал  |10          |10          |1           |4,187 х 10 |4,187 x 10  |4,187       |"]
["|--------|------------|------------|------------|-----------|------------|------------|"]
["|        |            |          -3|          -9|           |  -3        |  -9        |"]
["|1 Дж    |0,239       |0,239 x 10  |0,239 х 10  |1          |10          |10          |"]
["|--------|------------|------------|------------|-----------|------------|------------|"]
["|        |          -3|            |          -6|  3        |            |  -6        |"]
["|1 кДж   |0,239 x 10  |0,239       |0,239 x 10  |10         |1           |10          |"]
["|--------|------------|------------|------------|-----------|------------|------------|"]
["|        |          -9|          -6|            |  9        |            |            |"]
["|1 ГДж   |0,239 х 10  |0,239 x 10  |0,239       |10         |10          |1           |"]
["---------------------------------------------------------------------------------------"]

{"sheet":"Лист4","index":3,"n_rows":130,"n_cols":44,"rows_kept":130,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["t-t'",null,null,"Показания по сухому термометру"]
[null,-4,-3,-2,-1,0,1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,16,17,18,19,20,21,22,23,24,25,26,27,28,29,30,31,32,33,34,35,36,37,38]
[0,100,100,100,100,100,100,100,100,100,100,100,100,100,100,100,100,100,100,100,100,100,100,100,100,100,100,100,100,100,100,100,100,100,100,100,100,100,100,100,100,100,100,100]
[0.1,98,98,98,98,98,98,98,99,98,98,98,99,99,99,99,99,99,99,99,99,99,99,99,99,99,99,99,99,99,99,99,99,99,99,99,99,99,99,99,99,99,99,99]
[0.2,95,95,96,96,96,96,96,97,97,97,97,97,97,97,97,97,98,98,98,98,98,98,98,98,98,98,98,98,98,98,98,98,98,98,98,99,99,99,99,99,99,99,99]
[0.3,93,93,93,94,94,94,94,95,95,95,95,96,96,96,96,96,96,96,97,97,97,97,97,97,97,97,97,97,97,97,98,95,98,97,98,98,98,98,98,98,98,98,98]
[0.4,90,91,91,92,92,92,93,93,93,94,94,94,94,95,95,95,95,95,95,96,96,96,96,96,96,96,96,96,97,97,97,97,97,97,97,97,97,97,97,97,97,97,97]
[0.5,88,88,89,89,90,90,91,92,92,92,92,93,93,93,93,94,94,94,94,94,95,95,95,95,95,95,95,96,96,96,96,96,96,96,96,96,96,96,97,98,97,97,96]
[0.6,85,86,87,87,88,89,89,90,90,90,91,91,92,92,92,92,93,93,93,93,93,94,94,94,94,94,95,95,95,95,95,95,95,95,95,96,96,96,96,96,96,96,96]
[0.7,83,84,84,85,86,87,87,88,88,89,89,90,90,91,91,91,92,92,92,92,93,93,93,93,93,94,94,94,94,94,94,94,95,94,95,95,95,95,95,95,95,95,95]
[0.8,80,81,82,83,84,85,85,86,87,87,88,88,89,89,90,90,90,91,91,91,91,92,92,92,92,93,93,93,93,93,93,94,94,94,94,94,94,94,94,95,95,95,95]
[0.9,78,79,80,81,82,83,84,85,85,86,86,87,87,88,88,89,89,89,90,90,90,91,91,91,91,92,92,92,92,93,93,93,93,93,93,93,94,94,94,94,94,94,94]
[1,75,77,78,79,80,81,82,83,83,84,85,85,86,87,87,87,88,88,89,89,89,90,90,90,91,91,91,91,91,92,92,92,92,92,93,93,93,93,93,93,93,93,94]
[1.1,73,74,76,77,78,79,80,81,82,83,83,84,85,85,86,86,87,87,88,88,88,89,89,89,90,90,90,90,91,91,91,91,91,91,92,92,92,92,92,93,93,93,93]
[1.2,70,72,73,75,76,77,78,80,80,81,82,83,83,84,84,85,86,86,86,87,87,88,88,88,89,89,89,90,90,90,90,90,91,91,91,91,91,92,92,92,92,92,92]
[1.3,68,70,71,73,74,75,76,78,79,79,80,81,82,83,83,84,84,85,85,86,86,87,87,87,88,88,88,89,89,89,89,90,87,90,90,91,91,91,91,91,91,91,92]
[1.4,65,67,69,71,72,73,75,76,77,78,79,80,80,81,82,83,83,84,84,85,85,86,86,87,87,87,88,88,88,88,89,89,89,89,90,90,90,90,90,91,91,91,91]
[1.5,63,65,67,69,70,72,73,74,75,76,77,78,79,80,81,81,82,83,83,84,84,85,85,86,86,86,87,87,87,88,88,88,88,88,89,89,89,90,90,90,92,90,90]
[1.6,61,63,62,66,68,70,71,73,74,75,76,77,78,79,79,80,81,82,82,83,83,83,84,85,85,85,86,86,87,87,87,87,88,88,88,88,89,89,89,89,89,90,90]
[1.7,58,60,63,64,66,68,69,71,72,73,74,75,76,77,78,79,80,80,81,82,82,83,83,84,84,85,85,85,86,86,86,87,87,87,87,88,88,88,88,89,89,89,89]
[1.8,56,58,60,62,64,66,68,69,70,72,73,74,75,76,77,78,79,79,80,81,81,82,82,83,83,84,84,85,85,85,86,86,86,86,87,87,87,87,88,88,88,88,89]
[1.9,53,56,58,60,62,64,66,68,69,70,71,73,74,75,76,77,77,78,79,80,80,81,81,82,82,83,83,84,84,84,85,85,85,86,86,86,87,87,87,87,87,88,88]
[2,51,54,56,58,60,62,64,66,67,68,70,71,72,73,74,75,76,77,78,78,79,80,80,81,81,82,82,83,83,84,84,84,85,85,85,86,86,86,86,87,87,87,87]
[2.1,49,51,54,56,58,60,62,64,66,67,69,70,71,72,73,74,75,76,77,77,78,79,79,80,81,81,82,82,82,83,83,84,84,84,85,85,85,85,86,86,86,86,87]
[2.2,46,49,52,54,56,59,61,63,64,66,67,68,70,71,72,73,74,75,76,76,77,78,78,79,80,80,81,81,82,82,82,83,83,83,84,84,85,85,85,85,86,86,86]
[2.3,44,47,50,52,55,57,59,61,62,64,66,67,68,70,71,72,73,74,75,75,76,77,78,78,79,79,80,80,81,81,82,82,83,80,83,84,84,84,84,85,85,85,85]
[2.4,41,45,47,50,53,55,57,59,61,63,64,66,67,68,69,71,72,73,74,74,75,76,77,77,78,78,79,80,80,81,81,81,82,82,83,83,83,84,84,84,84,85,85]
[2.5,39,42,45,48,51,53,55,57,59,61,63,64,66,67,68,69,70,71,72,73,74,75,76,76,77,78,78,79,79,80,80,81,81,81,82,82,83,83,83,83,84,86,84]
[2.6,37,40,43,46,49,51,54,56,58,60,61,63,64,66,67,68,69,70,71,72,73,74,75,75,76,77,77,78,78,79,79,80,80,81,81,82,82,82,83,83,83,83,84]
[2.7,34,38,41,44,47,49,52,54,56,58,60,61,63,64,66,67,68,69,70,71,72,73,74,75,75,76,77,77,78,78,79,79,80,80,80,81,81,82,82,82,82,83,83]
[2.8,32,36,39,42,45,48,50,53,54,57,58,60,62,63,65,66,67,68,69,70,71,72,73,74,74,75,76,76,77,77,78,78,79,79,80,80,81,81,81,82,82,82,82]
[2.9,29,33,37,40,43,46,48,51,53,55,57,59,60,62,63,65,66,67,68,69,70,71,72,73,74,74,75,76,76,76,77,78,78,78,79,79,80,80,81,81,81,82,82]
[3,27,31,35,38,41,44,47,49,51,54,55,57,59,61,62,64,65,66,67,68,69,70,71,72,73,73,74,75,75,76,76,77,77,78,78,79,79,80,80,80,81,81,81]
[3.1,25,29,33,36,39,42,45,48,50,52,54,56,58,59,61,62,64,65,66,67,68,69,70,71,72,73,73,74,75,75,76,76,77,77,78,78,79,79,79,80,80,80,81]
[3.2,22,27,30,34,37,40,43,46,48,51,53,55,56,58,60,61,63,64,65,66,67,68,69,70,71,72,72,73,74,74,75,76,76,76,77,77,78,78,79,79,79,80,80]
[3.3,20,24,28,32,35,39,42,44,47,49,51,53,55,57,59,60,61,63,64,65,66,67,68,69,70,71,72,72,73,74,74,75,75,76,74,77,77,78,78,78,79,79,80]
[3.4,18,22,26,30,34,37,40,43,45,48,50,52,54,56,57,59,60,62,63,64,65,66,67,68,69,70,71,72,72,73,74,74,75,75,76,76,77,77,77,78,78,79,79]
[3.5,15,20,24,28,32,35,38,41,44,46,48,51,53,54,56,58,59,61,62,63,64,65,67,67,68,69,70,71,71,72,73,73,74,74,75,76,76,76,77,77,78,78,80]
[3.6,13,18,22,26,30,33,36,40,42,45,47,49,51,53,55,57,58,60,61,62,63,65,66,66,68,68,69,70,71,71,72,73,73,74,74,75,75,76,76,77,77,77,78]
[3.7,11,16,20,24,28,31,35,38,41,43,46,48,50,52,54,55,57,59,60,61,62,64,65,66,67,68,68,69,70,71,71,72,73,73,74,74,75,75,76,76,76,77,77]
[3.8,8,13,18,22,26,30,33,36,39,41,44,47,49,51,53,54,56,58,59,60,62,63,64,65,66,67,68,68,69,70,71,71,72,72,73,74,74,75,75,75,76,76,77]
[3.9,6,11,16,20,24,28,31,35,38,40,43,45,47,50,51,53,55,56,58,59,61,62,63,64,65,66,67,68,68,69,70,71,71,72,72,73,73,74,74,75,75,76,76]
[4,4,9,14,18,22,26,30,33,36,39,41,44,46,48,50,52,54,55,57,58,60,61,62,63,64,65,66,67,68,68,69,70,71,71,72,72,73,74,74,74,75,75,75]
[4.1,null,7,12,16,20,24,28,32,35,37,40,43,45,47,49,51,53,54,56,57,59,60,61,62,63,64,65,66,67,68,68,69,70,70,71,72,72,73,73,74,74,75,75]
[4.2,null,5,10,14,19,23,26,30,33,36,39,41,44,46,48,50,52,53,55,56,58,59,60,61,62,63,64,65,66,67,68,69,69,70,70,71,72,72,73,73,74,74,74]
[4.3,null,null,8,12,17,21,25,28,31,35,37,40,42,45,47,49,51,52,54,55,57,58,59,61,62,63,64,65,65,66,67,68,68,69,70,68,71,71,72,72,73,73,74]
[4.4,null,null,6,10,15,19,23,27,30,33,36,39,41,43,46,48,49,51,53,54,56,57,59,60,61,62,63,64,65,66,66,67,68,68,69,70,70,71,71,72,72,73,73]
[4.5,null,null,3,8,13,17,21,25,28,31,35,37,40,42,44,46,48,50,52,53,55,56,58,59,60,61,62,63,64,65,66,66,67,68,68,69,70,70,71,71,72,72,73]
[4.6,null,null,1,7,11,16,20,24,27,30,33,36,39,41,43,45,47,49,51,53,54,55,57,58,59,60,61,62,63,64,65,66,66,67,68,68,69,70,70,71,71,72,72]
[4.7,null,null,null,5,9,14,18,22,25,29,32,35,37,40,42,44,46,48,50,52,53,55,56,57,58,59,61,62,62,63,64,65,66,66,67,68,68,69,70,70,71,71,72]
[4.8,null,null,null,3,8,12,16,20,24,27,30,33,36,39,41,43,45,47,49,51,52,54,55,56,58,59,60,61,62,63,64,64,65,66,67,67,68,68,69,70,70,71,71]
[4.9,{"$nulls":4},6,10,15,19,22,26,29,32,35,37,40,42,44,46,48,50,51,53,54,55,57,58,59,60,61,62,63,63,64,65,66,67,67,68,68,69,69,70,70]
[5,{"$nulls":4},4,9,13,17,21,24,28,31,33,36,39,41,43,45,47,49,50,52,53,55,56,57,58,59,60,61,62,63,64,64,65,66,67,67,68,68,69,69,70]
[5.1,{"$nulls":8},19,23,26,29,32,35,38,40,42,44,46,48,49,51,52,54,55,56,57,59,60,61,61,62,63,64,65,65,66,67,67,68,68,69,69]
[5.2,{"$nulls":8},18,22,25,28,31,34,36,39,41,43,45,47,48,50,52,53,54,56,57,58,59,60,61,62,63,63,64,65,65,66,67,67,68,68,69]
[5.3,{"$nulls":8},17,20,24,27,30,33,35,38,40,42,44,46,48,49,51,52,54,55,56,57,58,59,60,61,62,62,63,64,63,65,66,67,67,68,68]
[5.4,{"$nulls":8},15,19,22,26,29,31,34,37,39,41,43,45,47,48,50,51,53,54,55,56,57,58,59,60,61,62,63,63,64,65,66,66,67,67,68]
[5.5,{"$nulls":8},14,17,21,24,27,30,33,35,38,40,42,44,46,47,49,51,52,53,54,56,57,58,59,60,61,61,62,63,64,64,65,66,66,67,67]
[5.6,{"$nulls":8},12,16,20,23,26,29,32,34,37,39,41,43,45,47,48,50,51,52,54,55,56,57,58,59,60,61,62,62,63,64,64,65,66,66,67]
[5.7,{"$nulls":8},11,15,18,22,25,28,31,33,36,38,40,42,44,46,47,49,50,52,53,54,55,56,57,58,59,60,61,62,62,63,64,64,65,66,66]
[5.8,{"$nulls":8},9,13,17,20,24,27,30,32,35,37,39,41,43,45,47,48,50,51,52,53,55,56,57,58,59,59,60,61,62,63,63,64,64,65,66]
[5.9,{"$nulls":8},8,12,16,19,23,26,29,31,34,36,38,40,42,44,46,47,49,50,51,53,54,55,56,57,58,59,60,60,61,62,63,63,64,65,65]
[6,{"$nulls":8},6,10,14,18,21,24,27,30,33,35,37,39,41,43,45,46,48,49,51,52,53,54,55,56,57,58,59,60,61,61,62,63,63,64,65]
[6.1,{"$nulls":8},5,9,13,17,20,23,26,29,32,34,36,38,40,42,44,46,47,49,50,51,52,54,55,56,57,57,58,59,60,61,62,62,63,63,64]
[6.2,{"$nulls":8},3,8,12,15,19,22,25,28,31,33,35,38,40,41,43,45,46,48,49,51,52,53,54,55,56,57,58,59,59,60,61,62,62,63,64]
[6.3,{"$nulls":8},2,6,10,14,18,21,24,27,30,32,34,37,39,41,42,44,46,47,49,50,51,52,53,54,55,56,57,58,59,58,60,61,62,62,63]
[6.4,{"$nulls":9},5,9,13,17,20,23,26,29,31,33,36,38,40,42,43,45,46,48,49,50,52,53,54,55,56,57,58,58,59,60,61,61,62,62]
[6.5,{"$nulls":9},4,8,12,15,19,22,25,28,30,33,35,37,39,41,42,44,46,47,48,50,51,52,53,54,55,56,57,58,59,59,60,61,61,62]
[6.6,{"$nulls":9},2,6,10,14,18,21,24,27,29,32,34,36,38,40,42,43,45,46,48,49,50,51,52,54,54,55,56,57,58,59,59,60,61,61]
[6.7,{"$nulls":10},5,9,13,16,20,23,26,28,31,33,35,37,39,41,43,44,46,47,48,50,51,52,53,54,55,56,57,57,58,59,60,60,61]
[6.8,{"$nulls":10},4,8,11,15,19,22,25,27,30,32,34,36,38,40,42,43,45,46,48,49,50,51,52,53,54,55,56,57,58,58,59,60,60]
[6.9,{"$nulls":10},3,7,11,14,17,21,24,26,29,31,33,35,37,39,41,43,44,46,47,48,49,51,52,52,54,55,55,56,57,58,59,59,60]
[7,{"$nulls":11},5,9,13,16,20,23,25,28,30,33,35,37,38,40,42,43,45,46,48,49,50,51,52,53,54,55,56,57,57,58,59,59]
[7.1,{"$nulls":11},4,8,12,15,19,22,24,27,29,32,34,36,38,39,41,43,44,46,47,48,49,50,51,52,53,54,55,56,57,58,58,59]
[7.2,{"$nulls":11},3,7,11,14,17,21,23,26,28,31,33,35,37,39,40,42,44,45,46,48,49,50,51,52,53,54,55,55,56,57,58,58]
[7.3,{"$nulls":11},2,6,10,13,16,20,22,25,28,30,32,34,36,38,40,41,43,44,46,47,48,49,50,51,52,53,54,53,56,56,57,58]
[7.4,{"$nulls":12},5,8,12,15,19,21,24,27,29,31,33,35,37,39,41,42,44,45,46,47,49,50,51,52,53,54,54,55,56,57,57]
[7.5,{"$nulls":12},3,7,11,14,18,20,23,26,28,30,33,35,36,38,40,41,43,44,46,47,48,49,50,51,52,53,54,55,55,56,57]
[7.6,{"$nulls":12},2,6,10,13,17,20,22,25,27,30,32,34,36,38,39,41,42,44,45,46,47,48,50,51,52,52,53,54,55,56,56]
[7.7,{"$nulls":13},5,9,12,16,19,21,24,27,29,31,33,35,37,38,40,42,43,44,46,47,48,49,50,51,52,53,54,54,55,56]
[7.8,{"$nulls":13},4,8,11,15,18,21,23,26,28,30,32,34,36,38,39,41,42,44,45,46,47,48,49,50,51,52,53,54,55,55]
[7.9,{"$nulls":13},3,7,10,14,17,20,22,25,27,29,32,34,35,37,39,40,42,43,44,46,47,48,49,50,51,52,53,53,54,55]
[8,{"$nulls":14},6,9,13,16,19,21,24,26,29,31,33,35,36,38,40,41,42,44,45,46,47,48,49,50,51,52,53,54,54]
[8.1,{"$nulls":14},5,8,12,15,18,21,23,26,28,30,32,34,36,37,39,40,42,43,44,45,47,48,49,50,51,52,52,53,54]
[8.2,{"$nulls":14},4,7,11,14,17,20,22,25,27,29,31,33,35,37,38,40,41,43,44,45,46,47,48,49,50,51,52,53,53]
[8.3,{"$nulls":14},3,6,10,13,16,19,22,24,26,29,31,33,34,36,38,39,41,42,43,44,46,47,48,49,50,49,51,52,53]
[8.4,{"$nulls":15},5,9,12,15,18,21,23,26,28,30,32,34,35,37,39,40,41,43,44,45,46,47,48,49,50,51,52,53]
[8.5,{"$nulls":15},4,8,11,14,17,20,22,25,27,29,31,33,35,36,38,39,41,42,43,44,46,47,48,49,50,50,51,52]
[8.6,{"$nulls":15},3,7,10,13,16,19,22,24,26,28,30,32,34,36,37,39,40,41,43,44,45,46,47,48,49,50,51,52]
[8.7,{"$nulls":15},2,6,9,12,15,18,21,23,26,28,30,32,33,35,37,38,40,41,42,43,45,46,47,48,49,49,50,51]
[8.8,{"$nulls":16},5,8,12,15,17,20,22,25,27,29,31,33,34,36,38,39,40,42,43,44,45,46,47,48,49,50,51]
[8.9,{"$nulls":16},4,7,11,14,17,19,22,24,26,28,30,32,34,35,37,38,40,41,42,43,45,46,47,48,48,49,50]
[9,{"$nulls":16},3,7,10,13,16,18,21,23,26,28,30,31,33,35,36,38,39,40,42,43,44,45,46,47,48,49,50]
[9.1,{"$nulls":17},6,9,12,15,18,20,23,25,27,29,31,33,34,36,37,39,40,41,42,43,45,46,47,47,48,49]
[9.2,{"$nulls":17},5,8,11,14,17,19,22,24,26,28,30,32,34,35,37,38,39,41,42,43,44,45,46,47,48,49]
[9.3,{"$nulls":17},4,7,10,13,16,19,21,23,26,28,29,31,33,35,36,37,39,40,41,42,44,45,46,45,47,48]
[9.4,{"$nulls":17},3,6,10,12,15,18,20,23,25,27,29,31,32,34,36,37,38,40,41,42,43,44,45,46,47,48]
[9.5,{"$nulls":17},2,5,9,12,15,17,20,22,24,26,28,30,32,33,35,36,38,39,40,41,43,44,45,46,46,47]
[9.6,{"$nulls":18},5,8,11,14,16,19,21,24,26,28,29,31,33,34,36,37,38,40,41,42,43,44,45,46,47]
[9.7,{"$nulls":18},4,7,10,13,16,18,21,23,25,27,29,31,32,34,35,37,38,39,40,42,43,44,45,46,46]
[9.8,{"$nulls":18},3,6,9,12,15,17,20,22,24,26,28,30,32,33,35,36,37,39,40,41,42,43,44,45,46]
[9.9,{"$nulls":19},5,8,11,14,17,19,21,24,26,28,29,31,33,34,35,37,38,39,41,42,43,44,45,45]
[10,{"$nulls":19},5,8,11,13,16,19,21,23,25,27,29,30,32,34,35,36,38,39,40,41,42,43,44,45]
[10.1,{"$nulls":20},7,10,13,15,18,20,22,24,26,28,30,31,33,34,36,37,38,40,41,42,43,44,45]
[10.2,{"$nulls":20},6,9,12,15,17,19,22,24,26,28,29,31,32,34,35,37,38,39,40,41,42,43,44]
[10.3,{"$nulls":20},5,8,11,14,16,19,21,23,25,27,29,30,32,33,35,36,37,39,40,41,42,41,44]
[10.4,{"$nulls":20},5,8,11,13,16,18,20,22,24,26,28,30,31,33,34,36,37,38,39,40,41,42,43]
[10.5,{"$nulls":20},4,7,10,13,15,17,20,22,24,26,28,29,31,32,34,35,36,38,39,40,41,42,43]
[10.6,{"$nulls":20},3,6,9,12,14,17,19,21,23,25,27,29,30,32,33,35,36,37,38,39,40,41,42]
[10.7,{"$nulls":21},5,8,11,14,16,18,21,23,25,26,28,30,31,33,34,35,37,38,39,40,41,42]
[10.8,{"$nulls":21},5,8,10,13,16,18,20,22,24,26,28,29,31,32,34,35,36,37,38,39,41,41]
[10.9,{"$nulls":21},4,7,10,12,15,17,19,21,23,25,27,29,30,32,33,34,35,37,38,39,40,41]
[11,{"$nulls":21},3,6,9,12,14,17,19,21,23,25,26,28,30,31,33,34,35,36,37,39,40,41]
[11.1,{"$nulls":22},5,8,11,14,16,18,20,22,24,26,28,29,31,32,33,35,36,37,38,39,40]
[11.2,{"$nulls":22},5,8,10,13,15,18,20,22,24,25,27,29,30,31,33,34,36,37,38,39,40]
[11.3,{"$nulls":22},4,7,10,12,15,17,19,21,23,25,27,28,30,31,32,34,35,36,37,38,38]
[11.4,{"$nulls":22},3,6,9,12,14,16,19,21,22,24,26,28,29,31,32,33,34,36,37,38,39]
[11.5,{"$nulls":22},3,6,8,11,13,16,18,20,22,24,25,27,29,30,31,33,34,35,36,37,38]
[11.6,{"$nulls":23},5,8,10,13,15,17,19,21,23,25,27,28,30,31,32,34,35,36,37,38]
[11.7,{"$nulls":23},4,7,10,12,15,17,19,21,23,24,26,28,29,31,32,33,34,35,37,38]
[11.8,{"$nulls":23},4,6,9,12,14,16,18,20,22,24,25,27,29,30,31,33,34,35,36,37]
[11.9,{"$nulls":23},3,6,8,11,13,16,18,20,22,23,25,27,28,30,31,32,33,35,36,37]
[12,{"$nulls":23},2,5,8,10,13,15,17,19,21,23,24,26,28,29,30,32,33,34,35,36]
[12.1,{"$nulls":24},4,7,10,12,14,17,19,21,22,24,26,27,29,30,31,33,34,35,36]
[12.2,{"$nulls":24},4,7,9,12,14,16,18,20,22,23,25,27,28,30,31,32,33,34,35]
[12.3,{"$nulls":24},3,6,9,11,13,15,18,19,21,23,25,26,28,29,30,32,33,34,35]
[12.4,{"$nulls":24},2,5,8,10,13,15,17,19,21,22,24,26,27,29,30,31,32,34,35]
[12.5,{"$nulls":24},2,5,7,10,12,14,16,18,20,22,24,25,27,28,30,31,32,33,34]
[12.6,{"$nulls":25},4,7,9,12,14,16,18,20,21,23,25,26,28,29,30,32,33,34]
[12.7,{"$nulls":25},3,6,9,11,13,15,17,19,21,23,24,26,27,29,30,31,32,33]