{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Лист1"],"not_rendered":{"charts":1,"images":0,"macros":0,"external_links":1,"defined_names":1,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Лист1","index":0,"n_rows":52,"n_cols":20,"rows_kept":52,"cut":false,"hidden":false,"merged":[[11,11,11,12],[1,1,1,14],[15,19,18,19],[1,16,1,19],[3,19,14,19]],"flags":["formulas_cached_only"]}
[]
[null,"Температурный режим",{"$nulls":14},"Исходные данные"]
[null,"Т н. возд","φ"," Т1п","Т1"," Т2",{"$nulls":8},"U",null,"Наименование","Обозн","Знач"]
[null,8,0.23529411764705882,70,42.58241515469956,36.70006221352309,{"$nulls":8},4.660989423701074,null,"Температура наружного воздуха начала/конца",null,8,"                             вводится"]
[null,7,0.2549019607843137,70,44.12636520301935,37.7538161834115,{"$nulls":8},4.060170383526193,null,"Расчётная температура наружного воздуха","Тнр",-31]
[null,6,0.27450980392156865,70,45.65046443714618,38.78771933910696,{"$nulls":8},3.548075182015841,null,"Расчётная температура внутреннего воздуха","Твр",20]
[null,5,0.29411764705882354,70,47.1564052313886,39.80346405491801,{"$nulls":8},3.1067288885311513,null,"Расчётная температура в подающем тр-де теплосети","Т1п",150]
[null,4,0.3137254901960784,70,48.645632824826734,40.80249556992477,{"$nulls":8},2.722681814834591,null,"Расчётная температура в подающем тр-де отопления","Т1р",95]
[null,3,0.3333333333333333,70,50.11939457532327,41.78606124198994,{"$nulls":8},2.385672650961209,null,"Расчётная температура в обратном тр-де отопления","Т2р",70]
[null,2,0.35294117647058826,70.99054178464473,51.57877707876238,42.755247666997676,{"$nulls":8},2.200000000000001,null,"Относительная поверхность нагрева","f",1]
[null,1,0.37254901960784315,73.51493072993571,53.02473465150433,43.711009161308255,{"$nulls":8},2.200000000000001,null,"Относительный расход теплоносителя","g",1]
[null,0,0.39215686274509803,76.02673898545619,54.4581115344758,44.654189965848346,"Средн тем-ра воды в т/сети","Тем-pа воды до котла",null,null,"Тем-pа воды за котлом","Диапазон",null,"Степень отк клап",2.2,null,"Инфильтрация","i",0]
[null,-1,0.4117647058823529,78.5267182710303,55.87965944750089,45.58554180044207,39.64123868411133,60,60.05882352941177,2.9757894237010745,60.08705882352941,57.08705882352941,63.08705882352941,25.152237541521927,2.200000000000001,null,"Относительные внутренние тепловыделения","w",0]
[null,-2,0.43137254901960786,81.01554183862702,57.29005164254858,46.50573791705838,40.940090693215424,60,60.06372549019608,2.5057396142954245,60.094313725490196,57.094313725490196,63.094313725490196,28.52465128677213,2.1999999999999993,null,"Константа (0,25; 0,32)","n",0.25]
[null,-3,0.45098039215686275,83.49381585010488,58.689894281477436,47.41538447755586,42.21909188812657,60,60.068627450980394,2.1057323248729847,60.10156862745098,57.10156862745098,63.10156862745098,32.19852503035325,2.1999999999999984,null,"Нижняя температурная срезка в подающем трубопроводе","Тсрез",70]
[null,-4,0.47058823529411764,85.9620886829264,60.07973574174994,48.315029859397,43.4799346431533,60,60.0735294117647,1.7615288885311513,60.108823529411765,57.108823529411765,63.108823529411765,36.2118246943959,2.1999999999999993,null,"Расчётная разность температур наружного воздуха",null,51,"вычисляется"]
[null,-5,0.49019607843137253,88.42085861172848,61.46007429800299,49.205172337218684,44.72406419737575,60,60.07843137254902,1.4624818148345915,60.11607843137255,57.11607843137255,63.11607843137255,40.609436949980946,2.2,null,"Расчётная разность температур теплоносителя отопления",null,25]
[null,-6,0.5098039215686274,90.87058020278357,62.83136451650906,50.08626647729338,45.952727908656605,60,60.083333333333336,1.2004726509612085,60.123333333333335,57.123333333333335,63.123333333333335,45.4447820364039,2.2000000000000006,null,"Температурный напор в отопительном приборе","Ө",62.5]
[null,-7,0.5294117647058824,93.31166967817904,64.19402261935551,50.95872850170845,47.16701237288002,60,60.088235294117645,0.969205264406931,60.13058823529412,57.13058823529412,63.13058823529412,50.78190771042711,2.2000000000000006,null,"Расчётный коэффициент смешения","U",2.2]
[null,-8,0.5490196078431373,95.74450944768562,65.54843101631306,51.822940820234635,48.36787190640629,60,60.09313725490196,0.7637232268911142,60.137843137254904,57.137843137254904,63.137843137254904,56.69823840573237,2.2000000000000015]
[null,-9,0.5686274509803921,98.16945196253847,66.89494215861691,52.6792558841071,49.556150750162075,60,60.09803921568628,0.5800726234834689,60.14509803921569,57.14509803921569,63.14509803921569,63.288230245732265,2.199999999999998]
[null,-10,0.5882352941176471,100.58682301244775,68.23388183597716,53.527999483035984,50.73260062397148,60,60.10294117647059,0.41506165367134246,60.152352941176474,57.152352941176474,63.152352941176474,70.66829896814211,2.2000000000000006]
[null,-11,0.6078431372549019,102.99692456213376,69.56555201311414,54.3694735817416,51.89789477980348,60,60.1078431372549,0.2660861204182219,60.15960784313725,57.15960784313725,63.15960784313725,78.98356864299826,2.2000000000000015]
[null,-12,0.6274509803921569,105.40003720446059,70.89023328289196,55.20395877308804,53.05263937951665,60,60.11274509803921,0.13100068112113147,60.16686274509804,57.16686274509804,63.16686274509804,88.41727654918175,2.200000000000001]
[null,-13,0.6470588235294118,107.79642229233804,72.2081869982204,56.0317164099851,54.19738280057347,60,60.11764705882353,0.008022461951254698,60.17411764705882,57.17411764705882,63.17411764705882,99.20413857289196,2.199999999999999]
[null,-14,0.6666666666666666,110.1863237999041,73.51965713323743,56.852990466570766,55.33262331761084,60,60.122549019607845,-0.10434206271704444,60.181372549019606,57.181372549019606,63.181372549019606,111.64976698956902,2.2000000000000006]
[null,-15,0.6862745098039216,112.56996995430649,74.82487191509081,57.66800916999277,56.458815496901224,50.08626647729338,50.21371745768553,{"$error":"#REF!"},{"$error":"#REF!"},{"$error":"#REF!"},{"$error":"#REF!"},{"$error":"#REF!"},2.1999999999999993]
[null,-16,0.7058823529411765,114.94757467209638,76.12404526033166,58.47698643680225,57.57637556053198,50.95872850170845,51.09108144288492,{"$error":"#REF!"},{"$error":"#REF!"},{"$error":"#REF!"},{"$error":"#REF!"},{"$error":"#REF!"},2.200000000000002]
[null,-17,0.7254901960784313,117.31933882840056,77.41737804408683,59.280123142126044,58.68568591827385,51.822940820234635,51.96019572219542,{"$error":"#REF!"},{"$error":"#REF!"},{"$error":"#REF!"},{"$error":"#REF!"},{"$error":"#REF!"},2.1999999999999997]
[null,-18,0.7450980392156863,119.68545138232741,78.70505922546467,60.07760824507251,59.78709902136201,52.6792558841071,52.8214127468522,{"$error":"#REF!"},{"$error":"#REF!"},{"$error":"#REF!"},{"$error":"#REF!"},{"$error":"#REF!"},2.2000000000000006]
[null,-19,0.7647058823529411,122.0460903782414,79.98726684882962,60.8696197900061,60.88094065950657,53.527999483035984,53.6750583065654,{"$error":"#REF!"},{"$error":"#REF!"},{"$error":"#REF!"},{"$error":"#REF!"},{"$error":"#REF!"},2.200000000000002]
[null,-20,0.7843137254901961,124.40142383942575,81.26416893746496,61.656325800210055,61.96751279742787,54.3694735817416,54.521434366055324,{"$error":"#REF!"},{"$error":"#REF!"},{"$error":"#REF!"},{"$error":"#REF!"},{"$error":"#REF!"},2.2]
[null,-21,0.803921568627451,126.75161056809662,82.53592429358682,62.43788507790054,63.047096027989994,55.20395877308804,55.36082151818608,{"$error":"#REF!"},{"$error":"#REF!"},{"$error":"#REF!"},{"$error":"#REF!"},{"$error":"#REF!"},2.1999999999999997]
[null,-22,0.8235294117647058,129.09680086362403,83.8026832165652,63.214447922447555,{"$nulls":8},2.2]
[null,-23,0.8431372549019608,131.4371371690681,85.06458814946026,63.986156776911244,{"$nulls":8},2.2]
[null,-24,0.8627450980392157,133.77275465468392,86.32177426252704,64.75314681154666,{"$nulls":8},2.2000000000000015]
[null,-25,0.8823529411764706,136.10378174583084,87.57436998112496,65.51554645171319,{"$nulls":8},2.1999999999999997]
[null,-26,0.9019607843137255,138.4303406017002,88.82249746444532,66.27347785660218,{"$nulls":8},2.1999999999999997]
[null,-27,0.9215686274509803,140.75254755041058,90.06627304060666,67.02705735433216,{"$nulls":8},2.2000000000000006]
[null,-28,0.9411764705882353,143.07051348529075,91.30580760293779,67.7763958382319,{"$nulls":8},2.2000000000000006]
[null,-29,0.9607843137254902,145.38434422654765,92.54120697164569,68.52159912850844,{"$nulls":8},2.2]
[null,-30,0.9803921568627451,147.69414085198707,93.77257222453609,69.26276830296746,{"$nulls":8},2.1999999999999997]
[null,-31,1,150,95,70,{"$nulls":8},2.2]
[null,-32]
[null,-33]
[null,-34]
[null,-35]
[null,-36]
[null,-37]
[null,-38]
[null,-39]
[null,-40]