{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Расчёт теплопотерь БК"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":0,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Расчёт теплопотерь БК","index":0,"n_rows":15,"n_cols":17,"rows_kept":15,"cut":false,"hidden":false,"merged":[[67,16,68,16],[69,0,69,15],[70,0,70,15],[67,0,68,0],[67,1,68,1],[67,2,68,2],[67,14,68,14],[60,2,62,2],[60,14,62,14],[60,16,62,16],[63,0,66,0],[63,1,66,1],[63,2,66,2],[63,14,66,14],[63,16,66,16],[60,0,62,0],[60,1,62,1],[15,2,18,2],[57,0,59,0],[57,1,59,1],[57,2,59,2],[56,0,56,16],[57,14,59,14],[57,16,59,16],[19,14,24,14],[40,0,40,16],[15,14,18,14],[19,16,24,16],[19,0,24,0],[19,1,24,1],[19,2,24,2],[15,16,18,16],[15,0,18,0],[15,1,18,1],[0,0,1,0],[0,1,1,1],[0,2,1,2],[2,0,2,16],[0,15,1,15],[0,16,1,16],[0,10,0,12],[0,14,1,14],[0,13,1,13],[3,14,14,14],[0,6,1,6],[0,3,0,5],[0,8,1,8],[0,9,1,9],[0,7,1,7],[7,17,7,21],[3,0,14,0],[3,1,14,1],[3,2,14,2],[3,16,14,16],[51,16,54,16],[55,0,55,15],[51,0,54,0],[51,1,54,1],[51,2,54,2],[51,14,54,14],[49,1,50,1],[49,2,50,2],[49,14,50,14],[49,16,50,16],[25,2,29,2],[25,14,29,14],[46,0,48,0],[46,1,48,1],[46,2,48,2],[46,14,48,14],[25,0,29,0],[25,1,29,1],[46,16,48,16],[49,0,50,0],[25,16,29,16],[34,16,38,16],[39,0,39,15],[41,0,44,0],[41,1,44,1],[41,2,44,2],[41,14,44,14],[41,16,44,16],[30,16,33,16],[34,0,38,0],[34,1,38,1],[34,2,38,2],[34,14,38,14],[30,0,33,0],[30,1,33,1],[30,2,33,2],[30,14,33,14],[74,0,75,0],[74,1,75,1],[74,2,75,2],[74,3,74,5],[74,6,75,6],[74,7,75,7],[74,8,75,8],[74,9,75,9],[74,10,74,12],[74,13,75,13],[74,14,75,14],[74,15,75,15],[74,16,75,16],[76,0,76,16],[77,0,84,0],[77,1,84,1],[77,2,84,2],[77,14,82,14],[77,16,84,16],[83,3,84,13],[83,14,84,14],[83,15,84,15],[85,16,88,16],[89,0,94,0],[89,1,94,1],[89,2,94,2],[89,14,94,14],[89,16,94,16],[85,0,88,0],[85,1,88,1],[85,2,88,2],[85,14,88,14],[95,16,99,16],[100,0,103,0],[100,1,103,1],[100,2,103,2],[100,14,103,14],[100,16,103,16],[95,0,99,0],[95,1,99,1],[95,2,99,2],[95,14,99,14],[104,0,108,0],[104,1,108,1],[104,2,108,2],[104,14,108,14],[116,2,118,2],[116,14,118,14],[104,16,108,16],[109,0,109,15],[110,0,110,16],[111,0,114,0],[111,1,114,1],[111,2,114,2],[111,14,114,14],[111,16,114,16],[121,2,124,2],[121,14,124,14],[116,16,118,16],[119,0,120,0],[119,1,120,1],[119,2,120,2],[119,14,120,14],[119,16,120,16],[116,0,118,0],[116,1,118,1],[121,16,124,16],[125,0,125,15],[126,0,126,16],[127,0,129,0],[127,1,129,1],[127,2,129,2],[127,14,129,14],[127,16,129,16],[121,0,124,0],[121,1,124,1],[130,0,132,0],[130,1,132,1],[130,2,132,2],[130,14,132,14],[133,1,136,1],[133,2,136,2],[133,14,136,14],[133,16,136,16],[137,16,138,16],[139,0,139,15],[140,0,140,15],[73,0,73,16],[137,0,138,0],[137,1,138,1],[137,2,138,2],[137,14,138,14],[130,16,132,16],[133,0,136,0],[142,0,142,16],[143,0,144,0],[143,1,144,1],[143,2,144,2],[143,3,143,5],[143,6,144,6],[143,7,144,7],[143,8,144,8],[143,9,144,9],[143,10,143,12],[143,13,144,13],[143,14,144,14],[143,15,144,15],[143,16,144,16],[145,0,145,16],[146,0,153,0],[146,1,153,1],[146,2,153,2],[146,14,151,14],[146,16,153,16],[152,3,153,13],[152,14,153,14],[152,15,153,15],[154,16,157,16],[158,0,163,0],[158,1,163,1],[158,2,163,2],[158,14,163,14],[158,16,163,16],[154,0,157,0],[154,1,157,1],[154,2,157,2],[154,14,157,14],[164,16,168,16],[169,0,172,0],[169,1,172,1],[169,2,172,2],[169,14,172,14],[169,16,172,16],[164,0,168,0],[164,1,168,1],[164,2,168,2],[164,14,168,14],[173,0,177,0],[173,1,177,1],[173,2,177,2],[173,14,177,14],[185,2,187,2],[185,14,187,14],[173,16,177,16],[178,0,178,15],[179,0,179,16],[180,0,183,0],[180,1,183,1],[180,2,183,2],[180,14,183,14],[180,16,183,16],[190,2,193,2],[190,14,193,14],[185,16,187,16],[188,0,189,0],[188,1,189,1],[188,2,189,2],[188,14,189,14],[188,16,189,16],[185,0,187,0],[185,1,187,1],[190,16,193,16],[194,0,194,15],[195,0,195,16],[196,0,198,0],[196,1,198,1],[196,2,198,2],[196,14,198,14],[196,16,198,16],[190,0,193,0],[190,1,193,1],[202,16,205,16],[199,0,201,0],[199,1,201,1],[199,2,201,2],[199,14,201,14],[71,0,72,16],[206,0,207,0],[206,1,207,1],[206,2,207,2],[206,14,207,14],[199,16,201,16],[202,0,205,0],[202,1,205,1],[202,2,205,2],[202,14,205,14],[210,0,210,15],[206,16,207,16],[208,0,208,15],[209,0,209,15]],"flags":["formulas_cached_only"]}
["№ п/п","Наименование помещения","Температура воздуха внутри помещения, оС","Тип ограждения",null,null,"Коэффициент теплопередачи k, Вт/(м2·К)","Расчётная разность температур(tв-tн), оС","Поправочный коэффициент к расчётной разности температур n","Основные теплопотери Qосн, Вт","Добавочные теплопотери учитывающие",null,null,"Добавочный множитель","Потери теплоты на инфильтрацию,Вт","Общие теплопотери Q,Вт","Сумма"]
[null,null,null,"Наименование","Ориентация по сторонам горизонта","Площадь ограждения, м2",{"$nulls":4},"ориентацию ограждения","на наличие 2 и более наружных стен","наличие входных наружных дверей"]
["Помещения первого этажа (25% инф)"]
["129","Склад антисептиков",16,"Пл1","-",100,0.476,42,1,1999.1999999999998,0,0,0,1,4021.1949749999994,1999.1999999999998,22469.674815]
[null,null,null,"Пл2","-",100,0.233,42,1,978.6000000000001,0,0,0,1,null,978.6000000000001]
[null,null,null,"Пл3","-",100,0.116,42,1,487.2,0,0,0,1,null,487.2]
[null,null,null,"Пл4","-",320.3,0.07,42,1,941.6820000000001,0,0,0,1,null,941.6820000000001]
[null,null,null,"Нс3","В",9,0.201,42,1,75.97800000000001,0.1,0.05,0,1.1500000000000001,null,87.37470000000002]
[null,null,null,"Нс2","В",270,0.231,42,1,2619.54,0.1,0.05,0,1.1500000000000001,null,3012.4710000000005]
[null,null,null,"ДО","В",18,1.82,42,1,1375.92,0.1,0.05,0,1.1500000000000001,null,1582.3080000000002]
[null,null,null,"Нс3","З",5.3999999999999995,0.201,42,1,45.5868,0.05,0.05,0,1.1,null,50.14548]
[null,null,null,"Нс2","З",181.79999999999998,0.231,42,1,1763.8235999999997,0.05,0.05,0,1.1,null,1940.2059599999998]
[null,null,null,"ДО","З",10.8,1.82,42,1,825.552,0.05,0.05,0,1.1,null,908.1072000000001]
[null,null,null,"НД ","З",8,1.43,42,1,480.47999999999996,0.05,0.05,3,4.1,null,1969.9679999999996]
[null,null,null,"Пт","-",611.05,0.175,42,1,4491.2175,0,0,0,1,null,4491.2175]