{"text_format":"2","workbook":"xlsx","n_sheets":3,"sheets":["Лист1","Лист2","Лист3"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":0,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Лист1","index":0,"n_rows":103,"n_cols":13,"rows_kept":103,"cut":false,"hidden":false,"merged":[]}
["Ст. №6"]
[{"$nulls":8},"Потеря напора"]
[null,"№ участа","тепловая нагрузка на участке, Вт","Расход, кг/ч","Расход, м3/ч","Длина, м","Диаметр трубопровода ,мм","Скорость, м/с","на 1 м трубопровода","На участке","коэффицент местного сопротивления","Потери на сопротивлении, Па","Общие, Па"]
[null,1,26160,{"$f":"(3.6*C4)/(4.187*25)","v":899.69906854549788},{"$f":"D4/971.8","v":0.92580682089472932},9.9,40,0.21,{"$f":"J4/F4","v":14.447474747474747},143.03,2,{"$f":"(((H4^2)/(2*9.81))*971.8*K4)*9.81","v":42.856379999999987},{"$f":"L4+J4","v":185.88637999999997}]
[null,2,26160,{"$f":"(3.6*C5)/(4.187*25)","v":899.69906854549788},{"$f":"D5/971.8","v":0.92580682089472932},1.7,40,0.21,{"$f":"J5/F5","v":14.447058823529412},24.56,1,{"$f":"(((H5^2)/(2*9.81))*971.8*K5)*9.81","v":21.428189999999994},{"$f":"L5+J5","v":45.988189999999989}]
[null,3,19170,659.29782660616183,0.67842953962354591,14.2,40,0.15,{"$f":"J6/F6","v":8.183098591549296},116.2,1,{"$f":"(((H6^2)/(2*9.81))*971.8*K6)*9.81","v":10.932749999999999},127.13275]
[null,4,15280,525.51229997611654,0.5407617822351477,8.9600000000000009,40,0.12,5.3995535714285712,48.38,1,6.9969599999999987,55.376960000000004]
[null,5,11706,402.59469787437303,0.41427731824899472,5.35,40,0.09,0.44859813084112149,2.4,1,3.9357899999999995,6.3357899999999994]
[null,6,7612,261.79316933365175,0.26938996638572932,11.68,40,0.06,0.21575342465753425,2.52,2,3.4984799999999994,6.0184799999999994]
[null,7,4726,162.53737759732505,0.16725393866775576,6,40,3.6999999999999998E-2,9.6666666666666665E-2,0.57999999999999996,3,1.9955912999999996,2.5755912999999997]
[null,8,4726,162.53737759732505,0.16725393866775576,2.75,20,0.15,19.461818181818185,53.52,2,21.865499999999997,75.385500000000008]
[null,"8'",4726,162.53737759732505,0.16725393866775576,0.36,20,0.15,19.472222222222221,7.01,7.5,81.99562499999999,89.005624999999995]
[null,9,4726,162.53737759732505,0.16725393866775576,3.22,20,0.15,19.462732919254659,62.67,5,54.663749999999993,117.33374999999999]
[null,"9'",4726,162.53737759732505,0.16725393866775576,0.8,20,0.15,19.462499999999999,15.57,3,32.798249999999996,48.368249999999996]
[null,10,4726,162.53737759732505,0.16725393866775576,6,40,0.04,9.6666666666666665E-2,0.57999999999999996,1.5,1.1661600000000001,1.7461600000000002]
[null,11,7612,261.79316933365175,0.26938996638572932,8.18,40,0.06,0.21515892420537899,1.76,1.5,2.6238599999999996,4.3838599999999994]
[null,12,11706,402.59469787437303,0.41427731824899472,5.2,40,0.09,0.44807692307692309,2.33,1.5,5.9036849999999985,8.2336849999999977]
[null,13,15280,525.51229997611654,0.5407617822351477,8.9600000000000009,40,0.12,5.3995535714285712,48.38,1.5,10.495439999999999,58.875439999999998]
[null,14,19170,659.29782660616183,0.67842953962354591,9.7799999999999994,40,0.15,8.1830265848670756,80.03,1.5,16.399124999999998,96.429124999999999]
[null,"14'",26160,899.69906854549788,0.92580682089472932,6.7,40,0.21,14.44776119402985,96.8,2,42.856379999999987,139.65637999999998]
[null,null,null,0,0,{"$f":"SUM(F4:F20)","v":109.74},null,null,0,null,null,0,0]
[{"$nulls":9},{"$f":"SUM(J4:J21)","v":706.31999999999982},null,{"$f":"SUM(L4:L21)","v":362.41191629999986},{"$f":"SUM(M4:M21)","v":1068.7319163}]
[]
[]
["Ст №5",{"$nulls":7},"Потеря напора"]
[null,"№ участа","тепловая нагрузка на участке, Вт","Расход, кг/ч","Расход, м3/ч","Длина, м","Диаметр трубопровода ,мм","Скорость, м/с","на 1 м трубопровода","На участке","коэффицент местного сопротивления","Потери на сопротивлении, Па","Общие, Па"]
[null,1,26160,{"$f":"(3.6*C27)/(4.187*25)","v":899.69906854549788},{"$f":"D27/971.8","v":0.92580682089472932},9.9,40,0.21,{"$f":"J27/F27","v":14.447474747474747},143.03,2,{"$f":"(((H27^2)/(2*9.81))*971.8*K27)*9.81","v":42.856379999999987},{"$f":"L27+J27","v":185.88637999999997}]
[null,2,26160,{"$f":"(3.6*C28)/(4.187*25)","v":899.69906854549788},{"$f":"D28/971.8","v":0.92580682089472932},1.7,40,0.21,{"$f":"J28/F28","v":14.447058823529412},24.56,1,{"$f":"(((H28^2)/(2*9.81))*971.8*K28)*9.81","v":21.428189999999994},{"$f":"L28+J28","v":45.988189999999989}]
[null,3,19170,659.29782660616183,0.67842953962354591,14.2,40,0.15,{"$f":"J29/F29","v":8.183098591549296},116.2,1,{"$f":"(((H29^2)/(2*9.81))*971.8*K29)*9.81","v":10.932749999999999},127.13275]
[null,4,15280,525.51229997611654,0.5407617822351477,8.9600000000000009,40,0.12,5.3995535714285712,48.38,1,{"$f":"(((H30^2)/(2*9.81))*971.8*K30)*9.81","v":6.9969599999999987},55.376960000000004]
[null,5,11706,402.59469787437303,0.41427731824899472,5.35,40,0.09,0.44859813084112149,2.4,1,3.9357899999999995,6.3357899999999994]
[null,6,7612,261.79316933365175,0.26938996638572932,11.68,40,0.06,0.21575342465753425,2.52,3,5.2477199999999993,7.7677199999999988]
[null,15,2906,99.943635060902793,0.10284383109786252,3.27,15,0.16,30.23547400611621,98.87,5.5,68.414720000000003,167.28471999999999]
[null,16,2906,99.943635060902793,0.10284383109786252,3.11,15,0.16,30.237942122186499,94.04,7.5,93.2928,187.33280000000002]
[null,17,2906,99.943635060902793,0.10284383109786252,0.8,15,0.16,30.237500000000001,24.19,3,37.317120000000003,61.50712]
[null,11,7612,261.79316933365175,0.26938996638572932,8.18,40,0.06,0.21515892420537899,1.76,1.5,2.6238599999999996,4.3838599999999994]
[null,12,11706,402.59469787437303,0.41427731824899472,5.2,40,0.09,0.44807692307692309,2.33,1.5,5.9036849999999985,8.2336849999999977]
[null,13,15280,525.51229997611654,0.5407617822351477,8.9600000000000009,40,0.12,5.3995535714285712,48.38,1.5,10.495439999999999,58.875439999999998]
[null,14,19170,659.29782660616183,0.67842953962354591,9.7799999999999994,40,0.15,8.1830265848670756,80.03,1.5,16.399124999999998,96.429124999999999]
[null,"14'",26160,899.69906854549788,0.92580682089472932,6.7,40,0.21,14.44776119402985,96.8,2,42.856379999999987,139.65637999999998]
[{"$nulls":12},{"$f":"SUM(M27:M40)","v":1152.19092}]
[]
["Ст №4",{"$nulls":7},"Потеря напора"]
[null,"№ участа","тепловая нагрузка на участке, Вт","Расход, кг/ч","Расход, м3/ч","Длина, м","Диаметр трубопровода ,мм","Скорость, м/с","на 1 м трубопровода","На участке","коэффицент местного сопротивления","Потери на сопротивлении, Па","Общие, Па"]
[null,1,26160,{"$f":"(3.6*C45)/(4.187*25)","v":899.69906854549788},{"$f":"D45/971.8","v":0.92580682089472932},9.9,40,0.21,{"$f":"J45/F45","v":14.447474747474747},143.03,2,{"$f":"(((H45^2)/(2*9.81))*971.8*K45)*9.81","v":42.856379999999987},{"$f":"L45+J45","v":185.88637999999997}]
[null,2,26160,{"$f":"(3.6*C46)/(4.187*25)","v":899.69906854549788},{"$f":"D46/971.8","v":0.92580682089472932},1.7,40,0.21,{"$f":"J46/F46","v":14.447058823529412},24.56,1,{"$f":"(((H46^2)/(2*9.81))*971.8*K46)*9.81","v":21.428189999999994},{"$f":"L46+J46","v":45.988189999999989}]
[null,3,19170,659.29782660616183,0.67842953962354591,14.2,40,0.15,{"$f":"J47/F47","v":8.183098591549296},116.2,1,{"$f":"(((H47^2)/(2*9.81))*971.8*K47)*9.81","v":10.932749999999999},127.13275]
[null,4,15280,525.51229997611654,0.5407617822351477,8.9600000000000009,40,0.12,5.3995535714285712,48.38,1,{"$f":"(((H48^2)/(2*9.81))*971.8*K48)*9.81","v":6.9969599999999987},55.376960000000004]
[null,5,11706,402.59469787437303,0.41427731824899472,5.35,40,0.09,0.44859813084112149,2.4,3,11.807369999999997,14.207369999999997]
[null,18,4094,140.80152854072125,0.14488735186326535,2.75,20,0.12,13.712727272727273,37.71,3,20.990879999999997,58.700879999999998]
[null,"18э",4094,140.80152854072125,0.14488735186326535,1.65,15,0.22,13.709090909090911,22.62,4,94.070239999999984,116.69023999999999]
[null,19,4094,140.80152854072125,0.14488735186326535,7.51,20,0.12,13.712383488681759,102.98,5.5,38.483279999999993,141.46328]
[null,20,4094,140.80152854072125,0.14488735186326535,0.8,20,0.12,13.7125,10.97,3,20.990879999999997,31.960879999999996]
[null,12,11706,402.59469787437303,0.41427731824899472,5.2,40,0.09,0.44807692307692309,2.33,1.5,5.9036849999999985,8.2336849999999977]
[null,13,15280,525.51229997611654,0.5407617822351477,8.9600000000000009,40,0.12,5.3995535714285712,48.38,1.5,10.495439999999999,58.875439999999998]
[null,14,19170,659.29782660616183,0.67842953962354591,9.7799999999999994,40,0.15,8.1830265848670756,80.03,1.5,16.399124999999998,96.429124999999999]
[null,"14'",26160,899.69906854549788,0.92580682089472932,6.7,40,0.21,14.44776119402985,96.8,2,42.856379999999987,139.65637999999998]
[{"$nulls":12},{"$f":"SUM(M45:M57)","v":1080.6015600000001}]
[]
[]
["Ст №3",{"$nulls":7},"Потеря напора"]
[null,"№ участа","тепловая нагрузка на участке, Вт","Расход, кг/ч","Расход, м3/ч","Длина, м","Диаметр трубопровода ,мм","Скорость, м/с","на 1 м трубопровода","На участке","коэффицент местного сопротивления","Потери на сопротивлении, Па","Общие, Па"]
[null,1,26160,{"$f":"(3.6*C63)/(4.187*25)","v":899.69906854549788},{"$f":"D63/971.8","v":0.92580682089472932},9.9,40,0.21,{"$f":"J63/F63","v":14.447474747474747},143.03,2,{"$f":"(((H63^2)/(2*9.81))*971.8*K63)*9.81","v":42.856379999999987},{"$f":"L63+J63","v":185.88637999999997}]
[null,2,26160,{"$f":"(3.6*C64)/(4.187*25)","v":899.69906854549788},{"$f":"D64/971.8","v":0.92580682089472932},1.7,40,0.21,{"$f":"J64/F64","v":14.447058823529412},24.56,1,{"$f":"(((H64^2)/(2*9.81))*971.8*K64)*9.81","v":21.428189999999994},{"$f":"L64+J64","v":45.988189999999989}]
[null,3,19170,659.29782660616183,0.67842953962354591,14.2,40,0.15,{"$f":"J65/F65","v":8.183098591549296},116.2,1,{"$f":"(((H65^2)/(2*9.81))*971.8*K65)*9.81","v":10.932749999999999},127.13275]
[null,4,15280,525.51229997611654,0.5407617822351477,8.9600000000000009,40,0.12,5.3995535714285712,48.38,3,{"$f":"(((H66^2)/(2*9.81))*971.8*K66)*9.81","v":20.990879999999997},69.37088]
[null,21,3574,122.91760210174347,0.12648446398615298,3.46,20,0.12,12.000000000000002,41.52,5.5,38.483279999999993,80.00327999999999]
[null,22,3574,122.91760210174347,0.12648446398615298,4.3499999999999996,20,0.12,12.000000000000002,52.2,6.5,45.480239999999995,97.680239999999998]
[null,23,3574,122.91760210174347,0.12648446398615298,3.6,20,0.12,12,43.2,6.5,45.480239999999995,88.680239999999998]
[null,24,3574,122.91760210174347,0.12648446398615298,0.8,20,0.12,11.999999999999998,9.6,3,20.990879999999997,30.590879999999999]
[null,13,15280,525.51229997611654,0.5407617822351477,8.9600000000000009,40,0.12,5.3995535714285712,48.38,1.5,10.495439999999999,58.875439999999998]
[null,14,19170,659.29782660616183,0.67842953962354591,9.7799999999999994,40,0.15,8.1830265848670756,80.03,1.5,16.399124999999998,96.429124999999999]
[null,"14'",26160,899.69906854549788,0.92580682089472932,6.7,40,0.21,14.44776119402985,96.8,2,42.856379999999987,139.65637999999998]
[{"$nulls":12},{"$f":"SUM(M63:M73)","v":1020.293785}]
[]
[]
["Ст №2",{"$nulls":7},"Потеря напора"]
[null,"№ участа","тепловая нагрузка на участке, Вт","Расход, кг/ч","Расход, м3/ч","Длина, м","Диаметр трубопровода ,мм","Скорость, м/с","на 1 м трубопровода","На участке","коэффицент местного сопротивления","Потери на сопротивлении, Па","Общие, Па"]
[null,1,26160,{"$f":"(3.6*C79)/(4.187*25)","v":899.69906854549788},{"$f":"D79/971.8","v":0.92580682089472932},9.9,40,0.21,{"$f":"J79/F79","v":14.447474747474747},143.03,2,{"$f":"(((H79^2)/(2*9.81))*971.8*K79)*9.81","v":42.856379999999987},{"$f":"L79+J79","v":185.88637999999997}]
[null,2,26160,{"$f":"(3.6*C80)/(4.187*25)","v":899.69906854549788},{"$f":"D80/971.8","v":0.92580682089472932},1.7,40,0.21,{"$f":"J80/F80","v":14.447058823529412},24.56,1,{"$f":"(((H80^2)/(2*9.81))*971.8*K80)*9.81","v":21.428189999999994},{"$f":"L80+J80","v":45.988189999999989}]
[null,3,19170,659.29782660616183,0.67842953962354591,14.2,40,0.15,{"$f":"J81/F81","v":8.183098591549296},116.2,3,{"$f":"(((H81^2)/(2*9.81))*971.8*K81)*9.81","v":32.798249999999996},148.99824999999998]
[null,25,3890,133.78552663004535,0.13766775738839818,2.86,20,0.12,13.713286713286713,39.22,3,{"$f":"(((H82^2)/(2*9.81))*971.8*K82)*9.81","v":20.990879999999997},60.210879999999996]
[null,"25'",3890,133.78552663004535,0.13766775738839818,1.7,15,0.22,55.747058823529407,94.77,4,94.070239999999984,188.84023999999999]
[null,26,3890,133.78552663004535,0.13766775738839818,3,20,0.12,13.713333333333333,41.14,5,34.984799999999993,76.124799999999993]
[null,"26'",3890,133.78552663004535,0.13766775738839818,1,15,0.22,55.75,55.75,4,94.070239999999984,149.82023999999998]
[null,27,3890,133.78552663004535,0.13766775738839818,3,20,0.12,13.713333333333333,41.14,4.5,31.486319999999996,72.626319999999993]
[null,14,19170,659.29782660616183,0.67842953962354591,9.7799999999999994,40,0.15,8.1830265848670756,80.03,1.5,16.399124999999998,96.429124999999999]
[null,"14'",26160,899.69906854549788,0.92580682089472932,6.7,40,0.21,14.44776119402985,96.8,2,42.856379999999987,139.65637999999998]
[{"$nulls":12},{"$f":"SUM(M79:M88)","v":1164.5808049999998}]
[]
[]
["Ст №1",{"$nulls":7},"Потеря напора"]
[null,"№ участа","тепловая нагрузка на участке, Вт","Расход, кг/ч","Расход, м3/ч","Длина, м","Диаметр трубопровода ,мм","Скорость, м/с","на 1 м трубопровода","На участке","коэффицент местного сопротивления","Потери на сопротивлении, Па","Общие, Па"]
[null,1,26160,{"$f":"(3.6*C94)/(4.187*25)","v":899.69906854549788},{"$f":"D94/971.8","v":0.92580682089472932},9.9,40,0.21,{"$f":"J94/F94","v":14.447474747474747},143.03,2,{"$f":"(((H94^2)/(2*9.81))*971.8*K94)*9.81","v":42.856379999999987},{"$f":"L94+J94","v":185.88637999999997}]
[null,2,26160,{"$f":"(3.6*C95)/(4.187*25)","v":899.69906854549788},{"$f":"D95/971.8","v":0.92580682089472932},1.7,40,0.21,{"$f":"J95/F95","v":14.447058823529412},24.56,3,{"$f":"(((H95^2)/(2*9.81))*971.8*K95)*9.81","v":64.284569999999988},{"$f":"L95+J95","v":88.84456999999999}]
[null,28,6990,240.40124193933602,0.24737728127118341,2.71,25,0.14000000000000001,{"$f":"J96/F96","v":13.199261992619927},35.770000000000003,3,{"$f":"(((H96^2)/(2*9.81))*971.8*K96)*9.81","v":28.570920000000001},{"$f":"L96+J96","v":64.340920000000011}]
[null,"28'",6990,240.40124193933602,0.24737728127118341,1.5,20,0.22,39.226666666666667,58.84,4,94.070239999999984,152.91023999999999]
[null,29,6990,240.40124193933602,0.24737728127118341,3.75,25,0.14000000000000001,13.197333333333335,49.49,7.5,71.427300000000017,120.91730000000001]
[null,30,6990,240.40124193933602,0.24737728127118341,4.3,25,0.14000000000000001,13.197674418604652,56.75,7.5,71.427300000000017,128.1773]
[null,31,6990,240.40124193933602,0.24737728127118341,1.4,25,0.14000000000000001,13.200000000000001,18.48,5.5,52.380020000000009,70.860020000000006]
[null,32,6990,240.40124193933602,0.24737728127118341,0.8,25,0.14000000000000001,13.2,10.56,4.5,42.856380000000009,53.416380000000011]
[null,"14'",26160,899.69906854549788,0.92580682089472932,6.7,40,0.21,14.44776119402985,96.8,2,42.856379999999987,139.65637999999998]
[{"$nulls":12},{"$f":"SUM(M94:M102)","v":1005.00949}]

{"sheet":"Лист2","index":1,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[]}

{"sheet":"Лист3","index":2,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[]}