{"text_format":"2","workbook":"xls","n_sheets":11,"sheets":["T.A.C","сл-TAC","АДЛ","сл-АДЛ","Oventrop","COMAP","Danfoss","сл_Oventrop","сл_COMAP","сл_Danfoss","Лист1"],"not_rendered":{"charts":0,"images":8,"macros":1,"external_links":1,"defined_names":17,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"T.A.C","index":0,"n_rows":30,"n_cols":20,"rows_kept":30,"cut":false,"hidden":false,"merged":[[5,18,7,19],[0,1,0,9],[5,12,7,13],[5,14,7,15],[5,16,7,17]],"flags":["formulas_cached_only"]}
[null,"Вводя значение Kv выбираем клапан и определяем его настройку. Помним, что в \"Комменте\" всего лишь рекомендации, а не руководство к действию. Стараемся выбрать клапан откратым примерно на 70%"]
[null,"Kv =",61]
["№ п/п","Код по Базе","Наименование","Диапазон Kv","Настройка","Диапазон настроек","% открытия","Коммент",null,"Запись 1"]
[1,"TAC 52137115","TBV-LF-DN15","0,9-0,22-0,05","мал Kv","10-3-1","","","TAC 52137115","",null,null,"Существует несколько разновидностей клапанов TBV: "]
[2,"TAC 52138115","TBV-NF-DN15","1,8-0,45-0,22","мал Kv","10-3-1","","","TAC 52138115","",null,null,"TBV-LF","TBV-NF","TBV-С-LF","TBV-С-NF","TBV-СM-LF","TBV-СM-NF","TBV-СMP-LF","TBV-СMP-NF"]
[3,"TAC 52138120","TBV-NF-DN20","3,4-0,67-0,4","мал Kv","10-3-1","","","TAC 52138120","",null,null,"Простой балансировочный клапан",null,"Возможна установка привода TSE-M. Линейная характеристика",null,"Возможна установка привода TSE-M. Равнопроцентная характеристика",null,"Возможна установка привода TSE-M. Равнопроцентная характеристика + стабилизатор перепада"]
[4,"TAC 52133115","TBV-С-LF DN15","0,9 - 0,22 - 0,05","мал Kv","10-3-1","","","TAC 52133115",""]
[5,"TAC 52134115","TBV-С-NF DN15","1,8 - 0,45 - 0,22","мал Kv","10-3-1","","","TAC 52134115",""]
[6,"TAC 52134120","TBV-С-NF DN20","3,4 - 0,67 - 0,40","мал Kv","10-3-1","","","TAC 52134120","",null,15,"TAC 52137115",null,"TAC 52133115",null,null,"TAC 52144115"]
[7,"TAC 52134125","TBV-С-NF DN25","7,2 - 1,30 - 0,80","мал Kv","10-3-1","","","TAC 52134125","",null,15,null,"TAC 52138115",null,"TAC 52134115",null,"TAC 52144120"]
[8,"TAC 52143115","TBV-СM-LF DN15","0,4 - 0,21 - 0,05","мал Kv","10-3-1","","","TAC 52143115","",null,20,null,"TAC 52138120",null,"TAC 52134120",null,"TAC 52144125"]
[9,"TAC 52144115","TBV-СM-NF DN15","1 - 0,42 - 0,23","мал Kv","10-3-1","","","TAC 52144115","",null,25,null,null,null,"TAC 52134125",null,"TAC 52144125"]
[10,"TAC 52144120","TBV-СM-NF DN20","2 - 0,63 - 0,38","мал Kv","10-3-1","","","TAC 52144120",""]
[11,"TAC 52144125","TBV-СM-NF DN25","7,2-1,3-0,8","мал Kv","10-3-1","","","TAC 52144125","",null,null,"Клапаны TBV (LF,NF) можно тупо менять на TBV-C один в один, а вот клапаны TBV-CM (CMP) нет."]
[12,"TAC 52151014","STAD DN15","2,52 - 0,31 - 0,13","мал Kv","4-1,5-0,6","","","TAC 52151014","",null,null,"В таблице вверху даны возможные варианты замен, причем если TBV-C менять на указанные TBV-CM можно, то наоборот нет."]
[13,"TAC 52151020","STAD DN20","5,7 - 1,90 - 0,51","мал Kv","4-2-0,6","","","TAC 52151020","",null,null,"Рекомендуется сначала проверить Kv, поскольку ряды отличаются."]
[14,"TAC 52151025","STAD DN25","8,7 - 3,62 - 0,60","мал Kv","4-2-0,6","","","TAC 52151025",""]
[15,"TAC 52151032","STAD DN32","14,2 - 4,66 - 1,14","мал Kv","4-2-0,6","","","TAC 52151032","",null,null,"TBV-CMP все-таки следует подбирать индивидуально. Да и дорогие они: в 3 раза дороже CM."]
[16,"TAC 52151040","STAD DN40","19,2 - 6,10 - 1,75","мал Kv","4-2-0,6","","","TAC 52151040",""]
[17,"TAC 52182050","STAF DN50","33 - 11,7 - 2,56","мал Kv","4-2-0,6","","","TAC 52182050",""]
[18,"TAC 52181065","STAF DN65","85-1,8",5.533333333333333,"8-05",71.76470588235294,"","TAC 52181065","STAF DN65  n.-5,53"]
[19,"TAC 52181080","STAF DN80","120-2",5.230769230769231,"8-05",50.833333333333336,"неплохо","TAC 52181080","STAF DN80  n.-5,23"]
[20,"TAC 52181090","STAF DN100","190-2,5",3.9473684210526314,"8-05",32.10526315789474,"неплохо","TAC 52181090","STAF DN100  n.-3,95"]
[21,"TAC 52181091","STAF DN125","300-5,5",3.607142857142857,"8-05",20.333333333333332,"","TAC 52181091","STAF DN125  n.-3,61"]
[22,"TAC 52181092","STAF DN150","420-6,5",2.42,"8-05",14.523809523809524,"","TAC 52181092","STAF DN150  n.-2,42"]
[23,"TAC 52181093","STAF DN200","765-40",2.8666666666666667,"12-2",7.973856209150327,"","TAC 52181093","STAF DN200  n.-2,87"]
[24,"TAC 52181094","STAF DN250","1185-90",{"$error":"#N/A"},"12-2","","","TAC 52181094",""]
[25,"TAC 52181095","STAF DN300",{"$nulls":5},"TAC 52181095"]
[26,"TAC 52181096","STAF DN350",{"$nulls":5},"TAC 52181096"]
[27,"TAC 52181097","STAF DN400",{"$nulls":5},"TAC 52181097"]

{"sheet":"сл-TAC","index":1,"n_rows":22,"n_cols":54,"rows_kept":22,"cut":false,"hidden":true,"merged":[],"flags":["formulas_cached_only"]}
["_Массив_настроек (правило №1: все столбцы должны заканчиваться знаком \"-\")"]
["TBV-LF-DN15",null,"TBV-NF-DN15",null,"TBV-NF-DN20",null,"TBV-С-LF DN15",null,"TBV-С-NF DN15",null,"TBV-С-NF DN20",null,"TBV-С-NF DN25",null,"TBV-СM-LF DN15",null,"TBV-СM-NF DN15",null,"TBV-СM-NF DN20",null,"TBV-СM-NF DN25",null,"STAD DN15",null,"STAD DN20",null,"STAD DN25",null,"STAD DN32",null,"STAD DN40",null,"STAF DN50",null,"STAF DN65",null,"STAF DN80",null,"STAF DN100",null,"STAF DN125",null,"STAF DN150",null,"STAF DN200",null,"STAF DN250",null,"STAF DN300",null,"STAF DN350",null,"STAF DN400"]
["Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv"]
["настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка"]
[1,0.05,1,0.22,1,0.4,1,0.05,1,0.22,1,0.4,1,0.8,1,0.05,1,0.23,1,0.38,1,0.8,0.5,0.127,0.5,0.511,0.5,0.6,0.5,1.14,0.5,1.75,0.5,2.56,0.5,1.8,0.5,2,0.5,2.5,0.5,5.5,0.5,6.5,2,40,2,90]
[2,0.15,2,0.33,2,0.53,2,0.15,2,0.33,2,0.53,2,1,2,0.16,2,0.32,2,0.47,2,1.1,1,0.212,1,0.757,1,1.03,1,1.9,1,3.3,1,4.2,1,3.4,1,4,1,6,1,10.5,1,12,2.5,50,2.5,110]
[3,0.22,3,0.45,3,0.67,3,0.22,3,0.45,3,0.67,3,1.3,3,0.21,3,0.42,3,0.63,3,1.4,1.5,0.314,1.5,1.19,1.5,2.1,1.5,3.1,1.5,4.6,1.5,7.2,1.5,4.9,1.5,6,1.5,9,1.5,15.5,1.5,22,3,65,3,140]
[4,0.26,4,0.5,4,0.82,4,0.26,4,0.5,4,0.82,4,1.7,4,0.23,4,0.45,4,0.75,4,1.7,2,0.571,2,1.9,2,3.62,2,4.66,2,6.1,2,11.7,2,6.5,2,8,2,11.5,2,21.5,2,40,3.5,90,3.5,195]
[5,0.31,5,0.6,5,1.03,5,0.31,5,0.6,5,1,5,2.2,5,0.25,5,0.55,5,0.93,5,2.1,2.5,0.877,2.5,2.8,2.5,5.3,2.5,7.1,2.5,8.8,2.5,16.2,2.5,9.3,2.5,11,2.5,16,2.5,27,2.5,65,4,120,4,255]
[6,0.41,6,0.82,6,1.29,6,0.41,6,0.82,6,1.3,6,2.8,6,0.29,6,0.63,6,1.1,6,2.5,3,1.38,3,3.87,3,6.9,3,9.5,3,12.6,3,21.5,3,16.3,3,14,3,26,3,36,3,100,4.5,165,4.5,320]
[7,0.53,7,0.99,7,1.72,7,0.53,7,0.99,7,1.7,7,3.5,7,0.31,7,0.72,7,1.2,7,2.8,3.5,1.92,3.5,4.75,3.5,8,3.5,11.8,3.5,16,3.5,26.5,3.5,25.6,3.5,19.5,3.5,44,3.5,55,3.5,135,5,225,5,385]
[8,0.68,8,1.11,8,2.4,8,0.68,8,1.11,8,2.4,8,4.8,8,0.33,8,0.78,8,1.5,8,3.2,4,2.52,4,5.7,4,8.7,4,14.2,4,19.2,4,33,4,35.3,4,29,4,63,4,83,4,169,5.5,285,5.5,445]
[9,0.74,9,1.43,9,2.96,9,0.74,9,1.4,9,3,9,6.1,9,0.35,9,0.89,9,1.9,9,3.7,"-","-","-","-","-","-","-","-","-","-","-","-",4.5,44.5,4.5,41,4.5,80,4.5,114,4.5,207,6,340,6,500]
[10,0.9,10,1.8,10,3.4,10,0.9,10,1.8,10,3.4,10,7.2,10,0.4,10,1,10,2,10,4,"-","-","-","-","-","-","-","-","-","-","-","-",5,52,5,55,5,98,5,141,5,242,6.5,400,6.5,545]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",5.5,60.5,5.5,68,5.5,115,5.5,167,5.5,279,7,435,7,590,"-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",6,68,6,80,6,132,6,197,6,312,7.5,470,7.5,660,"-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",6.5,73,6.5,92,6.5,145,6.5,220,6.5,340,8,515,8,725]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",7,77,7,103,7,159,7,249,7,367,9,595,9,820]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",7.5,80.5,7.5,113,7.5,175,7.5,276,7.5,391,10,650,10,940]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",8,85,8,120,8,190,8,300,8,420,11,710,11,1050]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",12,765,12,1185,"-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]

{"sheet":"АДЛ","index":2,"n_rows":37,"n_cols":17,"rows_kept":37,"cut":false,"hidden":false,"merged":[[0,1,0,9]],"flags":["formulas_cached_only"]}
[null,"Вводя значение Kv выбираем клапан и определяем его настройку. Помним, что в \"Комменте\" всего лишь рекомендации, а не руководство к действию. Стараемся выбрать клапан откратым примерно на 70%"]
[null,"Kv =",2.5]
["№ п/п","Код по Базе","Наименование","Диапазон Kv","Настройка","Диапазон настроек","% открытия","Коммент",null,"Запись 1"]
[1,null,"VIR9505-DN15",null,3.7,null,93.63295880149813,"",0,"VIR9505-DN15  n.-3,7"]
[2,null,"VIR9505-DN20",null,3.129166666666667,null,60.97560975609757,"неплохо",0,"VIR9505-DN20  n.-3,13"]
[3,null,"VIR9505-DN25",null,1.4,null,39.0625,"неплохо",0,"VIR9505-DN25  n.-1,4"]
[4,null,"VIR9505-DN32",null,0.6791666666666666,null,20.833333333333332,"",0,"VIR9505-DN32  n.-0,68"]
[5,null,"VIR9505-DN40",null,{"$error":"#N/A"},null,"","",0,""]
[6,null,"VIR9505-DN50",null,{"$error":"#N/A"},null,"","",0,""]
[7,null,"VIR9515-DN15",null,"мал Kv",null,"","",0,""]
[8,null,"VIR9515-DN20",null,3.270731707317073,null,68.11989100817439,"неплохо",0,"VIR9515-DN20  n.-3,27"]
[9,null,"VIR9515-DN25",null,1.3461538461538463,null,40.06410256410256,"неплохо",0,"VIR9515-DN25  n.-1,35"]
[10,null,"VIR9515-DN32",null,{"$error":"#N/A"},null,"","",0,""]
[11,null,"VIR9515-DN40",null,{"$error":"#N/A"},null,"","",0,""]
[12,null,"VIR9515-DN50",null,{"$error":"#N/A"},null,"","",0,""]
[13,null,"КБЧ DN65",null,{"$error":"#N/A"},null,"","",0,""]
[14,null,"КБЧ DN80",null,{"$error":"#N/A"},null,"","",0,""]
[15,null,"КБЧ DN100",null,{"$error":"#N/A"},null,"","",0,""]
[16,null,"КБЧ DN125",null,{"$error":"#N/A"},null,"","",0,""]
[17,null,"КБЧ DN150",null,{"$error":"#N/A"},null,"","",0,""]
[18,null,"КБЧ DN200",null,{"$error":"#N/A"},null,"","",0,""]
[19,null,"КБЧ DN250",null,{"$error":"#N/A"},null,"","",0,"",null,null,"VIR 9505",null,"VIR 9515",null,"КБЧ, серии 10"]
[20,null,"КБЧ DN300",null,{"$error":"#N/A"},null,"","",0,""]
[]
[{"$nulls":13},"Для всех:"]
[]
[]
[]
[]
[]
[{"$nulls":14},"Функция дренажа"]
[{"$nulls":14},"Клапан может использоваться"]
[{"$nulls":14},"в качестве дренажного. Для этого"]
[{"$nulls":14},"необходимо установить специальный"]
[{"$nulls":14},"измерительный ниппель с функцией"]
[{"$nulls":14},"дренажа (поставляется отдельно от"]
[{"$nulls":14},"клапана)."]

{"sheet":"сл-АДЛ","index":3,"n_rows":86,"n_cols":40,"rows_kept":86,"cut":false,"hidden":true,"merged":[],"flags":["formulas_cached_only"]}
["_Массив_настроек (правило №1: все столбцы должны заканчиваться знаком \"-\")"]
["VIR9505-DN15",null,"VIR9505-DN20",null,"VIR9505-DN25",null,"VIR9505-DN32",null,"VIR9505-DN40",null,"VIR9505-DN50",null,"VIR9515-DN15",null,"VIR9515-DN20",null,"VIR9515-DN25",null,"VIR9515-DN32",null,"VIR9515-DN40",null,"VIR9515-DN50",null,"КБЧ DN65",null,"КБЧ DN80",null,"КБЧ DN100",null,"КБЧ DN125",null,"КБЧ DN150",null,"КБЧ DN200",null,"КБЧ DN250",null,"КБЧ DN300"]
["Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv"]
["настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка"]
[0.5,0.37,0.5,0.4,0.5,1.4,0.5,1.4,0.5,2.7,0.5,3.9,0.5,0.41,0.5,0.41,0.5,1.47,0.5,2.56,0.5,2.72,0.5,5.36,0.5,3.6,0.5,5.9,0.5,5.6,0.5,8.3,0.5,7.9,0.5,27.5,0.5,43.5,0.5,44.9]
[0.6,0.4,0.6,0.44,0.6,1.58,0.6,2.12,0.6,2.85,0.6,4.23,0.7,0.41,0.7,0.47,0.7,1.73,0.7,2.92,0.7,3.12,0.7,6.54,1,5.2,1,7.9,1,9.6,1,13,1,14.8,1,38.6,1,62.3,1,57.1]
[0.7,0.44,0.7,0.5,0.7,1.7,0.7,2.6,0.7,3,0.7,5,1,0.53,1,0.58,1,2.09,1,3.42,1,3.69,1,8.35,1.5,7,1.5,9.9,1.5,12.8,1.5,17.8,1.5,19.1,1.5,45.6,1.5,73.1,1.5,72.2]
[0.8,0.47,0.8,0.57,0.8,1.8,0.8,2.92,0.8,3.16,0.8,5.97,1.3,0.62,1.3,0.78,1.3,2.44,1.3,3.88,1.3,4.29,1.3,10.54,2,9.3,2,11.8,2,16.6,2,23.7,2,29.7,2,54.6,2,87.3,2,89.8]
[0.9,0.52,0.9,0.64,0.9,1.89,0.9,3.13,0.9,3.32,0.9,6.94,1.5,0.7,1.5,0.97,1.5,2.7,1.5,4.18,1.5,4.82,1.5,12.37,2.5,11.7,2.5,13.8,2.5,22.9,2.5,33.1,2.5,51.8,2.5,71.2,2.5,115.8,2.5,110.2]
[1,0.55,1,0.7,1,2,1,3.3,1,3.5,1,7.8,1.7,0.78,1.7,1.08,1.7,3.01,1.7,4.54,1.7,5.71,1.7,14.39,3,14.8,3,16.7,3,34,3,51.2,3,83.7,3,99.9,3,163.9,3,140.7]
[1.1,0.6,1.1,0.75,1.1,2.12,1.1,3.42,1.1,3.69,1.1,8.47,2,0.86,2,1.2,2,3.57,2,5.42,2,7.78,2,17.45,3.5,19.8,3.5,21.9,3.5,50.5,3.5,77,3.5,132,3.5,148.6,3.5,239.2,3.5,202]
[1.2,0.64,1.2,0.77,1.2,2.26,1.2,3.56,1.2,3.94,1.2,8.98,2.3,0.95,2.3,1.4,2.3,4.18,2.3,6.76,2.3,10.45,2.3,20.2,4,27.2,4,31.2,4,71.4,4,106.5,4,183.7,4,216.2,4,345.3,4,331.7]
[1.3,0.68,1.3,0.8,1.3,2.4,1.3,3.7,1.3,4.1,1.3,9.4,2.5,1.02,2.5,1.72,2.5,4.57,2.5,7.92,2.5,12.29,2.5,21.73,4.5,37.1,4.5,45.9,4.5,90.9,4.5,135.7,4.5,219.5,4.5,283.9,4.5,451.4,4.5,500.2]
[1.4,0.71,1.4,0.84,1.4,2.5,1.4,3.9,1.4,4.29,1.4,9.98,2.7,1.14,2.7,1.94,2.7,4.87,2.7,9.05,2.7,14.13,2.7,23.06,5,48.2,5,65,5,107.4,5,160.9,5,247.1,5,341.2,5,543.3,5,634.1]
[1.5,0.75,1.5,0.9,1.5,2.6,1.5,4.1,1.5,4.5,1.5,10.6,3,1.38,3,2.13,3,5.27,3,10.56,3,16.34,3,24.84,5.5,57.8,5.5,79.5,5.5,121.6,5.5,182.1,5.5,273.3,5.5,387.7,5.5,622,5.5,733.2]
[1.6,0.78,1.6,0.1,1.6,2.74,1.6,4.23,1.6,4.68,1.6,11.32,3.3,1.63,3.3,2.54,3.3,5.61,3.3,11.58,3.3,17.88,3.3,26.44,6,65,6,89.3,6,135,6,201.9,6,298.2,6,430.1,6,694,6,825.1]
[1.7,0.81,1.7,1,1.7,2.9,1.7,4.4,1.7,4.9,1.7,12.1,3.5,1.76,3.5,2.93,3.5,5.74,3.5,12.06,3.5,18.63,3.5,27.44,6.5,70.4,6.5,96.6,6.5,148.1,6.5,221.6,6.5,321.3,6.5,471.7,6.5,765.2,6.5,922.9]
[1.8,0.87,1.8,1.07,1.8,3.06,1.8,4.61,1.8,5.23,1.8,12.94,3.7,1.83,3.7,3.24,3.7,5.88,3.7,12.4,3.7,19.17,3.7,28.42,7,75.1,7,102.7,7,159.9,7,239.8,7,342.2,7,507.6,7,823.7,7,1018]
[1.9,0.91,1.9,1.14,1.9,3.27,1.9,4.86,1.9,5.62,1.9,13.84,4,1.89,4,3.51,4,6.14,4,12.54,4,19.59,4,29.72,7.5,79.8,7.5,108.2,7.5,169.8,7.5,255.9,7.5,360.7,7.5,535.2,7.5,876.3,7.5,1100]
[2,0.94,2,1.2,2,3.5,2,5.1,2,6.1,2,14.8,4.4,1.92,4.4,3.67,4.4,6.24,"-","-","-","-","-","-",8,85.2,8,113.4,8,177.9,8,270.8,8,376.8,8,560.8,8,925.3,8,1170]
[2.1,0.97,2.1,1.25,2.1,3.76,2.1,5.53,2.1,6.67,2.1,15.8,"-","-","-","-","-","-","-","-","-","-","-","-",8.5,"-",8.5,"-",8.5,184.7,8.5,285.1,8.5,390.2,8.5,590,8.5,974.3,8.5,1230]
[2.2,1,2.2,1.29,2.2,4.03,2.2,5.95,2.2,7.37,2.2,16.84,"-","-","-","-","-","-","-","-","-","-","-","-",9,"-",9,"-",9,"-",9,"-",9,"-",9,619.3,9,1022,9,1285]
[2.3,1.06,2.3,1.3,2.3,4.3,2.3,6.5,2.3,8.2,2.3,17.9,"-","-","-","-","-","-","-","-","-","-","-","-",9.5,"-",9.5,"-",9.5,"-",9.5,"-",9.5,"-",9.5,644.9,9.5,1068,9.5,1340]
[2.4,1.1,2.4,1.39,2.4,4.56,2.4,6.97,2.4,9.05,2.4,18.92,"-","-","-","-","-","-","-","-","-","-","-","-",10,"-",10,"-",10,"-",10,"-",10,"-",10,667.2,10,1110,10,1394]
[2.5,1.18,2.5,1.5,2.5,4.8,2.5,7.6,2.5,10,2.5,19.9,"-","-","-","-","-","-","-","-","-","-","-","-",10.5,"-",10.5,"-",10.5,"-",10.5,"-",10.5,"-",10.5,688.4,10.5,1150,10.5,1449]
[2.6,1.26,2.6,1.57,2.6,4.96,2.6,8.13,2.6,10.78,2.6,20.81,"-","-","-","-","-","-","-","-","-","-","-","-",11,"-",11,"-",11,"-",11,"-",11,"-",11,710,11,1188,11,1504]
[2.7,1.35,2.7,1.7,2.7,5.1,2.7,8.6,2.7,11.6,2.7,21.7,"-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
[2.8,1.49,2.8,1.85,2.8,5.24,2.8,9.32,2.8,12.53,2.8,22.45,"-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
[2.9,1.63,2.9,2.02,2.9,5.37,2.9,9.86,2.9,13.38,2.9,23.2,"-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
[3,1.75,3,2.2,3,5.5,3,10.4,3,1.41,3,23.9,"-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
[3.1,1.93,3.1,2.43,3.1,5.6,3.1,10.66,3.1,15,3.1,24.62,"-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
[3.2,2.08,3.2,2.67,3.2,5.71,3.2,10.86,3.2,15.74,3.2,25.29,"-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
[3.3,2.25,3.3,2.9,3.3,5.8,3.3,10.9,3.3,16.6,3.3,25.9,"-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
[3.4,2.35,3.4,3.15,3.4,5.91,3.4,11.06,3.4,17.06,3.4,26.56,"-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
[3.5,2.44,3.5,3.4,3.5,6,3.5,11.2,3.5,17.6,3.5,27.2,"-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
[3.6,2.46,3.6,3.61,3.6,6.1,3.6,11.25,3.6,18.13,3.6,27.74,"-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
[3.7,2.5,3.7,3.8,3.7,6.18,3.7,11.31,3.7,18.57,3.7,28.3,"-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
[3.8,2.55,3.8,3.96,3.8,6.26,3.8,11.47,3.8,18.94,3.8,28.83,"-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
[3.9,2.6,3.9,4.06,3.9,6.34,3.9,11.69,3.9,19.24,3.9,29.34,"-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
[4,2.67,4,4.1,4,6.4,4,12,4,19.5,4,29.8,"-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
[]
[]
[]
["VIR9505-DN15",null,"VIR9505-DN20",null,"VIR9505-DN25",null,"VIR9505-DN32",null,"VIR9505-DN40",null,"VIR9505-DN50",null,"VIR9515-DN15",null,"VIR9515-DN20",null,"VIR9515-DN25",null,"VIR9515-DN32",null,"VIR9515-DN40",null,"VIR9515-DN50",null,"КБЧ DN65",null,"КБЧ DN80",null,"КБЧ DN100",null,"КБЧ DN125",null,"КБЧ DN150",null,"КБЧ DN200",null,"КБЧ DN250",null,"КБЧ DN300"]
[]
[null,null,1,"VIR9505-DN15"]
[null,null,3,"VIR9505-DN20"]
[null,null,5,"VIR9505-DN25"]
[null,null,7,"VIR9505-DN32"]
[null,null,9,"VIR9505-DN40"]
[null,null,11,"VIR9505-DN50"]
[null,null,13,"VIR9515-DN15"]
[null,null,15,"VIR9515-DN20"]
[null,null,17,"VIR9515-DN25"]
[null,null,19,"VIR9515-DN32"]
[null,null,21,"VIR9515-DN40"]
[null,null,23,"VIR9515-DN50"]
[null,null,25,"КБЧ DN65"]
[null,null,27,"КБЧ DN80"]
[null,null,29,"КБЧ DN100"]
[null,null,31,"КБЧ DN125"]
[null,null,33,"КБЧ DN150"]
[null,null,35,"КБЧ DN200"]
[null,null,37,"КБЧ DN250"]
[null,null,39,"КБЧ DN300"]
[null,null,2]
[null,null,4]
[null,null,6]
[null,null,8]
[null,null,10]
[null,null,12]
[null,null,14]
[null,null,16]
[null,null,18]
[null,null,20]
[null,null,22]
[null,null,24]
[null,null,26]
[null,null,28]
[null,null,30]
[null,null,32]
[null,null,34]
[null,null,36]
[null,null,38]

{"sheet":"Oventrop","index":4,"n_rows":130,"n_cols":10,"rows_kept":130,"cut":false,"hidden":false,"merged":[[0,1,0,9]],"flags":["formulas_cached_only"]}
[null,"Вводя значение Kv выбираем клапан и определяем его настройку. Помним, что в \"Комменте\" всего лишь рекомендации, а не руководство к действию. Стараемся выбрать клапан открытым примерно на 70%"]
[null,"Kv =",61]
["№ п/п","Код по Базе","Наименование","Диапазон Kv","Настройка","Диапазон настроек","% открытия","Коммент",null,"Запись 1"]
[1,null,"AV6 , 1к","0,027-0,57","мал Kv",null,"","","",""]
[2,null,"AV6 , 2к","0,055-0,65","мал Kv",null,"","","",""]
[3,null,"AV6 , 3к","0,108-0,8","мал Kv",null,"","","",""]
[4,null,"Combi 2,3  - внутр рез, DN10","0,06-1,7","мал Kv",null,"","","",""]
[5,null,"Combi 2,3  - внутр рез, DN15","0,06-1,7","мал Kv",null,"","","",""]
[6,null,"Combi 2,3  - внутр рез, DN20","0,06-1,7","мал Kv",null,"","","",""]
[7,"OVN6974306","Hycocon VTZ, (ВР)  DN15",1.7,"мал Kv",null,"","","",""]
[8,"OVN6974307","Hycocon VTZ, (ВР) DN20",2.7,"мал Kv",null,"","","",""]
[9,"OVN6974308","Hycocon VTZ, (ВР) DN25",3.6,"мал Kv",null,"","","",""]
[10,"OVN6974309","Hycocon VTZ, (ВР) DN32",6.8,"мал Kv",null,"","","",""]
[11,"OVN6974310","Hycocon VTZ, (ВР) DN40",10,"мал Kv",null,"","","",""]
[12,null,"Hycocon VTZ, (ВР) DN50","?",{"$error":"#N/A"},null,"","","",""]
[13,"OVN6074264","Hydrocontrol VTR, (ВР+КИП), DN10","0,21-2,88","мал Kv",null,"","","",""]
[14,"OVN6074265","Hydrocontrol VTR, (ВР+КИП), DN15","0,23-3,88","мал Kv",null,"","","",""]
[15,"OVN6074266","Hydrocontrol VTR, (ВР+КИП), DN20","0,35-5,71","мал Kv",null,"","","",""]
[16,"OVN6074267","Hydrocontrol VTR, (ВР+КИП), DN25","0,57-8,89","мал Kv",null,"","","",""]
[17,"OVN6074268","Hydrocontrol VTR, (ВР+КИП), DN32","0,57-19,45","мал Kv",null,"","","",""]
[18,"OVN6074269","Hydrocontrol VTR, (ВР+КИП), DN40","1,2-27,51","мал Kv",null,"","","",""]
[19,"OVN6074270","Hydrocontrol VTR, (ВР+КИП), DN50","2,69-38,78","мал Kv",null,"","","",""]
[20,null,"Hydrocontrol R , DN65","7,0-50,00","мал Kv",null,"","","",""]
[21,"OVN4702377","Hydrocontrol VFC+КИП , DN20","0,11-4,77","мал Kv",null,"","","",""]
[22,"OVN4702378","Hydrocontrol VFC+КИП , DN25","0,51-8,38","мал Kv",null,"","","",""]
[23,"OVN4702379","Hydrocontrol VFC+КИП , DN32","0,4-17,08","мал Kv",null,"","","",""]
[24,"OVN4702380","Hydrocontrol VFC+КИП , DN40","0,89-26,88","мал Kv",null,"","","",""]
[25,"OVN4702381","Hydrocontrol VFC+КИП , DN50","3,29-36,00","мал Kv",null,"","","",""]
[26,"OVN4702382","Hydrocontrol VFC+КИП , DN65","1,9-98,00","мал Kv",null,"","","",""]
[27,"OVN4702383","Hydrocontrol VFC+КИП , DN80","2,3-122,2",4.8303317535545025,null,49.91816693944354,"неплохо","OVN4702383","Hydrocontrol VFC+КИП , DN80  n.-4,83"]
[28,"OVN4702384","Hydrocontrol VFC+КИП , DN100","3,4-201,0",3.72775,null,30.34825870646766,"неплохо","OVN4702384","Hydrocontrol VFC+КИП , DN100  n.-3,73"]
[29,"OVN4702385","Hydrocontrol VFC+КИП , DN125","5,5-293,0",3.4298507462686567,null,20.81911262798635,"","OVN4702385","Hydrocontrol VFC+КИП , DN125  n.-3,43"]
[30,"OVN4702386","Hydrocontrol VFC+КИП , DN150","5,2-404,3",2.6,null,15.08780608459065,"","OVN4702386","Hydrocontrol VFC+КИП , DN150  n.-2,6"]
[null,"OVN4702387","Hydrocontrol VFC+КИП , DN200","48,9-814,5",{"$nulls":4},""]
[null,"OVN4702388","Hydrocontrol VFC+КИП , DN250"]
[null,"OVN4702389","Hydrocontrol VFC+КИП , DN300"]
[null,"OVN4702390","Hydrocontrol VFC+КИП , DN350"]
[null,"OVN4702391","Hydrocontrol VFC+КИП , DN400"]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]
[null,null,0]

{"sheet":"COMAP","index":5,"n_rows":33,"n_cols":10,"rows_kept":33,"cut":false,"hidden":false,"merged":[[0,1,0,9]],"flags":["formulas_cached_only"]}
[null,"Вводя значение Kv выбираем клапан и определяем его настройку. Помним, что в \"Комменте\" всего лишь рекомендации, а не руководство к действию. Стараемся выбрать клапан открытым примерно на 70%"]
[null,"Kv =",61]
["№ п/п","Код по Базе","Наименование","Диапазон Kv","Настройка","Диапазон настроек","% открытия","Коммент",null,"Запись 1"]
[1,null,"Comap750R - резьба, DN15",null,"мал Kv","10-40","","",null,""]
[2,null,"Comap750R - резьба, DN20",null,"мал Kv","10-40","","",null,""]
[3,null,"Comap750R - резьба, DN25",null,"мал Kv","5-40","","",null,""]
[4,null,"Comap750 - резьба, DN10","0,05-1,95","мал Kv","5-40","","",null,""]
[5,null,"Comap750 - резьба, DN15","0,1-4,47","мал Kv","5-40","","",null,""]
[6,null,"Comap750 - резьба, DN20","0,13-5,9","мал Kv","5-40","","",null,""]
[7,null,"Comap750 - резьба, DN25","0,17-8,52","мал Kv","5-40","","",null,""]
[8,null,"Comap750 - резьба, DN32","0,2-14,88","мал Kv","5-40","","",null,""]
[9,null,"Comap750 - резьба, DN40","0,23-321,09","мал Kv","5-40","","",null,""]
[10,null,"Comap750 - резьба, DN50","0,55-35,48","мал Kv","5-40","","",null,""]
[11,null,"Comap751B - фланец, DN15",null,"мал Kv","0,5-6,6","","",null,""]
[12,null,"Comap751B - фланец, DN20",null,"мал Kv","0,5-6,6","","",null,""]
[13,null,"Comap751B - фланец, DN25",null,"мал Kv","0,5-6,6","","",null,""]
[14,null,"Comap751B - фланец, DN32",null,"мал Kv","0,5-6,6","","",null,""]
[15,null,"Comap751B - фланец, DN40",null,"мал Kv","0,5-7,5","","",null,""]
[16,null,"Comap751B - фланец, DN50",null,"мал Kv","0,5-7,5","","",null,""]
[17,null,"Comap751B - фланец, DN65",null,8.037499625,"0,5-10",81.98924731182795,"",null,"Comap751B - фланец, DN65  n.-8,04"]
[18,null,"Comap751B - фланец, DN80",null,7.35625,"0,5-12",54.95495495495496,"неплохо",null,"Comap751B - фланец, DN80  n.-7,36"]
[19,null,"Comap751B - фланец, DN100",null,5.957575757575758,"1,5-10",36.96969696969697,"неплохо",null,"Comap751B - фланец, DN100  n.-5,96"]
[20,null,"Comap751B - фланец, DN125",null,6.67,"1,5-13,5",25.206611570247933,"",null,"Comap751B - фланец, DN125  n.-6,67"]
[21,null,"Comap751B - фланец, DN150",null,6.464285714285714,"1,5-17,5",16.397849462365592,"",null,"Comap751B - фланец, DN150  n.-6,46"]
[22,null,"Comap751B - фланец, DN200",null,3.4214285714285713,"1,5-18,0",8.664772727272727,"",null,"Comap751B - фланец, DN200  n.-3,42"]
[23,null,0,null,{"$error":"#N/A"},null,"","",null,""]
[24,null,0,null,{"$error":"#N/A"},null,"","",null,""]
[25,null,0,null,{"$error":"#N/A"},null,"","",null,""]
[26,null,null,null,{"$error":"#N/A"},null,"","",null,""]
[27,null,null,null,{"$error":"#N/A"},null,"","",null,""]
[28,null,null,null,{"$error":"#N/A"},null,"","",null,""]
[29,null,null,null,{"$error":"#N/A"},null,"","",null,""]
[30,null,null,null,{"$error":"#N/A"},null,"","",null,""]

{"sheet":"Danfoss","index":6,"n_rows":39,"n_cols":11,"rows_kept":39,"cut":false,"hidden":false,"merged":[[0,1,0,9]],"flags":["formulas_cached_only"]}
[null,"Вводя значение Kv выбираем клапан и определяем его настройку. Помним, что в \"Комменте\" всего лишь рекомендации, а не руководство к действию. Стараемся выбрать клапан открытым примерно на 70%"]
[null,"Kv =",3.28]
["№ п/п","Код по Базе","Наименование","Диапазон Kv","Настройка","Диапазон настроек","% открытия","Коммент",null,"Запись 1"]
[1,1,"MSV-C с ИД-DN15",null,"мал Kv",null,"","","DAN003Z3020","","Старье"]
[2,2,"MSV-C без ИД-DN15",null,7.114285714285714,null,84.1025641025641,"","DAN003Z3030","MSV-C без ИД-DN15  n.-7,11","Старье"]
[3,3,"MSV-C с ИД-DN20",null,5.449999999999999,null,86.31578947368422,"","DAN003Z3021","MSV-C с ИД-DN20  n.-5,45","Старье"]
[4,4,"MSV-C без ИД-DN20",null,4.4363636363636365,null,44.93150684931507,"неплохо","DAN003Z3031","MSV-C без ИД-DN20  n.-4,44","Старье"]
[5,5,"MSV-C с ИД-DN25",null,3.853333333333333,null,46.857142857142854,"неплохо","DAN003Z3022","MSV-C с ИД-DN25  n.-3,85","Старье"]
[6,6,"MSV-C без ИД-DN25",null,3.986666666666667,null,27.796610169491522,"","DAN003Z3032","MSV-C без ИД-DN25  n.-3,99","Старье"]
[7,7,"MSV-C с ИД-DN32",null,3.1,null,20.759493670886076,"","DAN003Z3023","MSV-C с ИД-DN32  n.-3,1","Старье"]
[8,8,"MSV-C без ИД-DN32",null,2.272,null,15.185185185185183,"","DAN003Z3033","MSV-C без ИД-DN32  n.-2,27","Старье"]
[9,9,"MSV-C с ИД-DN40",null,2.432,null,15.619047619047619,"","DAN003Z3024","MSV-C с ИД-DN40  n.-2,43","Старье"]
[10,10,"MSV-C без ИД-DN40",null,2.0439024390243903,null,11.508771929824562,"","DAN003Z3034","MSV-C без ИД-DN40  n.-2,04","Старье"]
[11,11,"MSV-C с ИД-DN50",null,2.123809523809524,null,7.471526195899773,"","DAN003Z3025","MSV-C с ИД-DN50  n.-2,12","Старье"]
[12,12,"MSV-C без ИД-DN50",null,{"$error":"#N/A"},null,"","","DAN003Z3035","","Старье"]
[13,"DAN3939348","      USV-I - DN15",null,"мал Kv",null,"","",null,""]
[14,"DAN3939349","      USV-I - DN20",null,"мал Kv",null,"","",null,""]
[15,"DAN3939350","      USV-I - DN25",null,1.9833333333333334,null,82,"",null,"      USV-I - DN25  n.-1,98"]
[16,"DAN3939351","      USV-I - DN32",null,1.075,null,52.06349206349206,"неплохо",null,"      USV-I - DN32  n.-1,08"]
[17,"DAN3939352","      USV-I - DN40",null,0.7809523809523808,null,32.8,"неплохо",null,"      USV-I - DN40  n.-0,78"]
[18,"DAN3939353","      USV-I - DN50",null,2.0256637168141594,null,20.5,"",null,"      USV-I - DN50  n.-2,03"]
[19,"DAN3939338","MSV-BD- DN15 LF",null,"мал Kv",null,"","","DAN3939338",""]
[20,"DAN3939339","MSV-BD- DN15",null,"мал Kv",null,"","","DAN3939339",""]
[21,"DAN3939340","MSV-BD- DN20",null,3.664285714285714,null,62.95585412667946,"неплохо","DAN3939340","MSV-BD- DN20  n.-3,66"]
[22,"DAN3939341","MSV-BD- DN25",null,3.2244897959183674,null,40.1468788249694,"неплохо","DAN3939341","MSV-BD- DN25  n.-3,22"]
[23,"DAN3939342","MSV-BD- DN32",null,1.3561904761904762,null,24.04692082111437,"","DAN3939342","MSV-BD- DN32  n.-1,36"]
[24,"DAN3939343","MSV-BD- DN40",null,1.0559999999999998,null,16.416416416416418,"","DAN3939343","MSV-BD- DN40  n.-1,06"]
[25,"DAN3939344","MSV-BD- DN50",null,0.6651685393258426,null,10.376463144574503,"","DAN3939344","MSV-BD- DN50  n.-0,67"]
[26,"DAN3939365","MSV-F2- DN50",null,1.3724137931034481,null,7.192982456140351,"","DAN3939365","MSV-F2- DN50  n.-1,37"]
[27,"DAN3939366","MSV-F2- DN65",null,{"$error":"#N/A"},null,"","","DAN3939366",""]
[28,"DAN3939367","MSV-F2- DN80",null,{"$error":"#N/A"},null,"","","DAN3939367",""]
[29,"DAN3939368","MSV-F2- DN100",null,1.529032258064516,null,1.9878787878787878,"","DAN3939368","MSV-F2- DN100  n.-1,53"]
[30,"DAN3939369","MSV-F2- DN125",null,1.2902654867256635,null,1.3553719008264462,"","DAN3939369","MSV-F2- DN125  n.-1,29"]
[31,"DAN3939370","MSV-F2- DN150",null,1.1607843137254903,null,0.9010989010989011,"","DAN3939370","MSV-F2- DN150  n.-1,16"]
[32,"DAN3939371","MSV-F2- DN200",null,1.0794188861985472,null,0.488822652757079,"","DAN3939371","MSV-F2- DN200  n.-1,08"]
[33,"DAN3939372","MSV-F2- DN250",null,2.011043771043771,null,0.401468788249694,"","DAN3939372","MSV-F2- DN250  n.-2,01"]
[34,"DAN3939373","MSV-F2- DN300",null,2.0079805352798052,null,0.23768115942028986,"","DAN3939373","MSV-F2- DN300  n.-2,01"]
[35,"DAN3939374","MSV-F2- DN350",null,2.0066262626262628,null,0.19866747425802544,"","DAN3939374","MSV-F2- DN350  n.-2,01"]
[36,"DAN3939375","MSV-F2- DN400",null,2.0047536231884058,null,0.13729593972373377,"","DAN3939375","MSV-F2- DN400  n.-2"]

{"sheet":"сл_Oventrop","index":7,"n_rows":395,"n_cols":70,"rows_kept":395,"cut":false,"hidden":true,"merged":[],"flags":["formulas_cached_only"]}
["м_н_Oventrop (правило №1: все столбцы должны заканчиваться знаком \"-\")"]
["AV6 , 1к",null,"AV6 , 2к",null,"AV6 , 3к",null,"Combi 2,3  - внутр рез, DN10",null,"Combi 2,3  - внутр рез, DN15",null,"Combi 2,3  - внутр рез, DN20",null,"Hycocon VTZ, (ВР)  DN15",null,"Hycocon VTZ, (ВР) DN20",null,"Hycocon VTZ, (ВР) DN25",null,"Hycocon VTZ, (ВР) DN32",null,"Hycocon VTZ, (ВР) DN40",null,"Hycocon VTZ, (ВР) DN50",null,"Hydrocontrol VTR, (ВР+КИП), DN10",null,"Hydrocontrol VTR, (ВР+КИП), DN15",null,"Hydrocontrol VTR, (ВР+КИП), DN20",null,"Hydrocontrol VTR, (ВР+КИП), DN25",null,"Hydrocontrol VTR, (ВР+КИП), DN32",null,"Hydrocontrol VTR, (ВР+КИП), DN40",null,"Hydrocontrol VTR, (ВР+КИП), DN50",null,"Hydrocontrol R , DN65",null,"Hydrocontrol VFC+КИП , DN20",null,"Hydrocontrol VFC+КИП , DN25",null,"Hydrocontrol VFC+КИП , DN32",null,"Hydrocontrol VFC+КИП , DN40",null,"Hydrocontrol VFC+КИП , DN50",null,"Hydrocontrol VFC+КИП , DN65",null,"Hydrocontrol VFC+КИП , DN80",null,"Hydrocontrol VFC+КИП , DN100",null,"Hydrocontrol VFC+КИП , DN125",null,"Hydrocontrol VFC+КИП , DN150",null,"Hydrocontrol VFC+КИП , DN200",null,"Hydrocontrol VFC+КИП , DN250",null,"Hydrocontrol VFC+КИП , DN300",null,"Hydrocontrol VFC+КИП , DN350",null,"Hydrocontrol VFC+КИП , DN400"]
["Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv"]
["настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка"]
[1,0.027,1,0.055,1,0.1075,0.25,0.06,0.25,0.06,0.25,0.06,0.3,0.11,0.3,0.13,0.3,0.16,0.4,0.48,0.4,0.67,0.3,"-",0.25,0.21,0.25,0.23,0.25,0.35,0.25,0.57,0.25,0.57,0.25,1.2,0.5,2.69,1,7,"Oventrop",null,"Oventrop",null,"Oventrop",null,"Oventrop",null,"Oventrop",null,"Oventrop",null,"Oventrop",null,"Oventrop",null,"Oventrop",null,"Oventrop",null,"Oventrop"]
[2,0.056,2,0.17,2,0.38375,0.5,0.126,0.5,0.126,0.5,0.126,0.4,0.23,0.4,0.25,0.4,0.27,0.5,0.7,0.5,0.95,0.4,"-",0.5,0.34,0.5,0.34,0.5,0.5,0.5,0.93,0.5,1.03,0.5,2.66,0.75,4.17,1.1,7.3,"HydroctrF",null,"HydroctrF",null,"HydroctrF",null,"HydroctrF",null,"HydroctrF",null,"HydroctrF",null,"HydroctrF",null,"HydroctrF",null,"HydroctrF",null,"HydroctrF",null,"HydroctrF"]
[3,0.171,3,0.313,3,0.5792499999999998,0.75,0.19,0.75,0.19,0.75,0.19,0.5,0.34,0.5,0.36,0.5,0.39,0.6,0.85,0.6,1.17,0.5,"-",0.75,0.4,0.75,0.4,0.75,0.63,0.75,1.22,0.75,1.53,0.75,3.54,1,5.06,1.2,7.6,"DN20",null,"DN25",null,"DN32",null,"DN40",null,"DN50",null,"DN50",null,"DN80",null,"DN100",null,"DN125",null,"DN150",null,"DN200"]
[4,0.314,4,0.446,4,0.6934999999999998,1,0.25,1,0.25,1,0.25,0.6,0.45,0.6,0.48,0.6,0.51,0.7,1.1,0.7,1.41,0.6,"-",1,0.46,1,0.46,1,0.72,1,1.52,1,2.06,1,4.13,1.1,5.5,1.3,7.9]
[5,0.447,5,0.56,5,0.771875,1.5,0.42,1.5,0.42,1.5,0.42,0.7,0.55,0.7,0.6,0.7,0.63,0.8,1.3,0.8,1.65,0.7,"-",1.1,0.48,1.1,0.48,1.1,0.76,1.1,1.64,1.1,2.2,1.1,4.46,1.2,5.95,1.4,8.2,"Pos","Kv","Pos","Kv","Pos","Kv","Pos","Kv","Pos","Kv","Pos","Kv","Pos","Kv","Pos","Kv","Pos","Kv","Pos","Kv","Pos","Kv"]
[6,0.57,6,0.65,6,0.8,2,0.819,2,0.819,2,0.819,0.8,0.66,0.8,0.72,0.8,0.75,0.9,1.52,0.9,1.88,0.8,"-",1.2,0.5,1.2,0.5,1.2,0.81,1.2,1.76,1.2,2.35,1.2,4.78,1.3,6.35,1.5,8.5,0.25,0.11,0.25,0.51,0.25,0.4,0.25,0.89,0.5,3.29,0.5,3.29,0.5,2.3,0.5,3.4,0.5,5.5,0.5,5.2,2,48.9]
["-","-","-","-","-","-",3,1.236,3,1.236,3,1.236,0.9,0.76,0.9,0.84,0.9,0.87,1,1.7,1,2.1,0.9,"-",1.3,0.52,1.3,0.52,1.3,0.85,1.3,1.87,1.3,2.52,1.3,5.1,1.4,6.75,1.6,8.8,0.5,0.22,0.5,0.83,0.5,0.83,0.5,1.67,0.75,4.76,0.75,4.76,1,4.4,0.7,5.46,0.7,8.28,0.7,9.21,2.1,51.6]
["-","-","-","-","-","-",4,1.7,4,1.7,4,1.7,1,0.86,1,0.94,1,1,1.1,1.9,1.1,2.33,1,"-",1.4,0.54,1.4,0.55,1.4,0.89,1.4,1.98,1.4,2.7,1.4,5.42,1.5,7.15,1.7,9.1,0.75,0.33,0.75,1.08,0.75,1.25,0.75,2.49,1,5.76,1,5.76,1.1,4.74,1,8.55,1,12.45,1,15.22,2.2,54.2]
["-","-","-","-","-","-","-","-","-","-","-","-",1.1,0.97,1.1,1.02,1.1,1.1,1.2,2.1,1.2,2.56,1.1,"-",1.5,0.56,1.5,0.57,1.5,0.93,1.5,2.08,1.5,2.9,1.5,5.74,1.6,7.55,1.8,9.4,1,0.42,1,1.33,1,1.73,1,3.27,1.1,6.1,1.1,6.1,1.2,5.17,1.1,9.58,1.1,13.84,1.1,17.22,2.3,56.8]
["-","-","-","-","-","-","-","-","-","-","-","-",1.2,1.03,1.2,1.1,1.2,1.2,1.3,2.3,1.3,2.8,1.2,"-",1.6,0.58,1.6,0.6,1.6,0.97,1.6,2.18,1.6,3.1,1.6,6.06,1.7,7.95,1.9,9.7,1.1,0.48,1.1,1.43,1.1,1.92,1.1,3.58,1.2,6.41,1.2,6.41,1.3,5.67,1.2,10.61,1.2,15.23,1.2,19.23,2.4,59.4]
["-","-","-","-","-","-","-","-","-","-","-","-",1.3,1.1,1.3,1.2,1.3,1.3,1.4,2.5,1.4,3.05,1.3,"-",1.7,0.6,1.7,0.63,1.7,1.01,1.7,2.28,1.7,3.32,1.7,6.38,1.8,8.4,2,10,1.2,0.52,1.2,1.53,1.2,2.11,1.2,3.85,1.3,6.7,1.3,6.7,1.4,6.28,1.3,11.64,1.3,16.62,1.3,21.23,2.5,62]
["-","-","-","-","-","-","-","-","-","-","-","-",1.4,1.16,1.4,1.3,1.4,1.4,1.5,2.7,1.5,3.3,1.4,"-",1.8,0.63,1.8,0.66,1.8,1.05,1.8,2.38,1.8,3.55,1.8,6.7,1.9,8.8,2.1,10.4,1.3,0.55,1.3,1.63,1.3,2.3,1.3,4.18,1.4,6.98,1.4,6.98,1.5,7,1.4,12.67,1.4,18.01,1.4,23.24,2.6,66.4]
["-","-","-","-","-","-","-","-","-","-","-","-",1.5,1.22,1.5,1.4,1.5,1.5,1.6,2.85,1.6,3.57,1.5,"-",1.9,0.65,1.9,0.69,1.9,1.1,1.9,2.48,1.9,3.78,1.9,7.02,2,9.17,2.2,10.8,1.4,0.59,1.4,1.73,1.4,2.49,1.4,4.48,1.5,7.24,1.5,7.24,1.6,7.89,1.5,14,1.5,19.4,1.5,25.26,2.7,70.8]
["-","-","-","-","-","-","-","-","-","-","-","-",1.6,1.26,1.6,1.51,1.6,1.6,1.7,3.01,1.7,3.9,1.6,"-",2,0.67,2,0.72,2,1.14,2,2.58,2,4.02,2,7.34,2.1,9.65,2.3,11.2,1.5,0.63,1.5,1.83,1.5,2.68,1.5,4.77,1.6,7.66,1.6,7.66,1.7,8.82,1.6,14.73,1.6,20.94,1.6,27.24,2.8,75.2]
["-","-","-","-","-","-","-","-","-","-","-","-",1.7,1.31,1.7,1.62,1.7,1.7,1.8,3.2,1.8,4.25,1.7,"-",2.1,0.7,2.1,0.76,2.1,1.18,2.1,2.67,2.1,4.25,2.1,7.62,2.2,10.15,2.4,11.6,1.6,0.67,1.6,1.94,1.6,2.87,1.6,5.06,1.7,8.2,1.7,8.2,1.8,9.78,1.7,15.76,1.7,22.47,1.7,29.5,2.9,79.6]
["-","-","-","-","-","-","-","-","-","-","-","-",1.8,1.36,1.8,1.68,1.8,1.8,1.9,3.4,1.9,4.55,1.8,"-",2.2,0.73,2.2,0.8,2.2,1.22,2.2,2.77,2.2,4.48,2.2,7.89,2.3,10.65,2.5,12,1.7,0.7,1.7,2.04,1.7,3.06,1.7,5.35,1.8,8.66,1.8,8.66,1.9,10.79,1.8,16.79,1.8,24.01,1.8,31.25,3,84]
["-","-","-","-","-","-","-","-","-","-","-","-",1.9,1.41,1.9,1.74,1.9,1.9,2,3.6,2,4.8,1.9,"-",2.3,0.76,2.3,0.85,2.3,1.26,2.3,2.87,2.3,4.68,2.3,8.16,2.4,11.15,2.6,12.4,1.8,0.75,1.8,2.14,1.8,3.25,1.8,5.64,1.9,9.1,1.9,9.1,2,11.85,1.9,17.82,1.9,25.54,1.9,33.26,3.1,90]
["-","-","-","-","-","-","-","-","-","-","-","-",2,1.46,2,1.8,2,2,2.1,3.81,2.1,5.01,2,"-",2.4,0.79,2.4,0.91,2.4,1.3,2.4,2.98,2.4,4.88,2.4,8.43,2.5,11.65,2.7,12.8,1.9,0.79,1.9,2.24,1.9,3.44,1.9,5.92,2,9.55,2,9.55,2.1,12.95,2,18.5,2,26.6,2,35.26,3.2,96]
["-","-","-","-","-","-","-","-","-","-","-","-",2.1,1.5,2.1,1.86,2.1,2.1,2.2,4.02,2.2,5.2,2.1,"-",2.5,0.83,2.5,0.98,2.5,1.35,2.5,3.09,2.5,5.08,2.5,8.7,2.6,12.15,2.8,13.2,2,0.83,2,2.34,2,3.63,2,6.2,2.1,9.96,2.1,9.96,2.2,14.11,2.1,19.88,2.1,28.61,2.1,37.13,3.3,102]
["-","-","-","-","-","-","-","-","-","-","-","-",2.2,1.53,2.2,1.93,2.2,2.21,2.3,4.22,2.3,5.41,2.2,"-",2.6,0.87,2.6,1.05,2.6,1.4,2.6,3.2,2.6,5.25,2.6,8.97,2.7,12.65,2.9,13.6,2.1,0.87,2.1,2.44,2.1,3.82,2.1,6.43,2.2,10.38,2.2,10.38,2.3,15.33,2.2,20.91,2.2,30.15,2.2,39.41,3.4,108]
["-","-","-","-","-","-","-","-","-","-","-","-",2.3,1.55,2.3,1.99,2.3,2.31,2.4,4.33,2.4,5.64,2.3,"-",2.7,0.91,2.7,1.12,2.7,1.45,2.7,3.31,2.7,5.45,2.7,9.24,2.8,13.2,3,14,2.2,0.91,2.2,2.53,2.2,4.01,2.2,6.67,2.3,10.78,2.3,10.78,2.4,16.61,2.3,21.94,2.3,31.68,2.3,42.3,3.5,114]
["-","-","-","-","-","-","-","-","-","-","-","-",2.4,1.57,2.4,2.05,2.4,2.41,2.5,4.6,2.5,5.9,2.4,"-",2.8,0.96,2.8,1.2,2.8,1.5,2.8,3.43,2.8,5.65,2.8,9.51,2.9,13.7,3.1,14.3,2.3,0.95,2.3,2.63,2.3,4.2,2.3,6.9,2.4,11.18,2.4,11.18,2.5,18.65,2.4,22.97,2.4,33.22,2.4,46.25,3.6,121]
["-","-","-","-","-","-","-","-","-","-","-","-",2.5,1.58,2.5,2.1,2.5,2.5,2.6,4.76,2.6,6.15,2.5,"-",2.9,1.03,2.9,1.27,2.9,1.55,2.9,3.56,2.9,5.83,2.9,9.77,3,14.23,3.2,14.6,2.4,0.99,2.4,2.73,2.4,4.39,2.4,7.15,2.5,11.57,2.5,11.57,2.6,19.39,2.5,24,2.5,34.75,2.5,53.92,3.7,128.8]
["-","-","-","-","-","-","-","-","-","-","-","-",2.6,1.59,2.6,2.14,2.6,2.58,2.7,4.9,2.7,6.38,2.6,"-",3,1.1,3,1.34,3,1.6,3,3.69,3,6,3,10.02,3.1,14.65,3.3,14.9,2.5,1.04,2.5,2.83,2.5,4.58,2.5,7.39,2.6,11.95,2.6,11.95,2.7,20.9,2.6,26,2.6,37.18,2.6,61,3.8,136.2]
["-","-","-","-","-","-","-","-","-","-","-","-",2.7,1.6,2.7,2.18,2.7,2.64,2.8,5,2.8,6.6,2.7,"-",3.1,1.16,3.1,1.41,3.1,1.66,3.1,3.82,3.1,6.17,3.1,10.25,3.2,15.1,3.4,15.2,2.6,1.08,2.6,2.93,2.6,4.77,2.6,7.64,2.7,12.33,2.7,12.33,2.8,22.51,2.7,28.13,2.7,39.69,2.7,68.55,3.9,143.6]
["-","-","-","-","-","-","-","-","-","-","-","-",2.8,1.61,2.8,2.21,2.8,2.7,2.9,5.15,2.9,6.8,2.8,"-",3.2,1.23,3.2,1.48,3.2,1.74,3.2,3.96,3.2,6.35,3.2,10.5,3.3,15.5,3.5,15.5,2.7,1.12,2.7,3.03,2.7,4.96,2.7,7.89,2.8,12.69,2.8,12.69,2.9,24.24,2.8,30.4,2.8,42.29,2.8,76.64,4,151]
["-","-","-","-","-","-","-","-","-","-","-","-",2.9,1.62,2.9,2.23,2.9,2.75,3,5.25,3,7,2.9,"-",3.3,1.29,3.3,1.55,3.3,1.82,3.3,4.11,3.3,6.52,3.3,10.73,3.4,15.95,3.6,15.8,2.8,1.16,2.8,3.12,2.8,5.15,2.8,8.14,2.9,13.06,2.9,13.06,3,26.1,2.9,32.81,2.9,44.97,2.9,85.4,4.1,162]
["-","-","-","-","-","-","-","-","-","-","-","-",3,1.63,3,2.25,3,2.8,3.5,5.69,3.5,7.85,3,"-",3.4,1.36,3.4,1.62,3.4,1.93,3.4,4.26,3.4,6.7,3.4,10.97,3.5,16.35,3.7,16.1,2.9,1.2,2.9,3.22,2.9,5.34,2.9,8.39,3,13.41,3,13.41,3.1,27.85,3,35.4,3,47.75,3,95.02,4.2,173]
["-","-","-","-","-","-","-","-","-","-","-","-",3.5,1.65,3.5,2.33,3.5,2.98,4,6,4,8.4,3.5,"-",3.5,1.42,3.5,1.7,3.5,2.04,3.5,4.42,3.5,6.85,3.5,11.2,3.6,16.8,3.8,16.4,3,1.25,3,3.32,3,5.53,3,8.69,3.1,13.87,3.1,13.87,3.2,29.61,3.1,38.18,3.1,50.63,3.1,105.51,4.3,184]
["-","-","-","-","-","-","-","-","-","-","-","-",4,1.66,4,2.4,4,3.1,4.5,6.18,4.5,8.8,4,"-",3.6,1.49,3.6,1.77,3.6,2.15,3.6,4.57,3.6,7,3.6,11.43,3.7,17.25,3.9,16.7,3.1,1.3,3.1,3.45,3.1,5.73,3.1,8.91,3.2,14.32,3.2,14.32,3.3,31.39,3.2,41.17,3.2,53.62,3.2,114.45,4.4,195]
["-","-","-","-","-","-","-","-","-","-","-","-",4.5,1.67,4.5,2.47,4.5,3.2,5,6.3,5,9.1,4.5,"-",3.7,1.56,3.7,1.84,3.7,2.25,3.7,4.72,3.7,7.16,3.7,11.66,3.8,17.65,4,17,3.2,1.35,3.2,3.58,3.2,5.92,3.2,9.17,3.3,14.78,3.3,14.78,3.4,33.19,3.3,44.44,3.3,56.73,3.3,122.36,4.5,206]
["-","-","-","-","-","-","-","-","-","-","-","-",5,1.68,5,2.55,5,3.3,5.5,6.4,5.5,9.35,5,"-",3.8,1.62,3.8,1.91,3.8,2.36,3.8,4.87,3.8,7.33,3.8,11.9,3.9,18.1,4.1,17.5,3.3,1.41,3.3,3.7,3.3,6.12,3.3,9.43,3.4,15.25,3.4,15.25,3.5,35,3.4,48.02,3.4,60,3.4,129.52,4.6,216.8]
["-","-","-","-","-","-","-","-","-","-","-","-",5.5,1.69,5.5,2.63,5.5,3.43,6,6.5,6,9.5,5.5,"-",3.9,1.69,3.9,1.98,3.9,2.47,3.9,5.02,3.9,7.49,3.9,12.13,4,18.5,4.2,18,3.4,1.47,3.4,3.84,3.4,6.31,3.4,9.69,3.5,15.56,3.5,15.56,3.6,36.83,3.5,52,3.5,63.35,3.5,135.45,4.7,227.6]
["-","-","-","-","-","-","-","-","-","-","-","-",6,1.7,6,2.7,6,3.6,6.5,6.58,6.5,9.65,6,"-",4,1.76,4,2.05,4,2.58,4,5.16,4,7.64,4,12.36,4.1,19,4.3,18.5,3.5,1.54,3.5,3.98,3.5,6.51,3.5,9.97,3.6,16.2,3.6,16.2,3.7,38.68,3.6,55.93,3.6,66.62,3.6,142.21,4.8,238.4]
["-","-","-","-","-","-","-","-","-","-","-","-",6.5,"-",6.5,"-",6.5,"-",7,6.65,7,9.8,6.5,"-",4.1,1.82,4.1,2.12,4.1,2.69,4.1,5.32,4.1,7.85,4.1,12.65,4.2,19.45,4.4,19,3.6,1.61,3.6,4.13,3.6,6.71,3.6,10.25,3.7,16.67,3.7,16.67,3.8,40.55,3.7,59.89,3.7,70,3.7,147.41,4.9,249.2]
["-","-","-","-","-","-","-","-","-","-","-","-",7,"-",7,"-",7,"-",7.5,6.72,7.5,9.9,7,"-",4.2,1.88,4.2,2.18,4.2,2.8,4.2,5.47,4.2,8.05,4.2,12.95,4.3,19.85,4.5,19.5,3.7,1.7,3.7,4.27,3.7,6.9,3.7,10.52,3.8,17.14,3.8,17.14,3.9,42.43,3.8,63.89,3.8,73.53,3.8,153.33,5,260.3]
["-","-","-","-","-","-","-","-","-","-","-","-",7.5,"-",7.5,"-",7.5,"-",8,6.8,8,10,7.5,"-",4.3,1.94,4.3,2.24,4.3,2.91,4.3,5.63,4.3,8.25,4.3,13.25,4.4,20.3,4.6,20,3.8,1.79,3.8,4.42,3.8,7.1,3.8,10.8,3.9,17.6,3.9,17.6,4,44.75,3.9,67.92,3.9,77.21,3.9,160,5.1,271.9]
["-","-","-","-","-","-","-","-","-","-","-","-",8,"-",8,"-",8,"-","-","-","-","-",8,"-",4.4,2,4.4,2.31,4.4,3.01,4.4,5.79,4.4,8.45,4.4,13.52,4.5,20.7,4.7,20.5,3.9,1.89,3.9,4.58,3.9,7.3,3.9,11.09,4,18.34,4,18.34,4.1,46.27,4,72,4,81.05,4,167.12,5.2,283.8]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",4.5,2.06,4.5,2.38,4.5,3.12,4.5,5.95,4.5,8.65,4.5,13.8,4.6,21.15,4.8,21,4,2,4,4.74,4,7.46,4,11.38,4.1,18.52,4.1,18.52,4.2,48.21,4.1,76.11,4.1,85.07,4.1,174.48,5.3,295.6]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",4.6,2.12,4.6,2.44,4.6,3.23,4.6,6.1,4.6,8.85,4.6,14.1,4.7,21.6,4.9,21.5,4.1,2.11,4.1,4.9,4.1,7.69,4.1,11.67,4.2,19.01,4.2,19.01,4.3,50.19,4.2,80.27,4.2,89.3,4.2,181.76,5.4,307.5]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",4.7,2.19,4.7,2.51,4.7,3.34,4.7,6.26,4.7,9.05,4.7,14.4,4.8,22.05,5,22,4.2,2.22,4.2,5.07,4.2,7.88,4.2,11.97,4.3,19.48,4.3,19.48,4.4,52.18,4.3,84.47,4.3,93.77,4.3,189.05,5.5,320]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",4.8,2.25,4.8,2.57,4.8,3.44,4.8,6.42,4.8,9.25,4.8,14.7,4.9,22.5,5.1,22.4,4.3,2.33,4.3,5.24,4.3,8.08,4.3,12.27,4.4,19.95,4.4,19.95,4.5,55.2,4.4,88.71,4.4,98.5,4.4,196.34,5.6,332]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",4.9,2.31,4.9,2.63,4.9,3.55,4.9,6.57,4.9,9.47,4.9,14.98,5,22.93,5.2,22.8,4.4,2.43,4.4,5.42,4.4,8.27,4.4,12.58,4.5,20.55,4.5,20.55,4.6,56.22,4.5,93,4.5,103.55,4.5,203.65,5.7,344.8]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",5,2.37,5,2.7,5,3.65,5,6.72,5,9.69,5,15.26,5.1,23.25,5.3,23.2,4.5,2.54,4.5,5.6,4.5,8.47,4.5,12.89,4.6,20.89,4.6,20.89,4.7,58.28,4.6,97.37,4.6,108.16,4.6,210.78,5.8,357.6]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",5.1,2.42,5.1,2.77,5.1,3.78,5.1,6.84,5.1,9.9,5.1,15.65,5.2,23.57,5.4,23.6,4.6,2.65,4.6,5.8,4.6,8.67,4.6,13.2,4.7,21.36,4.7,21.36,4.8,60.36,4.7,101.62,4.7,112.92,4.7,217.79,5.9,370.3]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",5.2,2.47,5.2,2.84,5.2,3.9,5.2,6.96,5.2,10.1,5.2,16.1,5.3,23.9,5.5,24,4.7,2.76,4.7,6,4.7,8.86,4.7,13.52,4.8,21.83,4.8,21.83,4.9,62.47,4.8,105.74,4.8,117.84,4.8,224.14,6,383]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",5.3,2.52,5.3,2.92,5.3,4.02,5.3,7.08,5.3,10.3,5.3,16.55,5.4,24.2,5.6,24.4,4.8,2.87,4.8,6.2,4.8,9.06,4.8,13.84,4.9,22.3,4.9,22.3,5,64.6,4.9,109.75,4.9,122.95,4.9,231.46,6.1,396]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",5.4,2.56,5.4,2.99,5.4,4.15,5.4,7.2,5.4,10.5,5.4,16.95,5.5,24.5,5.7,24.8,4.9,2.98,4.9,6.42,4.9,9.25,4.9,14.17,5,22.7,5,22.7,5.1,66.98,5,112,5,128.25,5,238.91,6.2,409]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",5.5,2.6,5.5,3.06,5.5,4.27,5.5,7.32,5.5,10.7,5.5,17.35,5.6,24.8,5.8,25.2,5,3.09,5,6.64,5,9.45,5,14.51,5.1,23.12,5.1,23.12,5.2,69.32,5.1,117.46,5.1,133.77,5.1,244.72,6.3,422]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",5.6,2.63,5.6,3.13,5.6,4.4,5.6,7.44,5.6,10.9,5.6,17.8,5.7,25.15,5.9,25.6,5.1,3.19,5.1,6.85,5.1,9.68,5.1,14.91,5.2,23.54,5.2,23.54,5.3,71.63,5.2,121.17,5.2,139.54,5.2,251.2,6.4,435]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",5.7,2.66,5.7,3.2,5.7,4.52,5.7,7.56,5.7,11.1,5.7,18.2,5.8,25.45,6,26,5.2,3.3,5.2,7.03,5.2,9.92,5.2,15.32,5.3,23.95,5.3,23.95,5.4,73.9,5.3,124.79,5.3,145.6,5.3,257.6,6.5,447.8]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",5.8,2.69,5.8,3.27,5.8,4.65,5.8,7.68,5.8,11.3,5.8,18.65,5.9,25.8,6.1,26.3,5.3,3.41,5.3,7.18,5.3,10.15,5.3,15.75,5.4,24.37,5.4,24.37,5.5,75.45,5.4,127.52,5.4,151.96,5.4,263.9,6.6,460]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",5.9,2.72,5.9,3.34,5.9,4.77,5.9,7.8,5.9,11.5,5.9,19.05,6,26.09,6.2,26.6,5.4,3.52,5.4,7.32,5.4,10.35,5.4,16.14,5.5,24.8,5.5,24.8,5.6,78.37,5.5,132,5.5,158.7,5.5,272.4,6.7,472.5]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",6,2.75,6,3.4,6,4.89,6,7.91,6,11.7,6,19.45,6.1,26.45,6.3,26.9,5.5,3.63,5.5,7.44,5.5,10.6,5.5,16.62,5.6,25.21,5.6,25.21,5.7,80.56,5.6,135.16,5.6,164.1,5.6,276.24,6.8,484.8]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",6.1,2.77,6.1,3.47,6.1,5.02,6.1,8.02,6.1,11.9,6.1,19.75,6.2,26.8,6.4,27.2,5.6,3.74,5.6,7.55,5.6,10.83,5.6,17.1,5.7,25.63,5.7,25.63,5.8,82.72,5.7,138.47,5.7,169.6,5.7,282.3,6.9,497.2]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",6.2,2.79,6.2,3.54,6.2,5.15,6.2,8.12,6.2,12.12,6.2,20.05,6.3,27.1,6.5,27.5,5.7,3.84,5.7,7.65,5.7,11.05,5.7,17.58,5.8,26.04,5.8,26.04,5.9,84.85,5.8,141.71,5.8,175.21,5.8,288.27,7,509.5]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",6.3,2.81,6.3,3.61,6.3,5.28,6.3,8.22,6.3,12.35,6.3,20.35,6.4,27.45,6.6,27.7,5.8,3.95,5.8,7.74,5.8,11.27,5.8,18.07,5.9,26.46,5.9,26.46,6,87,5.9,144.89,5.9,180.94,5.9,294.17,7.1,519.4]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",6.4,2.83,6.4,3.67,6.4,5.36,6.4,8.31,6.4,12.57,6.4,20.65,6.5,27.75,6.7,27.9,5.9,4.06,5.9,7.82,5.9,11.48,5.9,18.59,6,26.88,6,26.88,6.1,89.04,6,148,6,185.3,6,300.4,7.2,529.3]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",6.5,2.84,6.5,3.72,6.5,5.44,6.5,8.41,6.5,12.8,6.5,20.95,6.6,28.05,6.8,28.1,6,4.17,6,7.9,6,11.7,6,19.13,6.1,27.18,6.1,27.18,6.2,91,6.1,151.94,6.1,192.75,6.1,305.76,7.3,539.2]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",6.6,2.85,6.6,3.76,6.6,5.5,6.6,8.51,6.6,13,6.6,21.25,6.7,28.4,6.9,28.3,6.1,4.27,6.1,7.97,6.1,11.96,6.1,19.53,6.2,27.48,6.2,27.48,6.3,93.13,6.2,155.63,6.2,198.85,6.2,311.45,7.4,549.1]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",6.7,2.86,6.7,3.79,6.7,5.56,6.7,8.61,6.7,13.22,6.7,21.55,6.8,28.75,7,28.5,6.2,4.35,6.2,8.03,6.2,12.2,6.2,19.9,6.3,27.75,6.3,27.75,6.4,95.14,6.3,159.1,6.3,205.1,6.3,317.08,7.5,559]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",6.8,2.87,6.8,3.82,6.8,5.61,6.8,8.71,6.8,13.45,6.8,21.85,6.9,29.1,7.1,28.8,6.3,4.43,6.3,8.09,6.3,12.41,6.3,20.25,6.4,28.06,6.4,28.06,6.5,97.55,6.4,162.38,6.4,211.5,6.4,322.07,7.6,571]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",6.9,2.87,6.9,3.85,6.9,5.66,6.9,8.8,6.9,13.68,6.9,22.15,7,29.41,7.2,29.1,6.4,4.5,6.4,8.15,6.4,12.62,6.4,20.59,6.5,28.31,6.5,28.31,6.6,99.1,6.5,164.03,6.5,218.05,6.5,326.7,7.7,582.5]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",7,2.88,7,3.88,7,5.71,7,8.89,7,13.91,7,22.45,7.1,29.75,7.3,29.4,6.5,4.56,6.5,8.2,6.5,12.81,6.5,20.9,6.6,28.61,6.6,28.61,6.7,101.04,6.6,168.44,6.6,223.37,6.6,333.58,7.8,594.2]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",7.1,14.13,7.1,22.7,7.2,30.1,7.4,29.7,6.6,4.61,6.6,8.24,6.6,13,6.6,21.21,6.7,28.88,6.7,28.88,6.8,102.96,6.7,171.26,6.7,228.64,6.7,338.34,7.9,606]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",7.2,14.35,7.2,22.95,7.3,30.4,7.5,30,6.7,4.66,6.7,8.28,6.7,13.17,6.7,21.5,6.8,29.15,6.8,29.15,6.9,104.87,6.8,173.95,6.8,233.89,6.8,344.29,8,618]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",7.3,14.57,7.3,23.15,7.4,30.75,7.6,30.4,6.8,4.7,6.8,8.32,6.8,13.33,6.8,21.74,6.9,29.41,6.9,29.41,7,106.75,6.9,176.53,6.9,239.03,6.9,349.56,8.099999,626.8]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",7.4,14.8,7.4,23.35,7.5,31.1,7.7,30.8,6.9,4.74,6.9,8.35,6.9,13.49,6.9,22.04,7,29.68,7,29.68,7.1,108.39,7,179.01,7,244.15,7,355.6,8.2,634.8]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",7.5,15.02,7.5,23.62,7.6,31.45,7.8,31.2,7,4.77,7,8.38,7,13.65,7,22.3,7.1,29.91,7.1,29.91,7.2,110,7.1,181.37,7.1,249.23,7.1,360,8.3,644.2]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",7.6,15.24,7.6,23.87,7.7,31.8,7.9,31.6,"-","-","-","-",7.1,13.78,7.1,22.55,7.2,30.15,7.2,30.15,7.3,111.6,7.2,183.65,7.2,254.26,7.2,365.06,8.4,651.6]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",7.7,15.46,7.7,24.1,7.8,32.1,8,32,"-","-","-","-",7.2,13.92,7.2,22.79,7.3,30.4,7.3,30.4,7.4,113,7.3,185.85,7.3,259.25,7.3,370.13,8.5,660]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",7.8,15.68,7.8,24.35,7.9,32.45,8.099999,32.3,"-","-","-","-",7.3,14.06,7.3,23.03,7.4,30.64,7.4,30.64,7.5,114.5,7.4,187.96,7.4,264.19,7.4,375.15,8.599999,672.8]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",7.9,15.9,7.9,24.58,8,32.73,8.2,32.6,"-","-","-","-",7.4,14.18,7.4,23.26,7.5,30.88,7.5,30.88,7.6,116.13,7.5,190.04,7.5,268.15,7.5,382,8.7,685.2]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",8,16.11,8,24.82,8.1,33.15,8.3,32.9,"-","-","-","-",7.5,14.3,7.5,23.47,7.6,31.11,7.6,31.11,7.7,117.78,7.6,192.37,7.6,273.95,7.6,385.04,8.8,698.7]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",8.1,16.33,8.1,24.95,8.2,33.55,8.4,33.2,"-","-","-","-",7.6,14.42,7.6,23.7,7.7,31.33,7.7,31.33,7.8,119.27,7.7,194.66,7.7,278.77,7.7,389.33,8.9,711.6]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",8.2,16.55,8.2,25.07,8.3,33.9,8.5,33.5,"-","-","-","-",7.7,14.54,7.7,23.91,7.8,31.57,7.8,31.57,7.9,120.74,7.8,196.85,7.8,283.55,7.8,394.2,9,724.5]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",8.3,16.77,8.3,25.2,8.4,34.3,8.599999,33.8,"-","-","-","-",7.8,14.65,7.8,24.11,7.9,31.79,7.9,31.79,8,122.2,7.9,198.96,7.9,287.96,7.9,399.54,9.099999,731.4]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",8.4,16.98,8.4,25.32,8.5,34.7,8.7,34.1,"-","-","-","-",7.9,14.76,7.9,24.31,8,32,8,32,"-","-",8,201,8,293,8,404.3,9.2,738.2]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",8.5,17.17,8.5,25.45,8.6,35.1,8.8,34.4,"-","-","-","-",8,14.86,8,24.51,8.099999,32.22,8.099999,32.22,"-","-","-","-","-","-","-","-",9.3,744.9]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",8.6,17.36,8.6,25.57,8.7,35.5,8.9,34.7,"-","-","-","-",8.099999,14.97,8.099999,24.64,8.2,32.44,8.2,32.44,"-","-","-","-","-","-","-","-",9.4,751.7]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",8.7,17.57,8.7,25.7,8.8,35.9,9,35,"-","-","-","-",8.2,15.1,8.2,24.78,8.3,32.65,8.3,32.65,"-","-","-","-","-","-","-","-",9.5,758.5]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",8.8,17.78,8.8,25.83,8.9,36.3,9.099999,35.5,"-","-","-","-",8.3,15.2,8.3,24.9,8.4,32.86,8.4,32.86,"-","-","-","-","-","-","-","-",9.599999,760.6]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",8.9,17.98,8.9,25.96,9,36.68,9.2,36,"-","-","-","-",8.4,15.31,8.4,25.03,8.5,33.06,8.5,33.06,"-","-","-","-","-","-","-","-",9.7,762.7]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",9,18.18,9,26.09,9.1,37,9.3,36.5,"-","-","-","-",8.5,15.42,8.5,25.16,8.599999,33.27,8.599999,33.27,"-","-","-","-","-","-","-","-",9.8,764.8]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",9.1,18.35,9.1,26.24,9.2,37.25,9.4,37,"-","-","-","-",8.599999,15.53,8.599999,25.29,8.7,33.47,8.7,33.47,"-","-","-","-","-","-","-","-",9.9,766.9]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",9.2,18.5,9.2,26.38,9.3,37.5,9.5,37.5,"-","-","-","-",8.7,15.64,8.7,25.41,8.8,33.67,8.8,33.67,"-","-","-","-","-","-","-","-",10,769]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",9.3,18.65,9.3,26.52,9.4,37.75,9.599999,38,"-","-","-","-",8.8,15.75,8.8,25.53,8.9,33.87,8.9,33.87,"-","-","-","-","-","-","-","-",10.099999,771.2]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",9.4,18.8,9.4,26.66,9.5,37.95,9.7,38.5,"-","-","-","-",8.9,15.86,8.9,25.65,9,34.06,9,34.06,"-","-","-","-","-","-","-","-",10.2,773.4]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",9.5,18.93,9.5,26.8,9.6,38.15,9.8,39,"-","-","-","-",9,15.97,9,25.77,9.099999,34.25,9.099999,34.25,"-","-","-","-","-","-","-","-",10.3,775.6]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",9.6,19.05,9.6,26.94,9.7,38.35,9.9,39.5,"-","-","-","-",9.099999,16.08,9.099999,25.89,9.2,34.44,9.2,34.44,"-","-","-","-","-","-","-","-",10.4,778]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",9.7,19.15,9.7,27.08,9.8,38.5,10,40,"-","-","-","-",9.2,16.2,9.2,26,9.3,34.69,9.3,34.69,"-","-","-","-","-","-","-","-",10.5,780]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",9.8,19.25,9.8,27.22,9.9,38.65,10.099999,40.5,"-","-","-","-",9.3,16.3,9.3,26.12,9.4,34.82,9.4,34.82,"-","-","-","-","-","-","-","-",10.599999,782]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",9.9,19.35,9.9,27.37,10,38.78,10.2,41,"-","-","-","-",9.4,16.41,9.4,26.23,9.5,35,9.5,35,"-","-","-","-","-","-","-","-",10.7,784]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",10,19.45,10,27.51,"-","-",10.3,41.5,"-","-","-","-",9.5,16.53,9.5,26.34,9.599999,35.2,9.599999,35.2,"-","-","-","-","-","-","-","-",10.8,786]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",10.4,42,"-","-","-","-",9.599999,16.64,9.599999,26.45,9.7,35.4,9.7,35.4,"-","-","-","-","-","-","-","-",10.9,788]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",10.5,42.5,"-","-","-","-",9.7,16.75,9.7,26.56,9.8,35.6,9.8,35.6,"-","-","-","-","-","-","-","-",11,790]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",10.599999,43,"-","-","-","-",9.8,16.86,9.8,26.67,9.9,35.8,9.9,35.8,"-","-","-","-","-","-","-","-",11.099999,792.2]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",10.7,43.5,"-","-","-","-",9.9,16.97,9.9,26.77,10,36,10,36,"-","-","-","-","-","-","-","-",11.2,794.5]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",10.8,44,"-","-","-","-",10,17.08,10,26.88,"-","-","-","-","-","-","-","-","-","-","-","-",11.3,796.8]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",10.9,44.5,"-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",11.4,799.1]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",11,45,"-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",11.5,801.4]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",11.099999,45.5,"-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",11.599999,804]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",11.2,46,"-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",11.7,806.6]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",11.3,46.5,"-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",11.8,809.2]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",11.4,47,"-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",11.9,812]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",11.5,47.5,"-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",12,814.5]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",11.599999,48,"-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",11.7,48.5,"-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",11.8,49,"-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",11.9,49.5,"-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",12,50,"-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-",{"$nulls":12},"-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",{"$nulls":8},"-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-",{"$nulls":12},"-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",{"$nulls":8},"-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-",{"$nulls":12},"-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",{"$nulls":8},"-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-",{"$nulls":12},"-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",{"$nulls":8},"-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-",{"$nulls":12},"-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",{"$nulls":8},"-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
[{"$nulls":32},6.8,13.45,6.8,21.85,6.9,29.1,7.1,28.8]
[{"$nulls":32},6.9,13.68,6.9,22.15,7,29.41,7.2,29.1]
[{"$nulls":32},7,13.91,7,22.45,7.1,29.75,7.3,29.4]
[{"$nulls":32},7.1,14.13,7.1,22.7,7.2,30.1,7.4,29.7]
[{"$nulls":32},7.2,14.35,7.2,22.95,7.3,30.4,7.5,30]
[{"$nulls":32},7.3,14.57,7.3,23.15,7.4,30.75,7.6,30.4]
[{"$nulls":32},7.4,14.8,7.4,23.35,7.5,31.1,7.7,30.8]
[{"$nulls":32},7.5,15.02,7.5,23.62,7.6,31.45,7.8,31.2]
[{"$nulls":32},7.6,15.24,7.6,23.87,7.7,31.8,7.9,31.6]
[{"$nulls":32},7.7,15.46,7.7,24.1,7.8,32.1,8,32]
[{"$nulls":12},"Hycocon VTZ, ATZ , DN15",null,"Hycocon VTZ,ATZ , DN20",null,"Hycocon VTZ,ATZ , DN25",null,"Hycocon VTZ,ATZ , DN32",null,"Hycocon VTZ,ATZ , DN40",null,"Hycocon VTZ,ATZ , DN50",{"$nulls":9},7.8,15.68,7.8,24.35,7.9,32.45,8.099999,32.3]
[{"$nulls":12},"Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.",{"$nulls":9},7.9,15.9,7.9,24.58,8,32.73,8.2,32.6]
[{"$nulls":12},"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",{"$nulls":9},8,16.11,8,24.82,8.099999,33.15,8.3,32.9]
[{"$nulls":12},0.3,0.11,0.3,0.13,0.3,0.16,0.4,0.48,0.4,0.67,0.3,{"$nulls":9},8.099999,16.33,8.099999,24.95,8.2,33.55,8.4,33.2]
[{"$nulls":12},0.4,0.23,0.4,0.25,0.4,0.27,0.5,0.7,0.5,0.95,0.4,{"$nulls":9},8.2,16.55,8.2,25.07,8.3,33.9,8.5,33.5]
[{"$nulls":12},0.5,0.34,0.5,0.36,0.5,0.39,0.6,0.85,0.6,1.17,0.5,{"$nulls":9},8.3,16.77,8.3,25.2,8.4,34.3,8.599999,33.8]
[{"$nulls":12},0.6,0.45,0.6,0.48,0.6,0.51,0.7,1.1,0.7,1.41,0.6,{"$nulls":9},8.4,16.98,8.4,25.32,8.5,34.7,8.7,34.1]
[{"$nulls":12},0.7,0.55,0.7,0.6,0.7,0.63,0.8,1.3,0.8,1.65,0.7,{"$nulls":9},8.5,17.17,8.5,25.45,8.599999,35.1,8.8,34.4]
[{"$nulls":12},0.8,0.66,0.8,0.72,0.8,0.75,0.9,1.52,0.9,1.88,0.8,{"$nulls":9},8.599999,17.36,8.599999,25.57,8.7,35.5,8.9,34.7]
[{"$nulls":12},0.9,0.76,0.9,0.84,0.9,0.87,1,1.7,1,2.1,0.9,{"$nulls":9},8.7,17.57,8.7,25.7,8.8,35.9,9,35]
[{"$nulls":12},1,0.86,1,0.94,1,1,1.1,1.9,1.1,2.33,1,{"$nulls":9},8.8,17.78,8.8,25.83,8.9,36.3,9.099999,35.5]
[{"$nulls":12},1.1,0.97,1.1,1.02,1.1,1.1,1.2,2.1,1.2,2.56,1.1,{"$nulls":9},8.9,17.98,8.9,25.96,9,36.68,9.2,36]
[{"$nulls":12},1.2,1.03,1.2,1.1,1.2,1.2,1.3,2.3,1.3,2.8,1.2,{"$nulls":9},9,18.18,9,26.09,9.099999,37,9.3,36.5]
[{"$nulls":12},1.3,1.1,1.3,1.2,1.3,1.3,1.4,2.5,1.4,3.05,1.3,{"$nulls":9},9.099999,18.35,9.099999,26.24,9.2,37.25,9.4,37]
[{"$nulls":12},1.4,1.16,1.4,1.3,1.4,1.4,1.5,2.7,1.5,3.3,1.4,{"$nulls":9},9.2,18.5,9.2,26.38,9.3,37.5,9.5,37.5]
[{"$nulls":12},1.5,1.22,1.5,1.4,1.5,1.5,1.6,2.85,1.6,3.57,1.5,{"$nulls":9},9.3,18.65,9.3,26.52,9.4,37.75,9.599999,38]
[{"$nulls":12},1.6,1.26,1.6,1.51,1.6,1.6,1.7,3.01,1.7,3.9,1.6,{"$nulls":9},9.4,18.8,9.4,26.66,9.5,37.95,9.7,38.5]
[{"$nulls":12},1.7,1.31,1.7,1.62,1.7,1.7,1.8,3.2,1.8,4.25,1.7,{"$nulls":9},9.5,18.93,9.5,26.8,9.599999,38.15,9.8,39]
[{"$nulls":12},1.8,1.36,1.8,1.68,1.8,1.8,1.9,3.4,1.9,4.55,1.8,{"$nulls":9},9.599999,19.05,9.599999,26.94,9.7,38.35,9.9,39.5]
[{"$nulls":12},1.9,1.41,1.9,1.74,1.9,1.9,2,3.6,2,4.8,1.9,{"$nulls":9},9.7,19.15,9.7,27.08,9.8,38.5,10,40]
[{"$nulls":12},2,1.46,2,1.8,2,2,2.1,3.81,2.1,5.01,2,{"$nulls":9},9.8,19.25,9.8,27.22,9.9,38.65,10.099999,40.5]
[{"$nulls":12},2.1,1.5,2.1,1.86,2.1,2.1,2.2,4.02,2.2,5.2,2.1,{"$nulls":9},9.9,19.35,9.9,27.37,10,38.78,10.2,41]
[{"$nulls":12},2.2,1.53,2.2,1.93,2.2,2.21,2.3,4.22,2.3,5.41,2.2,{"$nulls":9},10,19.45,10,27.51,null,null,10.3,41.5]
[{"$nulls":12},2.3,1.55,2.3,1.99,2.3,2.31,2.4,4.33,2.4,5.64,2.3,{"$nulls":15},10.4,42]
[{"$nulls":12},2.4,1.57,2.4,2.05,2.4,2.41,2.5,4.6,2.5,5.9,2.4,{"$nulls":15},10.5,42.5]
[{"$nulls":12},2.5,1.58,2.5,2.1,2.5,2.5,2.6,4.76,2.6,6.15,2.5,{"$nulls":15},10.599999,43]
[{"$nulls":12},2.6,1.59,2.6,2.14,2.6,2.58,2.7,4.9,2.7,6.38,2.6,{"$nulls":15},10.7,43.5]
[{"$nulls":12},2.7,1.6,2.7,2.18,2.7,2.64,2.8,5,2.8,6.6,2.7,{"$nulls":15},10.8,44]
[{"$nulls":12},2.8,1.61,2.8,2.21,2.8,2.7,2.9,5.15,2.9,6.8,2.8,{"$nulls":15},10.9,44.5]
[{"$nulls":12},2.9,1.62,2.9,2.23,2.9,2.75,3,5.25,3,7,2.9,{"$nulls":15},11,45]
[{"$nulls":12},3,1.63,3,2.25,3,2.8,3.5,5.69,3.5,7.85,3,{"$nulls":15},11.099999,45.5]
[{"$nulls":12},3.5,1.65,3.5,2.33,3.5,2.98,4,6,4,8.4,3.5,{"$nulls":15},11.2,46]
[{"$nulls":12},4,1.66,4,2.4,4,3.1,4.5,6.18,4.5,8.8,4,{"$nulls":15},11.3,46.5]
[{"$nulls":12},4.5,1.67,4.5,2.47,4.5,3.2,5,6.3,5,9.1,4.5,{"$nulls":15},11.4,47]
[{"$nulls":12},5,1.68,5,2.55,5,3.3,5.5,6.4,5.5,9.35,5,{"$nulls":15},11.5,47.5]
[{"$nulls":12},5.5,1.69,5.5,2.63,5.5,3.43,6,6.5,6,9.5,5.5,{"$nulls":15},11.599999,48]
[{"$nulls":12},6,1.7,6,2.7,6,3.6,6.5,6.58,6.5,9.65,6,{"$nulls":15},11.7,48.5]
[{"$nulls":12},6.5,"-",6.5,"-",6.5,"-",7,6.65,7,9.8,6.5,{"$nulls":15},11.8,49]
[{"$nulls":12},7,"-",7,"-",7,"-",7.5,6.72,7.5,9.9,7,{"$nulls":15},11.9,49.5]
[{"$nulls":12},7.5,"-",7.5,"-",7.5,"-",8,6.8,8,10,7.5,{"$nulls":15},12,50]
[1,{"$nulls":11},8,"-",8,"-",8,"-","-","-","-","-",8]
[{"$nulls":12},"-","-","-","-","-","-","-","-","-","-","-"]
["AV6 , DN15",null,"AV6 , DN20",null,"AV6 , DN25",null,"Combi 2,3  - внутр рез, DN10",null,"Combi 2,3  - внутр рез, DN15",null,"Combi 2,3  - внутр рез, DN20",null,"-","-","-","-","-","-","-","-","-","-","-",null,"Hydrocontrol VTR , DN10",null,"Hydrocontrol VTR , DN15",null,"Hydrocontrol VTR , DN20",null,"Hydrocontrol VTR , DN25",null,"Hydrocontrol VTR , DN32",null,"Hydrocontrol VTR , DN40",null,"Hydrocontrol VTR , DN50",null,"Hycocon VTZ, ATZ , DN15",null,"Hycocon VTZ,ATZ , DN20",null,"Hycocon VTZ,ATZ , DN25",null,"Hycocon VTZ,ATZ , DN32",null,"Hycocon VTZ,ATZ , DN40",null,"Hycocon VTZ,ATZ , DN50"]
["Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","-","-","-","-","-","-","-","-","-","-","-",null,"Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред."]
["настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"-","-","-","-","-","-","-","-","-","-","-",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка"]
[1,0.027,1,0.055,1,0.1075,0.25,0.06,0.25,0.06,0.25,0.06,"-","-","-","-","-","-","-","-","-","-","-",null,0.25,0.21,0.25,0.23,0.25,0.35,0.25,0.57,0.25,0.57,0.25,1.2,0.5,2.69,1,7,"-",0,"-",0,"-",0,"-",0,"-"]
[2,0.056,2,0.17,2,0.38375,0.5,0.126,0.5,0.126,0.5,0.126,"-","-","-","-","-","-","-","-","-","-","-",null,0.5,0.34,0.5,0.34,0.5,0.5,0.5,0.93,0.5,1.03,0.5,2.66,0.75,4.17,1.1,7.3,"-",0,"-",0,"-",0,"-",0,"-"]
[3,0.171,3,0.313,3,0.5792499999999998,0.75,0.19,0.75,0.19,0.75,0.19,"-","-","-","-","-","-","-","-","-","-","-",null,0.75,0.4,0.75,0.4,0.75,0.63,0.75,1.22,0.75,1.53,0.75,3.54,1,5.06,1.2,7.6,"-",0,"-",0,"-",0,"-",0,"-"]
[4,0.314,4,0.446,4,0.6934999999999998,1,0.25,1,0.25,1,0.25,"-","-","-","-","-","-","-","-","-","-","-",null,1,0.46,1,0.46,1,0.72,1,1.52,1,2.06,1,4.13,1.1,5.5,1.3,7.9,0,0,0,0,0,0,0,0,0]
[5,0.447,5,0.56,5,0.771875,1.5,0.42,1.5,0.42,1.5,0.42,"-","-","-","-","-","-","-","-","-","-","-",null,1.1,0.48,1.1,0.48,1.1,0.76,1.1,1.64,1.1,2.2,1.1,4.46,1.2,5.95,1.4,8.2,"-","-","-","-","-","-","-","-","-"]
[6,0.57,6,0.65,6,0.8,2,0.819,2,0.819,2,0.819,"-","-","-","-","-","-","-","-","-","-","-",null,1.2,0.5,1.2,0.5,1.2,0.81,1.2,1.76,1.2,2.35,1.2,4.78,1.3,6.35,1.5,8.5,0.25,0.11,0.25,0.51,0.25,0.4,0.25,0.89,0.5]
["-","-","-","-","-","-",3,1.236,3,1.236,3,1.236,"-","-","-","-","-","-","-","-","-","-","-",null,1.3,0.52,1.3,0.52,1.3,0.85,1.3,1.87,1.3,2.52,1.3,5.1,1.4,6.75,1.6,8.8,0.5,0.22,0.5,0.83,0.5,0.83,0.5,1.67,0.75]
["-","-","-","-","-","-",4,1.7,4,1.7,4,1.7,"-","-","-","-","-","-","-","-","-","-","-",null,1.4,0.54,1.4,0.55,1.4,0.89,1.4,1.98,1.4,2.7,1.4,5.42,1.5,7.15,1.7,9.1,0.75,0.33,0.75,1.08,0.75,1.25,0.75,2.49,1]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,1.5,0.56,1.5,0.57,1.5,0.93,1.5,2.08,1.5,2.9,1.5,5.74,1.6,7.55,1.8,9.4,1,0.42,1,1.33,1,1.73,1,3.27,1.1]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,1.6,0.58,1.6,0.6,1.6,0.97,1.6,2.18,1.6,3.1,1.6,6.06,1.7,7.95,1.9,9.7,1.1,0.48,1.1,1.43,1.1,1.92,1.1,3.58,1.2]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,1.7,0.6,1.7,0.63,1.7,1.01,1.7,2.28,1.7,3.32,1.7,6.38,1.8,8.4,2,10,1.2,0.52,1.2,1.53,1.2,2.11,1.2,3.85,1.3]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,1.8,0.63,1.8,0.66,1.8,1.05,1.8,2.38,1.8,3.55,1.8,6.7,1.9,8.8,2.1,10.4,1.3,0.55,1.3,1.63,1.3,2.3,1.3,4.18,1.4]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,1.9,0.65,1.9,0.69,1.9,1.1,1.9,2.48,1.9,3.78,1.9,7.02,2,9.17,2.2,10.8,1.4,0.59,1.4,1.73,1.4,2.49,1.4,4.48,1.5]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,2,0.67,2,0.72,2,1.14,2,2.58,2,4.02,2,7.34,2.1,9.65,2.3,11.2,1.5,0.63,1.5,1.83,1.5,2.68,1.5,4.77,1.6]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,2.1,0.7,2.1,0.76,2.1,1.18,2.1,2.67,2.1,4.25,2.1,7.62,2.2,10.15,2.4,11.6,1.6,0.67,1.6,1.94,1.6,2.87,1.6,5.06,1.7]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,2.2,0.73,2.2,0.8,2.2,1.22,2.2,2.77,2.2,4.48,2.2,7.89,2.3,10.65,2.5,12,1.7,0.7,1.7,2.04,1.7,3.06,1.7,5.35,1.8]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,2.3,0.76,2.3,0.85,2.3,1.26,2.3,2.87,2.3,4.68,2.3,8.16,2.4,11.15,2.6,12.4,1.8,0.75,1.8,2.14,1.8,3.25,1.8,5.64,1.9]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,2.4,0.79,2.4,0.91,2.4,1.3,2.4,2.98,2.4,4.88,2.4,8.43,2.5,11.65,2.7,12.8,1.9,0.79,1.9,2.24,1.9,3.44,1.9,5.92,2]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,2.5,0.83,2.5,0.98,2.5,1.35,2.5,3.09,2.5,5.08,2.5,8.7,2.6,12.15,2.8,13.2,2,0.83,2,2.34,2,3.63,2,6.2,2.1]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,2.6,0.87,2.6,1.05,2.6,1.4,2.6,3.2,2.6,5.25,2.6,8.97,2.7,12.65,2.9,13.6,2.1,0.87,2.1,2.44,2.1,3.82,2.1,6.43,2.2]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,2.7,0.91,2.7,1.12,2.7,1.45,2.7,3.31,2.7,5.45,2.7,9.24,2.8,13.2,3,14,2.2,0.91,2.2,2.53,2.2,4.01,2.2,6.67,2.3]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,2.8,0.96,2.8,1.2,2.8,1.5,2.8,3.43,2.8,5.65,2.8,9.51,2.9,13.7,3.1,14.3,2.3,0.95,2.3,2.63,2.3,4.2,2.3,6.9,2.4]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,2.9,1.03,2.9,1.27,2.9,1.55,2.9,3.56,2.9,5.83,2.9,9.77,3,14.23,3.2,14.6,2.4,0.99,2.4,2.73,2.4,4.39,2.4,7.15,2.5]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,3,1.1,3,1.34,3,1.6,3,3.69,3,6,3,10.02,3.1,14.65,3.3,14.9,2.5,1.04,2.5,2.83,2.5,4.58,2.5,7.39,2.6]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,3.1,1.16,3.1,1.41,3.1,1.66,3.1,3.82,3.1,6.17,3.1,10.25,3.2,15.1,3.4,15.2,2.6,1.08,2.6,2.93,2.6,4.77,2.6,7.64,2.7]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,3.2,1.23,3.2,1.48,3.2,1.74,3.2,3.96,3.2,6.35,3.2,10.5,3.3,15.5,3.5,15.5,2.7,1.12,2.7,3.03,2.7,4.96,2.7,7.89,2.8]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,3.3,1.29,3.3,1.55,3.3,1.82,3.3,4.11,3.3,6.52,3.3,10.73,3.4,15.95,3.6,15.8,2.8,1.16,2.8,3.12,2.8,5.15,2.8,8.14,2.9]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,3.4,1.36,3.4,1.62,3.4,1.93,3.4,4.26,3.4,6.7,3.4,10.97,3.5,16.35,3.7,16.1,2.9,1.2,2.9,3.22,2.9,5.34,2.9,8.39,3]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,3.5,1.42,3.5,1.7,3.5,2.04,3.5,4.42,3.5,6.85,3.5,11.2,3.6,16.8,3.8,16.4,3,1.25,3,3.32,3,5.53,3,8.69,3.1]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,3.6,1.49,3.6,1.77,3.6,2.15,3.6,4.57,3.6,7,3.6,11.43,3.7,17.25,3.9,16.7,3.1,1.3,3.1,3.45,3.1,5.73,3.1,8.91,3.2]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,3.7,1.56,3.7,1.84,3.7,2.25,3.7,4.72,3.7,7.16,3.7,11.66,3.8,17.65,4,17,3.2,1.35,3.2,3.58,3.2,5.92,3.2,9.17,3.3]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,3.8,1.62,3.8,1.91,3.8,2.36,3.8,4.87,3.8,7.33,3.8,11.9,3.9,18.1,4.1,17.5,3.3,1.41,3.3,3.7,3.3,6.12,3.3,9.43,3.4]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,3.9,1.69,3.9,1.98,3.9,2.47,3.9,5.02,3.9,7.49,3.9,12.13,4,18.5,4.2,18,3.4,1.47,3.4,3.84,3.4,6.31,3.4,9.69,3.5]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,4,1.76,4,2.05,4,2.58,4,5.16,4,7.64,4,12.36,4.1,19,4.3,18.5,3.5,1.54,3.5,3.98,3.5,6.51,3.5,9.97,3.6]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,4.1,1.82,4.1,2.12,4.1,2.69,4.1,5.32,4.1,7.85,4.1,12.65,4.2,19.45,4.4,19,3.6,1.61,3.6,4.13,3.6,6.71,3.6,10.25,3.7]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,4.2,1.88,4.2,2.18,4.2,2.8,4.2,5.47,4.2,8.05,4.2,12.95,4.3,19.85,4.5,19.5,3.7,1.7,3.7,4.27,3.7,6.9,3.7,10.52,3.8]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,4.3,1.94,4.3,2.24,4.3,2.91,4.3,5.63,4.3,8.25,4.3,13.25,4.4,20.3,4.6,20,3.8,1.79,3.8,4.42,3.8,7.1,3.8,10.8,3.9]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,4.4,2,4.4,2.31,4.4,3.01,4.4,5.79,4.4,8.45,4.4,13.52,4.5,20.7,4.7,20.5,3.9,1.89,3.9,4.58,3.9,7.3,3.9,11.09,4]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,4.5,2.06,4.5,2.38,4.5,3.12,4.5,5.95,4.5,8.65,4.5,13.8,4.6,21.15,4.8,21,4,2,4,4.74,4,7.46,4,11.38,4.1]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,4.6,2.12,4.6,2.44,4.6,3.23,4.6,6.1,4.6,8.85,4.6,14.1,4.7,21.6,4.9,21.5,4.1,2.11,4.1,4.9,4.1,7.69,4.1,11.67,4.2]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,4.7,2.19,4.7,2.51,4.7,3.34,4.7,6.26,4.7,9.05,4.7,14.4,4.8,22.05,5,22,4.2,2.22,4.2,5.07,4.2,7.88,4.2,11.97,4.3]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,4.8,2.25,4.8,2.57,4.8,3.44,4.8,6.42,4.8,9.25,4.8,14.7,4.9,22.5,5.1,22.4,4.3,2.33,4.3,5.24,4.3,8.08,4.3,12.27,4.4]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,4.9,2.31,4.9,2.63,4.9,3.55,4.9,6.57,4.9,9.47,4.9,14.98,5,22.93,5.2,22.8,4.4,2.43,4.4,5.42,4.4,8.27,4.4,12.58,4.5]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,5,2.37,5,2.7,5,3.65,5,6.72,5,9.69,5,15.26,5.1,23.25,5.3,23.2,4.5,2.54,4.5,5.6,4.5,8.47,4.5,12.89,4.6]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,5.1,2.42,5.1,2.77,5.1,3.78,5.1,6.84,5.1,9.9,5.1,15.65,5.2,23.57,5.4,23.6,4.6,2.65,4.6,5.8,4.6,8.67,4.6,13.2,4.7]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,5.2,2.47,5.2,2.84,5.2,3.9,5.2,6.96,5.2,10.1,5.2,16.1,5.3,23.9,5.5,24,4.7,2.76,4.7,6,4.7,8.86,4.7,13.52,4.8]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,5.3,2.52,5.3,2.92,5.3,4.02,5.3,7.08,5.3,10.3,5.3,16.55,5.4,24.2,5.6,24.4,4.8,2.87,4.8,6.2,4.8,9.06,4.8,13.84,4.9]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,5.4,2.56,5.4,2.99,5.4,4.15,5.4,7.2,5.4,10.5,5.4,16.95,5.5,24.5,5.7,24.8,4.9,2.98,4.9,6.42,4.9,9.25,4.9,14.17,5]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,5.5,2.6,5.5,3.06,5.5,4.27,5.5,7.32,5.5,10.7,5.5,17.35,5.6,24.8,5.8,25.2,5,3.09,5,6.64,5,9.45,5,14.51,5.1]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,5.6,2.63,5.6,3.13,5.6,4.4,5.6,7.44,5.6,10.9,5.6,17.8,5.7,25.15,5.9,25.6,5.1,3.19,5.1,6.85,5.1,9.68,5.1,14.91,5.2]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,5.7,2.66,5.7,3.2,5.7,4.52,5.7,7.56,5.7,11.1,5.7,18.2,5.8,25.45,6,26,5.2,3.3,5.2,7.03,5.2,9.92,5.2,15.32,5.3]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,5.8,2.69,5.8,3.27,5.8,4.65,5.8,7.68,5.8,11.3,5.8,18.65,5.9,25.8,6.1,26.3,5.3,3.41,5.3,7.18,5.3,10.15,5.3,15.75,5.4]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,5.9,2.72,5.9,3.34,5.9,4.77,5.9,7.8,5.9,11.5,5.9,19.05,6,26.09,6.2,26.6,5.4,3.52,5.4,7.32,5.4,10.35,5.4,16.14,5.5]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,6,2.75,6,3.4,6,4.89,6,7.91,6,11.7,6,19.45,6.1,26.45,6.3,26.9,5.5,3.63,5.5,7.44,5.5,10.6,5.5,16.62,5.6]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,6.1,2.77,6.1,3.47,6.1,5.02,6.1,8.02,6.1,11.9,6.1,19.75,6.2,26.8,6.4,27.2,5.6,3.74,5.6,7.55,5.6,10.83,5.6,17.1,5.7]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,6.2,2.79,6.2,3.54,6.2,5.15,6.2,8.12,6.2,12.12,6.2,20.05,6.3,27.1,6.5,27.5,5.7,3.84,5.7,7.65,5.7,11.05,5.7,17.58,5.8]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,6.3,2.81,6.3,3.61,6.3,5.28,6.3,8.22,6.3,12.35,6.3,20.35,6.4,27.45,6.6,27.7,5.8,3.95,5.8,7.74,5.8,11.27,5.8,18.07,5.9]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,6.4,2.83,6.4,3.67,6.4,5.36,6.4,8.31,6.4,12.57,6.4,20.65,6.5,27.75,6.7,27.9,5.9,4.06,5.9,7.82,5.9,11.48,5.9,18.59,6]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,6.5,2.84,6.5,3.72,6.5,5.44,6.5,8.41,6.5,12.8,6.5,20.95,6.6,28.05,6.8,28.1,6,4.17,6,7.9,6,11.7,6,19.13,6.1]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,6.6,2.85,6.6,3.76,6.6,5.5,6.6,8.51,6.6,13,6.6,21.25,6.7,28.4,6.9,28.3,6.1,4.27,6.1,7.97,6.1,11.96,6.1,19.53,6.2]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,6.7,2.86,6.7,3.79,6.7,5.56,6.7,8.61,6.7,13.22,6.7,21.55,6.8,28.75,7,28.5,6.2,4.35,6.2,8.03,6.2,12.2,6.2,19.9,6.3]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,6.8,2.87,6.8,3.82,6.8,5.61,6.8,8.71,6.8,13.45,6.8,21.85,6.9,29.1,7.1,28.8,6.3,4.43,6.3,8.09,6.3,12.41,6.3,20.25,6.4]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,6.9,2.87,6.9,3.85,6.9,5.66,6.9,8.8,6.9,13.68,6.9,22.15,7,29.41,7.2,29.1,6.4,4.5,6.4,8.15,6.4,12.62,6.4,20.59,6.5]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,7,2.88,7,3.88,7,5.71,7,8.89,7,13.91,7,22.45,7.1,29.75,7.3,29.4,6.5,4.56,6.5,8.2,6.5,12.81,6.5,20.9,6.6]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,"-","-","-","-","-","-","-","-",7.1,14.13,7.1,22.7,7.2,30.1,7.4,29.7,6.6,4.61,6.6,8.24,6.6,13,6.6,21.21,6.7]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,"-","-","-","-","-","-","-","-",7.2,14.35,7.2,22.95,7.3,30.4,7.5,30,6.7,4.66,6.7,8.28,6.7,13.17,6.7,21.5,6.8]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,"-","-","-","-","-","-","-","-",7.3,14.57,7.3,23.15,7.4,30.75,7.6,30.4,6.8,4.7,6.8,8.32,6.8,13.33,6.8,21.74,6.9]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,"-","-","-","-","-","-","-","-",7.4,14.8,7.4,23.35,7.5,31.1,7.7,30.8,6.9,4.74,6.9,8.35,6.9,13.49,6.9,22.04,7]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,"-","-","-","-","-","-","-","-",7.5,15.02,7.5,23.62,7.6,31.45,7.8,31.2,7,4.77,7,8.38,7,13.65,7,22.3,7.1]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,"-","-","-","-","-","-","-","-",7.6,15.24,7.6,23.87,7.7,31.8,7.9,31.6,"-","-","-","-",7.1,13.78,7.1,22.55,7.2]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,"-","-","-","-","-","-","-","-",7.7,15.46,7.7,24.1,7.8,32.1,8,32,"-","-","-","-",7.2,13.92,7.2,22.79,7.3]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,"-","-","-","-","-","-","-","-",7.8,15.68,7.8,24.35,7.9,32.45,8.099999,32.3,"-","-","-","-",7.3,14.06,7.3,23.03,7.4]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,"-","-","-","-","-","-","-","-",7.9,15.9,7.9,24.58,8,32.73,8.2,32.6,"-","-","-","-",7.4,14.18,7.4,23.26,7.5]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,"-","-","-","-","-","-","-","-",8,16.11,8,24.82,8.1,33.15,8.3,32.9,"-","-","-","-",7.5,14.3,7.5,23.47,7.6]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,"-","-","-","-","-","-","-","-",8.1,16.33,8.1,24.95,8.2,33.55,8.4,33.2,"-","-","-","-",7.6,14.42,7.6,23.7,7.7]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,"-","-","-","-","-","-","-","-",8.2,16.55,8.2,25.07,8.3,33.9,8.5,33.5,"-","-","-","-",7.7,14.54,7.7,23.91,7.8]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,"-","-","-","-","-","-","-","-",8.3,16.77,8.3,25.2,8.4,34.3,8.599999,33.8,"-","-","-","-",7.8,14.65,7.8,24.11,7.9]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,"-","-","-","-","-","-","-","-",8.4,16.98,8.4,25.32,8.5,34.7,8.7,34.1,"-","-","-","-",7.9,14.76,7.9,24.31,8]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,"-","-","-","-","-","-","-","-",8.5,17.17,8.5,25.45,8.6,35.1,8.8,34.4,"-","-","-","-",8,14.86,8,24.51,8.099999]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,"-","-","-","-","-","-","-","-",8.6,17.36,8.6,25.57,8.7,35.5,8.9,34.7,"-","-","-","-",8.099999,14.97,8.099999,24.64,8.2]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,"-","-","-","-","-","-","-","-",8.7,17.57,8.7,25.7,8.8,35.9,9,35,"-","-","-","-",8.2,15.1,8.2,24.78,8.3]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,"-","-","-","-","-","-","-","-",8.8,17.78,8.8,25.83,8.9,36.3,9.099999,35.5,"-","-","-","-",8.3,15.2,8.3,24.9,8.4]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,"-","-","-","-","-","-","-","-",8.9,17.98,8.9,25.96,9,36.68,9.2,36,"-","-","-","-",8.4,15.31,8.4,25.03,8.5]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,"-","-","-","-","-","-","-","-",9,18.18,9,26.09,9.1,37,9.3,36.5,"-","-","-","-",8.5,15.42,8.5,25.16,8.599999]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,"-","-","-","-","-","-","-","-",9.1,18.35,9.1,26.24,9.2,37.25,9.4,37,"-","-","-","-",8.599999,15.53,8.599999,25.29,8.7]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,"-","-","-","-","-","-","-","-",9.2,18.5,9.2,26.38,9.3,37.5,9.5,37.5,"-","-","-","-",8.7,15.64,8.7,25.41,8.8]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,"-","-","-","-","-","-","-","-",9.3,18.65,9.3,26.52,9.4,37.75,9.599999,38,"-","-","-","-",8.8,15.75,8.8,25.53,8.9]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,"-","-","-","-","-","-","-","-",9.4,18.8,9.4,26.66,9.5,37.95,9.7,38.5,"-","-","-","-",8.9,15.86,8.9,25.65,9]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,"-","-","-","-","-","-","-","-",9.5,18.93,9.5,26.8,9.6,38.15,9.8,39,"-","-","-","-",9,15.97,9,25.77,9.099999]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,"-","-","-","-","-","-","-","-",9.6,19.05,9.6,26.94,9.7,38.35,9.9,39.5,"-","-","-","-",9.099999,16.08,9.099999,25.89,9.2]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,"-","-","-","-","-","-","-","-",9.7,19.15,9.7,27.08,9.8,38.5,10,40,"-","-","-","-",9.2,16.2,9.2,26,9.3]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,"-","-","-","-","-","-","-","-",9.8,19.25,9.8,27.22,9.9,38.65,10.099999,40.5,"-","-","-","-",9.3,16.3,9.3,26.12,9.4]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,"-","-","-","-","-","-","-","-",9.9,19.35,9.9,27.37,10,38.78,10.2,41,"-","-","-","-",9.4,16.41,9.4,26.23,9.5]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,"-","-","-","-","-","-","-","-",10,19.45,10,27.51,"-","-",10.3,41.5,"-","-","-","-",9.5,16.53,9.5,26.34,9.599999]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,"-","-","-","-","-","-","-","-","-","-","-","-","-","-",10.4,42,"-","-","-","-",9.599999,16.64,9.599999,26.45,9.7]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,"-","-","-","-","-","-","-","-","-","-","-","-","-","-",10.5,42.5,"-","-","-","-",9.7,16.75,9.7,26.56,9.8]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,"-","-","-","-","-","-","-","-","-","-","-","-","-","-",10.599999,43,"-","-","-","-",9.8,16.86,9.8,26.67,9.9]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,"-","-","-","-","-","-","-","-","-","-","-","-","-","-",10.7,43.5,"-","-","-","-",9.9,16.97,9.9,26.77,10]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,"-","-","-","-","-","-","-","-","-","-","-","-","-","-",10.8,44,"-","-","-","-",10,17.08,10,26.88,"-"]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,"-","-","-","-","-","-","-","-","-","-","-","-","-","-",10.9,44.5,"-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,"-","-","-","-","-","-","-","-","-","-","-","-","-","-",11,45,"-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,"-","-","-","-","-","-","-","-","-","-","-","-","-","-",11.099999,45.5,"-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,"-","-","-","-","-","-","-","-","-","-","-","-","-","-",11.2,46,"-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,"-","-","-","-","-","-","-","-","-","-","-","-","-","-",11.3,46.5,"-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,"-","-","-","-","-","-","-","-","-","-","-","-","-","-",11.4,47,"-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,"-","-","-","-","-","-","-","-","-","-","-","-","-","-",11.5,47.5,"-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,"-","-","-","-","-","-","-","-","-","-","-","-","-","-",11.599999,48,"-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,"-","-","-","-","-","-","-","-","-","-","-","-","-","-",11.7,48.5,"-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,"-","-","-","-","-","-","-","-","-","-","-","-","-","-",11.8,49,"-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,"-","-","-","-","-","-","-","-","-","-","-","-","-","-",11.9,49.5,"-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,"-","-","-","-","-","-","-","-","-","-","-","-","-","-",12,50,"-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,"-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,"-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,"-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,"-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,"-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,"-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,"-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,"-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,"-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",null,"-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-",0,0,0,0,0,0,0,0,0,0,0,null,"-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-",0,0,0,0,0,0,0,0,0,0,0,null,"-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-",0,0,0,0,0,0,0,0,0,0,0,null,"-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-",0,0,0,0,0,0,0,0,0,0,0,null,"-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-",0,0,0,0,0,0,0,0,0,0,0,null,"-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-",{"$nulls":12},"-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-",{"$nulls":12},"-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-",{"$nulls":12},"-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-",{"$nulls":12},"-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-",{"$nulls":12},"-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-",{"$nulls":12},"-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-",{"$nulls":12},"-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-",{"$nulls":12},"-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-",{"$nulls":12},"-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-",{"$nulls":12},"-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-",{"$nulls":12},"-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-",{"$nulls":12},"-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-",{"$nulls":12},"-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-",{"$nulls":12},"-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-",{"$nulls":12},"-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-",{"$nulls":12},"-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-",{"$nulls":12},"-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-",{"$nulls":12},"-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-",{"$nulls":12},"-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-",{"$nulls":12},"-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-",{"$nulls":12},"-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-",{"$nulls":12},"-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-",{"$nulls":12},"-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-",{"$nulls":12},"-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-",{"$nulls":12},"-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-",{"$nulls":12},"-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-",{"$nulls":12},"-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-",{"$nulls":12},"-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-",{"$nulls":12},"-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-",{"$nulls":12},"-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-",{"$nulls":12},"-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-",{"$nulls":12},"-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-",{"$nulls":12},"-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-",{"$nulls":12},"-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-",{"$nulls":12},"-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-",{"$nulls":12},"-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-",{"$nulls":12},"-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-",{"$nulls":12},"-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",0,0,0,0,0,0,0,0,"-"]
["-","-","-","-","-","-","-","-","-","-","-","-",{"$nulls":12},"-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",0,0,0,0,0,0,0,0,"-"]
["-","-","-","-","-","-","-","-","-","-","-","-",{"$nulls":12},"-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",0,0,0,0,0,0,0,0,"-"]
["-","-","-","-","-","-","-","-","-","-","-","-",{"$nulls":12},"-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",0,0,0,0,0,0,0,0,"-"]
["-","-","-","-","-","-","-","-","-","-","-","-",{"$nulls":12},"-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",0,0,0,0,0,0,0,0,"-"]

{"sheet":"сл_COMAP","index":8,"n_rows":172,"n_cols":44,"rows_kept":172,"cut":false,"hidden":true,"merged":[],"flags":["formulas_cached_only"]}
["м_н_COMAP (правило №1: все столбцы должны заканчиваться знаком \"-\")"]
["Comap750R - резьба, DN15",null,"Comap750R - резьба, DN20",null,"Comap750R - резьба, DN25",null,"Comap750 - резьба, DN10",null,"Comap750 - резьба, DN15",null,"Comap750 - резьба, DN20",null,"Comap750 - резьба, DN25",null,"Comap750 - резьба, DN32",null,"Comap750 - резьба, DN40",null,"Comap750 - резьба, DN50",null,"Comap751B - фланец, DN15",null,"Comap751B - фланец, DN20",null,"Comap751B - фланец, DN25",null,"Comap751B - фланец, DN32",null,"Comap751B - фланец, DN40",null,"Comap751B - фланец, DN50",null,"Comap751B - фланец, DN65",null,"Comap751B - фланец, DN80",null,"Comap751B - фланец, DN100",null,"Comap751B - фланец, DN125",null,"Comap751B - фланец, DN150",null,"Comap751B - фланец, DN200"]
["Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv"]
["настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка"]
[10,0.115,10,0.115,5,0.1,5,0.05,5,0.1,5,0.13,5,0.17,5,0.2,5,0.23,5,0.55,0.5,0.13,0.5,0.22,0.5,0.22,0.5,0.28,0.5,0.88,0.5,1.07,0.5,2.98,0.5,3.65,1.5,3.77,1.5,8.3,1.5,16.2,1.5,32.5]
[11,0.13,11,0.13,6,0.13,6,0.064,6,0.16,6,0.21,6,0.3,6,0.4,6,0.35,6,1.11,0.6,0.17,0.6,0.26,0.6,0.27,0.6,0.33,0.6,1.06,0.6,1.29,0.6,3.52,0.6,4.3,1.6,4.19,1.6,8.8,1.6,17.1,1.6,34.5]
[12,0.14,12,0.145,7,0.185,7,0.078,7,0.22,7,0.29,7,0.44,7,0.65,7,0.68,7,1.72,0.7,0.19,0.7,0.3,0.7,0.32,0.7,0.39,0.7,1.25,0.7,1.51,0.7,4.02,0.7,4.94,1.7,4.65,1.7,9.5,1.7,17.9,1.7,36.3]
[13,0.165,13,0.165,8,0.26,8,0.092,8,0.28,8,0.39,8,0.59,8,0.88,8,1.04,8,2.37,0.8,0.22,0.8,0.34,0.8,0.37,0.8,0.46,0.8,1.43,0.8,1.74,0.8,4.49,0.8,5.54,1.8,5.14,1.8,10.1,1.8,18.8,1.8,38.8]
[14,0.185,14,0.185,9,0.315,9,0.106,9,0.36,9,0.46,9,0.73,9,1.13,9,1.42,9,2.9,0.9,0.24,0.9,0.39,0.9,0.43,0.9,0.53,0.9,1.61,0.9,1.97,0.9,4.92,0.9,6.1,1.9,5.66,1.9,10.7,1.9,19.6,1.9,39.8]
[15,0.205,15,0.21,10,0.395,10,0.12,10,0.41,10,0.57,10,0.91,10,1.33,10,1.78,10,3.5,1,0.26,1,0.43,1,0.49,1,0.6,1,1.8,1,2.2,1,5.3,1,6.6,2,6.22,2,11.3,2,20.4,2,41.3]
[16,0.225,16,0.23,11,0.47,11,0.14,11,0.48,11,0.64,11,1.04,11,1.55,11,2.17,11,4.08,1.1,0.28,1.1,0.47,1.1,0.55,1.1,0.68,1.1,1.99,1.1,2.44,1.1,5.63,1.1,7.06,2.1,6.81,2.1,11.9,2.1,21.1,2.1,43]
[17,0.25,17,0.255,12,0.535,12,0.16,12,0.54,12,0.73,12,1.19,12,1.8,12,2.5,12,4.66,1.2,0.3,1.2,0.52,1.2,0.62,1.2,0.77,1.2,2.18,1.2,2.68,1.2,5.92,1.2,7.47,2.2,7.46,2.2,12.5,2.2,21.8,2.2,44.5]
[18,0.285,18,0.29,13,0.61,13,0.18,13,0.6,13,0.82,13,1.33,13,2.07,13,2.83,13,5.24,1.3,0.32,1.3,0.56,1.3,0.69,1.3,0.86,1.3,2.38,1.3,2.93,1.3,6.18,1.3,7.85,2.3,8.15,2.3,13.1,2.3,22.5,2.3,46]
[19,0.325,19,0.32,14,0.675,14,0.205,14,0.67,14,0.9,14,1.5,14,2.29,14,3.2,14,5.79,1.4,0.34,1.4,0.61,1.4,0.76,1.4,0.96,1.4,2.59,1.4,3.18,1.4,6.42,1.4,8.21,2.4,8.84,2.4,13.8,2.4,23.1,2.4,47.5]
[20,0.375,20,0.365,15,0.75,15,0.225,15,0.73,15,0.97,15,1.64,15,2.53,15,3.56,15,6.32,1.5,0.37,1.5,0.65,1.5,0.84,1.5,1.06,1.5,2.8,1.5,3.46,1.5,6.64,1.5,8.52,2.5,9.56,2.5,14.4,2.5,23.8,2.5,48.9]
[21,0.43,21,0.43,16,0.8,16,0.25,16,0.8,16,1.05,16,1.78,16,2.82,16,3.99,16,7,1.6,0.4,1.6,0.7,1.6,0.92,1.6,1.17,1.6,3.02,1.6,3.75,1.6,6.86,1.6,8.83,2.6,10.3,2.6,15.1,2.6,24.4,2.6,50.3]
[22,0.515,22,0.515,17,0.875,17,0.265,17,0.87,17,1.13,17,1.95,17,3.14,17,4.4,17,7.8,1.7,0.43,1.7,0.74,1.7,1.01,1.7,1.29,1.7,3.25,1.7,4.06,1.7,7.07,1.7,9.13,2.7,11.1,2.7,15.7,2.7,25,2.7,51.6]
[23,0.62,23,0.62,18,0.95,18,0.295,18,0.95,18,1.24,18,2.11,18,3.37,18,4.9,18,8.6,1.8,0.47,1.8,0.79,1.8,1.1,1.8,1.41,1.8,3.49,1.8,4.38,1.8,7.29,1.8,9.41,2.8,11.8,2.8,16.4,2.8,25.6,2.8,52.9]
[24,0.73,24,0.72,19,1.05,19,0.345,19,1.08,19,1.32,19,2.28,19,3.71,19,5.48,19,9.46,1.9,0.51,1.9,0.85,1.9,1.2,1.9,1.54,1.9,3.74,1.9,4.73,1.9,7.53,1.9,9.7,2.9,12.6,2.9,17,2.9,26.2,2.9,54.2]
[25,0.84,25,0.815,20,1.175,20,0.39,20,1.21,20,1.43,20,2.49,20,4.05,20,6.1,20,10.37,2,0.55,2,0.9,2,1.3,2,1.68,2,4,2,5.1,2,7.8,2,10,3,13.4,3,17.7,3,26.7,3,55.5]
[26,0.925,26,0.91,21,1.37,21,0.46,21,1.35,21,1.58,21,2.76,21,4.42,21,6.75,21,11.32,2.1,0.59,2.1,0.96,2.1,1.4,2.1,1.82,2.1,4.27,2.1,5.5,2.1,8.09,2.1,10.3,3.1,14.2,3.1,18.4,3.1,27.3,3.1,56.8]
[27,1.015,27,1.015,22,1.595,22,0.54,22,1.54,22,1.73,22,3.04,22,4.74,22,7.45,22,12.43,2.2,0.64,2.2,1.02,2.2,1.51,2.2,1.98,2.2,4.55,2.2,5.92,2.2,8.42,2.2,10.6,3.2,14.9,3.2,19,3.2,27.9,3.2,58.1]
[28,1.095,28,1.095,23,1.84,23,0.63,23,1.75,23,1.92,23,3.36,23,5.07,23,8.25,23,13.71,2.3,0.69,2.3,1.08,2.3,1.62,2.3,2.14,2.3,4.83,2.3,6.38,2.3,8.79,2.3,11,3.3,15.7,3.3,19.7,3.3,28.5,3.3,59.4]
[29,1.175,29,1.185,24,2.18,24,0.74,24,1.99,24,2.16,24,3.69,24,5.52,24,9.08,24,15.1,2.4,0.74,2.4,1.15,2.4,1.74,2.4,2.31,2.4,5.12,2.4,6.86,2.4,9.18,2.4,11.3,3.4,16.5,3.4,20.4,3.4,29,3.4,60.7]
[30,1.28,30,1.265,25,2.425,25,0.84,25,2.28,25,2.43,25,4.05,25,6.03,25,10.04,25,16.54,2.5,0.8,2.5,1.22,2.5,1.85,2.5,2.48,2.5,5.42,2.5,7.36,2.5,9.6,2.5,11.7,3.5,17.3,3.5,21.1,3.5,29.5,3.5,62.1]
[31,1.375,31,1.365,26,2.725,26,0.94,26,2.61,26,2.83,26,4.45,26,6.63,26,10.96,26,18.15,2.6,0.85,2.6,1.29,2.6,1.98,2.6,2.67,2.6,5.72,2.6,7.89,2.6,10,2.6,12.1,3.6,18.1,3.6,21.8,3.6,30.2,3.6,63.4]
[32,1.47,32,1.465,27,3.01,27,1.04,27,2.91,27,3.17,27,4.84,27,7.29,27,11.87,27,19.13,2.7,0.91,2.7,1.36,2.7,2.1,2.7,2.87,2.7,6.02,2.7,8.46,2.7,10.5,2.7,12.4,3.7,19,3.7,22.5,3.7,30.9,3.7,64.8]
[33,1.565,33,1.525,28,3.34,28,1.155,28,3.18,28,3.49,28,5.38,28,7.99,28,12.79,28,21.44,2.8,0.97,2.8,1.44,2.8,2.23,2.8,3.08,2.8,6.32,2.8,9.04,2.8,11,2.8,12.8,3.8,19.9,3.8,23.2,3.8,31.5,3.8,66.3]
[34,1.62,34,1.6,29,3.64,29,1.235,29,3.42,29,3.89,29,5.92,29,8.67,29,13.47,29,23.4,2.9,1,2.9,1.52,2.9,2.36,2.9,3.3,2.9,6.61,2.9,9.66,2.9,11.6,2.9,13.3,3.9,20.8,3.9,23.8,3.9,32.3,3.9,67.8]
[35,1.675,35,1.64,30,3.99,30,1.31,30,3.63,30,4.18,30,6.36,30,9.61,30,14.48,30,25.52,3,1.1,3,1.6,3,2.5,3,3.54,3,6.9,3,10.3,3,12.1,3,13.7,4,21.8,4,24.6,4,33,4,69.3]
[36,1.74,36,1.69,31,4.23,31,1.44,31,3.79,31,4.4,31,6.77,31,10.39,31,15.45,31,27.29,3.1,1.17,3.1,1.69,3.1,2.64,3.1,3.79,3.1,7.19,3.1,11,3.1,12.7,3.1,14.2,4.1,22.8,4.1,25.3,4.1,33.8,4.1,70.9]
[37,1.77,37,1.74,32,4.49,32,1.5,32,3.9,32,4.65,32,7.04,32,10.94,32,16.32,32,28.57,3.2,1.25,3.2,1.77,3.2,2.79,3.2,4.05,3.2,7.47,3.2,11.7,3.2,13.3,3.2,14.6,4.2,23.9,4.2,26,4.2,34.6,4.2,72.5]
[38,1.83,38,1.8,33,4.65,33,1.58,33,4.02,33,4.88,33,7.26,33,11.51,33,17.12,33,29.87,3.3,1.32,3.3,1.86,3.3,2.94,3.3,4.33,3.3,7.75,3.3,12.4,3.3,13.9,3.3,15.1,4.3,25.1,4.3,26.7,4.3,35.4,4.3,74.2]
[39,1.87,39,1.83,34,4.7,34,1.645,34,4.16,34,5.09,34,7.54,34,11.89,34,17.84,34,30.64,3.4,1.4,3.4,1.96,3.4,3.09,3.4,4.62,3.4,8.03,3.4,13.1,3.4,14.5,3.4,15.6,4.4,26.3,4.4,27.4,4.4,36.3,4.4,76]
[40,1.9,40,1.89,35,4.775,35,1.71,35,4.28,35,5.26,35,7.68,35,12.33,35,18.45,35,31.53,3.5,1.5,3.5,2.06,3.5,3.25,3.5,4.91,3.5,8.31,3.5,13.9,3.5,15.2,3.5,16.1,4.5,27.6,4.5,28.2,4.5,37.6,4.5,77.8]
["-","-","-","-",36,4.895,36,1.755,36,4.35,36,5.44,36,7.87,36,12.97,36,19.13,36,32.19,3.6,1.57,3.6,2.16,3.6,3.42,3.6,5.22,3.6,8.61,3.6,14.7,3.6,15.9,3.6,16.7,4.6,29,4.6,28.9,4.6,38.2,4.6,79.8]
["-","-","-","-",37,4.935,37,1.8,37,4.37,37,5.58,37,8.02,37,13.44,37,19.76,37,33.3,3.7,1.65,3.7,2.26,3.7,3.58,3.7,5.53,3.7,8.91,3.7,15.5,3.7,16.6,3.7,17.3,4.7,30.5,4.7,29.7,4.7,39.1,4.7,81.8]
["-","-","-","-",38,5.03,38,1.85,38,4.41,38,5.7,38,8.22,38,13.99,38,20.2,38,34.22,3.8,1.74,3.8,2.37,3.8,3.75,3.8,5.84,3.8,9.22,3.8,16.3,3.8,17.4,3.8,17.9,4.8,32.1,4.8,30.5,4.8,40.2,4.8,83.8]
["-","-","-","-",39,5.14,39,1.915,39,4.45,39,5.83,39,8.38,39,14.4,39,20.66,39,34.83,3.9,1.82,3.9,2.48,3.9,3.92,3.9,6.15,3.9,9.55,3.9,17.1,3.9,18.2,3.9,18.5,4.9,33.8,4.9,31.3,4.9,41.2,4.9,86]
["-","-","-","-",40,5.19,40,1.95,40,4.47,40,5.9,40,8.52,40,14.88,40,21.09,40,35.48,4,1.9,4,2.6,4,4.1,4,6.46,4,9.9,4,18.1,4,19,4,19.2,5,35.7,5,32.3,5,42.3,5,88.1]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",4.1,1.98,4.1,2.72,4.1,4.28,4.1,6.77,4.1,10.3,4.1,18.9,4.1,19.9,4.1,19.9,5.1,37.7,5.1,33.2,5.1,43.4,5.1,90.5]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",4.2,2.06,4.2,2.85,4.2,4.47,4.2,7.07,4.2,10.7,4.2,19.8,4.2,20.8,4.2,20.7,5.2,39.8,5.2,34.1,5.2,44.5,5.2,92.8]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",4.3,2.13,4.3,2.98,4.3,4.67,4.3,7.37,4.3,11.1,4.3,20.8,4.3,21.7,4.3,21.5,5.3,42.1,5.3,35.2,5.3,45.7,5.3,95.3]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",4.4,2.21,4.4,3.12,4.4,4.87,4.4,7.67,4.4,11.5,4.4,21.7,4.4,22.7,4.4,22.3,5.4,44.6,5.4,36.3,5.4,46.9,5.4,97.9]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",4.5,2.3,4.5,3.26,4.5,5.07,4.5,7.97,4.5,11.9,4.5,22.7,4.5,23.6,4.5,23.2,5.5,47.2,5.5,37.4,5.5,48,5.5,101]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",4.6,2.35,4.6,3.4,4.6,5.28,4.6,8.27,4.6,12.4,4.6,23.7,4.6,24.7,4.6,24.1,5.6,50,5.6,38.7,5.6,49.3,5.6,103]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",4.7,2.42,4.7,3.55,4.7,5.5,4.7,8.57,4.7,12.8,4.7,24.7,4.7,25.7,4.7,25.1,5.7,52.9,5.7,40,5.7,50.6,5.7,106]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",4.8,2.48,4.8,3.7,4.8,5.73,4.8,8.87,4.8,13.3,4.8,25.8,4.8,26.8,4.8,26,5.8,55.9,5.8,41.5,5.8,51.9,5.8,109]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",4.9,2.54,4.9,3.85,4.9,5.96,4.9,9.15,4.9,13.8,4.9,26.9,4.9,28,4.9,27.1,5.9,59.1,5.9,43.1,5.9,53.1,5.9,112]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",5,2.6,5,4,5,6.2,5,9.47,5,14.3,5,28,5,29.1,5,28.1,6,62.4,6,44.9,6,54.5,6,115]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",5.1,2.66,5.1,4.16,5.1,6.45,5.1,9.77,5.1,14.8,5.1,29.2,5.1,30.3,5.1,29.2,6.1,65.8,6.1,46.7,6.1,55.8,6.1,119]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",5.2,2.71,5.2,4.31,5.2,6.71,5.2,10.1,5.2,15.3,5.2,30.4,5.2,31.5,5.2,30.3,6.2,69.2,6.2,48.8,6.2,57.2,6.2,122]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",5.3,2.77,5.3,4.47,5.3,6.97,5.3,10.4,5.3,15.8,5.3,31.6,5.3,32.7,5.3,31.5,6.3,72.8,6.3,51,6.3,58.6,6.3,126]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",5.4,2.82,5.4,4.63,5.4,7.24,5.4,10.7,5.4,16.3,5.4,32.9,5.4,33.9,5.4,32.6,6.4,76.3,6.4,53.4,6.4,60.1,6.4,129]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",5.5,2.9,5.5,4.79,5.5,7.5,5.5,11,5.5,16.8,5.5,34.1,5.5,35.2,5.5,33.9,6.5,79.3,6.5,56.1,6.5,61.5,6.5,133]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",5.6,2.95,5.6,4.95,5.6,7.76,5.6,11.4,5.6,17.2,5.6,35.2,5.6,36.4,5.6,35.1,6.6,83.4,6.6,58.9,6.6,63.1,6.6,137]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",5.7,3.02,5.7,5.11,5.7,8.01,5.7,11.7,5.7,17.6,5.7,36.4,5.7,37.5,5.7,36.4,6.7,86.9,6.7,61.9,6.7,64.6,6.7,141]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",5.8,3.1,5.8,5.27,5.8,8.25,5.8,12,5.8,18,5.8,37.4,5.8,38.9,5.8,37.7,6.8,90.2,6.8,65.2,6.8,66.2,6.8,145]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",5.9,3.19,5.9,5.44,5.9,8.49,5.9,12.4,5.9,18.4,5.9,38.4,5.9,40.1,5.9,39.1,6.9,93.5,6.9,68.7,6.9,67.9,6.9,150]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",6,3.3,6,5.6,6,8.7,6,12.8,6,18.8,6,39.3,6,41.3,6,40.4,7,96.6,7,72.5,7,69.6,7,154]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",6.1,3.43,6.1,5.77,6.1,8.91,6.1,13.1,6.1,19.1,6.1,40.1,6.1,42.5,6.1,41.8,7.1,99.5,7.1,76.3,7.1,71.5,7.1,159]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",6.2,3.59,6.2,5.93,6.2,9.1,6.2,13.5,6.2,19.5,6.2,40.9,6.2,43.6,6.2,43.3,7.2,102,7.2,80.4,7.2,73.4,7.2,164]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",6.3,3.78,6.3,6.1,6.3,9.28,6.3,13.9,6.3,19.8,6.3,41.6,6.3,44.8,6.3,44.7,7.3,105,7.3,84.8,7.3,75.4,7.3,169]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",6.4,4,6.4,6.27,6.4,9.46,6.4,14.3,6.4,20.1,6.4,42.2,6.4,45.9,6.4,46.2,7.4,108,7.4,89.4,7.4,77.5,7.4,174]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",6.5,4.2,6.5,6.43,6.5,9.63,6.5,14.7,6.5,20.4,6.5,42.8,6.5,47,6.5,47.7,7.5,110,7.5,93.2,7.5,80,7.5,179]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",6.6,4.5,6.6,6.6,6.6,9.8,6.6,15.1,6.6,20.7,6.6,43.4,6.6,48,6.6,49.2,7.6,112,7.6,99.1,7.6,82,7.6,185]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",6.7,21,6.7,43.9,6.7,49.1,6.7,50.8,7.7,115,7.7,104,7.7,84.5,7.7,190]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",6.8,21.4,6.8,44.5,6.8,50.1,6.8,52.3,7.8,117,7.8,109,7.8,87.1,7.8,196]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",6.9,21.8,6.9,45,6.9,51.1,6.9,53.9,7.9,119,7.9,114,7.9,89.9,7.9,202]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",7,22.2,7,45.6,7,52.1,7,55.4,8,121,8,120,8,92.9,8,208]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",7.1,22.7,7.1,46.2,7.1,53.1,7.1,57,8.099999,123,8.099999,124,8.099999,96.1,8.099999,215]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",7.2,23.2,7.2,46.7,7.2,54,7.2,58.6,8.2,125,8.2,129,8.2,99.5,8.2,222]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",7.3,23.7,7.3,47.3,7.3,54.9,7.3,60.1,8.3,126,8.3,134,8.3,103,8.3,229]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",7.4,24.3,7.4,47.9,7.4,55.8,7.4,61.7,8.4,128,8.4,138,8.4,107,8.4,236]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",7.5,24.9,7.5,48.5,7.5,56.6,7.5,63.2,8.5,130,8.5,142,8.5,111,8.5,244]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",7.6,57.5,7.6,64.8,8.599999,131,8.599999,146,8.599999,116,8.599999,252]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",7.7,58.3,7.7,66.3,8.7,133,8.7,151,8.7,120,8.7,259]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",7.8,59.1,7.8,67.8,8.8,134,8.8,155,8.8,125,8.8,267]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",7.9,59.9,7.9,69.4,8.9,136,8.9,159,8.9,130,8.9,275]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",8,60.7,8,70.9,9,137,9,162,9,136,9,284]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",8.099999,61.5,8.099999,72.4,9.099999,138,9.099999,166,9.099999,141,9.099999,292]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",8.2,62.2,8.2,73.8,9.2,140,9.2,169,9.2,147,9.2,300]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",8.3,62.9,8.3,75.3,9.3,141,9.3,172,9.3,153,9.3,309]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",8.4,63.7,8.4,76.7,9.4,142,9.4,176,9.4,158,9.4,317]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",8.5,64.4,8.5,78.1,9.5,143,9.5,179,9.5,164,9.5,325]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",8.599999,65.1,8.599999,79.5,9.599999,144,9.599999,181,9.599999,170,9.599999,333]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",8.7,65.8,8.7,80.9,9.7,145,9.7,184,9.7,176,9.7,342]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",8.8,66.5,8.8,82.2,9.8,146,9.8,187,9.8,182,9.8,350]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",8.9,67.2,8.9,83.5,9.9,147,9.9,189,9.9,187,9.9,358]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",9,67.9,9,84.8,10,148,10,192,10,193,10,364]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",9.099999,68.5,9.099999,86.1,10.099999,149,10.099999,194,10.099999,198,10.099999,373]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",9.2,69.2,9.2,87.3,10.2,150,10.2,196,10.2,203,10.2,380]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",9.3,69.9,9.3,88.5,10.3,151,10.3,198,10.3,208,10.3,388]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",9.4,70.5,9.4,89.7,10.4,152,10.4,200,10.4,213,10.4,395]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",9.5,71.2,9.5,90.8,10.5,153,10.5,202,10.5,218,10.5,402]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",9.599999,71.8,9.599999,91.9,10.599999,154,10.599999,204,10.599999,223,10.599999,409]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",9.7,72.5,9.7,93,10.7,155,10.7,206,10.7,227,10.7,415]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",9.8,73.1,9.8,94.1,10.8,155.5,10.8,207,10.8,231,10.8,422]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",9.9,73.8,9.9,95.1,10.9,156,10.9,209,10.9,235,10.9,428]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",10,74.4,10,96.1,11,157,11,211,11,240,11,435]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",10.099999,97,11.099999,158,11.099999,212,11.099999,244,11.099999,441]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",10.2,97.9,11.2,159,11.2,214,11.2,247,11.2,447]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",10.3,98.8,11.3,159.5,11.3,215,11.3,251,11.3,453]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",10.4,99.7,11.4,160,11.4,217,11.4,255,11.4,458]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",10.5,100.5,11.5,161,11.5,218,11.5,258,11.5,464]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",10.599999,101,11.599999,162,11.599999,220,11.599999,262,11.599999,470]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",10.7,102,11.7,163,11.7,221,11.7,265,11.7,475]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",10.8,103,11.8,163.4,11.8,222,11.8,268,11.8,480]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",10.9,104,11.9,164,11.9,223,11.9,271,11.9,486]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",11,104.3,12,165,12,225,12,274,12,489]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",11.099999,105,"-","-",12.099999,226,12.099999,277,12.099999,496]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",11.2,106,"-","-",12.2,227,12.2,280,12.2,501]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",11.3,106.4,"-","-",12.3,228,12.3,282,12.3,506]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",11.4,107,"-","-",12.4,229,12.4,285,12.4,510]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",11.5,108,"-","-",12.5,231,12.5,288,12.5,515]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",11.599999,108.4,"-","-",12.599999,232,12.599999,290,12.599999,520]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",11.7,109,"-","-",12.7,233,12.7,293,12.7,524]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",11.8,110,"-","-",12.799999,234,12.799999,295,12.799999,529]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",11.9,110.4,"-","-",12.9,235,12.9,297,12.9,533]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",12,111,"-","-",13,236,13,300,13,537]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",13.099999,237,13.099999,302,13.099999,542]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",13.2,238,13.2,304,13.2,546]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",13.299999,239,13.299999,306,13.299999,550]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",13.4,240,13.4,308,13.4,554]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",13.5,242,13.5,310,13.5,558]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",13.599999,312,13.599999,562]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",13.7,314,13.7,566]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",13.799999,316,13.799999,570]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",13.9,318,13.9,573]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",14,320,14,575]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",14.099999,322,14.099999,581]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",14.2,324,14.2,585]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",14.299999,325,14.299999,588]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",14.4,327,14.4,592]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",14.5,329,14.5,595]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",14.599999,330,14.599999,599]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",14.7,332,14.7,602]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",14.799999,334,14.799999,606]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",14.9,335,14.9,609]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",15,337,15,613]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",15.099999,338,15.099999,616]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",15.2,340,15.2,620]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",15.299999,342,15.299999,623]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",15.4,343,15.4,626]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",15.5,345,15.5,630]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",15.599999,346,15.599999,633]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",15.7,348,15.7,636]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",15.799999,349,15.799999,639]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",15.9,350,15.9,642]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",16,352,16,646]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",16.1,353,16.1,649]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",16.199999,355,16.199999,652]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",16.299999,356,16.299999,655]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",16.4,357,16.4,658]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",16.5,359,16.5,661]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",16.6,360,16.6,664]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",16.699999,361,16.699999,667]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",16.799999,363,16.799999,670]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",16.9,364,16.9,674]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",17,365,17,677]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",17.1,367,17.1,680]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",17.199999,368,17.199999,683]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",17.299999,369,17.299999,686]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",17.4,371,17.4,689]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",17.5,372,17.5,692]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",17.6,695]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",17.699999,698]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",17.799999,701]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",17.9,703]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",18,704]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]

{"sheet":"сл_Danfoss","index":9,"n_rows":222,"n_cols":256,"rows_kept":222,"cut":false,"hidden":true,"merged":[],"flags":["formulas_cached_only"]}
["м_н_Danfoss (правило №1: все столбцы должны заканчиваться знаком \"-\")"]
["MSV-C с ИД-DN15",null,3.28,null,"MSV-C с ИД-DN20",null,"MSV-C без ИД-DN20",null,"MSV-C с ИД-DN25",null,"MSV-C без ИД-DN25",null,"MSV-C с ИД-DN32",null,"MSV-C без ИД-DN32",null,"MSV-C с ИД-DN40",null,"MSV-C без ИД-DN40",null,"MSV-C с ИД-DN50",null,"MSV-C без ИД-DN50",null,"      USV-I - DN15",null,"      USV-I - DN20",null,"      USV-I - DN25",null,"      USV-I - DN32",null,"      USV-I - DN40",null,"      USV-I - DN50",null,"MSV-BD- DN15 LF",null,"MSV-BD- DN15",null,"MSV-BD- DN20",null,"MSV-BD- DN25",null,"MSV-BD- DN32",null,"MSV-BD- DN40",null,"MSV-BD- DN50",null,"MSV-F- DN50",null,"MSV-F- DN65",null,"MSV-F- DN80",null,"MSV-F- DN100",null,"MSV-F- DN125",null,"MSV-F- DN150",null,"MSV-F- DN200",null,"MSV-F- DN250",null,"MSV-F- DN300",null,"MSV-F- DN350",null,"MSV-F- DN400"]
["Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv","Пред.","Kv"]
["настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка",null,"настройка"]
[2,0.51,2,0.6,2,0.8,2,0.9,2,0.9,2,0.8,2,1.3,2,2.6,2,2.2,2,3.1,2,2.5,2,5.4,0.2,0.2,0.2,0.3,0.2,0.4,0.2,0.7,0.2,0.9,0.2,1.7,0,0.07,0,0.1,0,0.12,0,0.34,0,0.51,0,1.05,0,1.75,1,2.2,1,5.3,1,6.6,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0]
[3,0.85,3,1.1,3,1.6,3,1.8,3,2,3,1.8,3,3,3,5.1,3,4.7,3,7.2,3,8.8,3,13.8,0.5,0.4,0.5,0.7,0.5,1.1,0.5,1.7,0.5,2.1,0.5,4.1,0.4,0.12,0.4,0.14,0.4,0.32,0.4,0.67,0.4,1.26,0.4,1.74,0.4,2.69,2,5.1,2,7.8,2,10,2,6.2,2,11.3,2,20.4,2,41.3,2,0,2,0,2,0,2,0]
[4,1.19,4,1.6,4,2.5,4,2.8,4,3.5,4,3.3,4,5.8,4,8.9,4,8.9,4,13.5,4,17,4,24.5,1,0.8,1,1.3,1,1.9,1,3.1,1,4.2,1,7.6,0.8,0.17,0.8,0.24,0.8,0.6,0.8,0.9,0.8,1.97,0.8,2.64,0.8,3.58,3,10.3,3,12.1,3,13.7,3,13.4,3,18.7,3,26.1,3,54.7,3,297,3,411,3,495,3,690]
[5,1.45,5,2.1,5,3.1,5,3.9,5,5,5,5.5,5,9.2,5,14,5,13.2,5,18.5,5,26.2,5,33,1.5,1.1,1.5,1.7,1.5,2.7,1.5,4.3,1.5,5.9,1.5,0.5,1.2,0.23,1.2,0.34,1.2,0.89,1.2,1.14,1.2,2.87,1.2,3.64,1.2,4.6,4,18.1,4,19,4,19.2,4,21.8,4,24.6,4,33,4,69,4,410,4,560,4,677,4,945]
[6,1.64,6,2.8,6,3.5,6,5.2,6,6.1,6,8.3,6,12.3,6,17,6,16.4,6,24,6,34.5,6,41,2,1.3,2,2,2,3.3,2,5.2,2,7.4,2,2.7,1.6,0.32,1.6,0.47,1.6,1.16,1.6,1.46,1.6,3.92,1.6,4.69,1.6,5.8,5,28,5,29.1,5,28.1,5,35.7,5,32.3,5,43,5,87.6,5,513,5,696,5,851,5,1182]
[7,1.72,7,3.2,7,3.7,7,6.3,7,6.7,7,10.2,7,14.6,7,20,7,19.3,7,26,7,40.2,7,49,2.5,1.5,2.5,2.3,2.5,3.6,2.5,5.7,2.5,8.7,2.5,14,2,0.43,2,0.61,2,1.45,2,1.85,2,5.05,2,5.8,2,7.14,6,39.3,6,41.3,6,40.4,6,62.4,6,44.9,6,54.5,6,115,6,587,6,825,6,1019,6,1409]
[8,1.8,8,3.9,8,3.8,8,7.3,8,7,8,11.8,8,15.8,8,21.6,8,21,8,28.5,8,43.9,8,50.5,3,1.6,3,2.5,3,3.9,3,6.1,3,9.7,3,5.2,2.4,0.56,2.4,0.77,2.4,1.78,2.4,2.29,2.4,6.27,2.4,6.99,2.4,8.55,7,45.6,7,52.1,7,55.4,7,96.6,7,72.5,7,67.8,7,153.2,7,649,7,944,7,1163,7,1612]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",3.2,1.6,3.2,2.5,3.2,4,3.2,6.3,3.2,10,3.2,16,2.8,0.69,2.8,0.93,2.8,2.17,2.8,2.77,2.8,7.67,2.8,8.33,2.8,10,8,"-",8,61.3,8,70.9,8,121,8,120,8,92.9,8,208,8,731,8,1044,8,1272,8,1752]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",3.2,0.83,3.2,1.08,3.2,2.65,3.2,3.25,3.2,9.38,3.2,9.9,3.2,11.49,9,"-",9,68.8,9,84.6,9,137,9,162,9,139.6,9,284,9,800,9,1138,9,1386,9,1874]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",3.6,0.97,3.6,1.25,3.6,3.19,3.6,3.74,3.6,11.46,3.6,11.74,3.6,13.09,10,"-",10,74.4,10,96,10,148,10,192,10,193,10,364,10,817,10,1226,10,1513,10,1991]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",4,1.14,4,1.47,4,3.75,4,4.26,4,13.64,4,13.85,4,14.88,11,"-",11,"-",11,105.3,11,157,11,217,11,238,11,432,11,812,11,1291,11,1606,11,2093]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",4.4,1.31,4.4,1.73,4.4,4.28,4.4,4.82,4.4,"-",4.4,16.13,4.4,17,12,"-",12,"-",12,111,12,165,12,233,12,274,12,489,12,null,12,1324,12,1651,12,2256]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",4.8,1.47,4.8,2.08,4.8,4.72,4.8,5.46,4.8,"-",4.8,18.32,4.8,19.54,13,"-",13,"-",13,"-",13,"-",13,241,13,301,13,537,13,"-",13,1345,13,"-",13,2389]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",5.2,1.66,5.2,2.36,5.2,5.04,5.2,6.19,5.2,"-",5.2,19.98,5.2,22.51,13.5,"-",13.5,"-",13.5,"-",13.5,"-",13.5,242,13.5,312,13.5,557,13.5,"-",13.5,1359,13.5,"-",13.5,"-"]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",5.6,1.93,5.6,2.54,5.6,5.21,5.6,6.96,5.6,"-",5.6,"-",5.6,25.76,14,"-",14,"-",14,"-",14,"-",14,"-",14,320,14,575,14,"-",14,1380,14,"-",14,"-"]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",6,2.14,6,"-",6,"-",6,7.69,6,"-",6,"-",6,28.9,15,"-",15,"-",15,"-",15,"-",15,"-",15,336,15,606,15,"-",15,"-",15,"-",15,"-"]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",6.4,"-",6.4,"-",6.4,"-",6.4,8.17,6.4,"-",6.4,"-",6.4,31.17,16,"-",16,"-",16,"-",16,"-",16,"-",16,350,16,640,16,"-",16,"-",16,"-",16,"-"]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-",6.6,"-",6.6,"-",6.6,"-",6.6,"-",6.6,"-",6.6,"-",6.6,31.61,17,"-",17,"-",17,"-",17,"-",17,"-",17,364,17,671,17,"-",17,"-",17,"-",17,"-"]
["-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-","-"]
[1,2,1,2,1,2,1,2,1,2,1,2,1,2,1,2,1,2,1,2,1,2,1,2,1,2,1,2,1,2,1,2,1,2,1,2,1,2,1,2,1,2,1,2,1,2,1,2,1,2,1,2,1,2,1,2,1,2,1,2,1,2,1,2,1,2,1,2,1,2,1,2,1,2,1,2,1,2,1,2]
["MSV-C с ИД"]
["MSV-C без ИД"]
["DN15","MSV-C с ИД",null,"MSV-C с ИД-DN15",null,null,null,"MSV-C с ИД-DN15","MSV-C без ИД-DN15",null,null,"MSV-C с ИД-DN15","MSV-C с ИД-DN20","MSV-C с ИД-DN25","MSV-C с ИД-DN32","MSV-C с ИД-DN40","MSV-C с ИД-DN50",{"$nulls":4},0.2,0.5,1,1.5,2,2.5,3,3.2]
["DN20","MSV-C с ИД",null,"MSV-C с ИД-DN20",null,null,null,"MSV-C с ИД-DN20","MSV-C без ИД-DN20",null,null,"MSV-C без ИД-DN15","MSV-C без ИД-DN20","MSV-C без ИД-DN25","MSV-C без ИД-DN32","MSV-C без ИД-DN40","MSV-C без ИД-DN50",null,null,null,15,0.2,0.4,0.8,1.1,1.3,1.5,1.6,1.6,{"$nulls":10},50,65,80,100,125,150,200,250,300,350,400]
["DN25","MSV-C с ИД",null,"MSV-C с ИД-DN25",null,null,null,"MSV-C с ИД-DN25","MSV-C без ИД-DN25",{"$nulls":11},20,0.3,0.7,1.3,1.7,2,2.3,2.5,2.5,{"$nulls":9},1,2.2,5.3,6.6]
["DN32","MSV-C с ИД",null,"MSV-C с ИД-DN32",null,null,null,"MSV-C с ИД-DN32","MSV-C без ИД-DN32",{"$nulls":11},25,0.4,1.1,1.9,2.7,3.3,3.6,3.9,4,{"$nulls":9},2,5.1,7.8,10,6.2,11.3,20.4,41.3]
["DN40","MSV-C с ИД",null,"MSV-C с ИД-DN40",null,null,null,"MSV-C с ИД-DN40","MSV-C без ИД-DN40",{"$nulls":11},32,0.7,1.7,3.1,4.3,5.2,5.7,6.1,6.3,{"$nulls":9},3,10.3,12.1,13.7,13.4,18.7,26.1,54.7,297,411,495,690]
["DN50","MSV-C с ИД",null,"MSV-C с ИД-DN50",null,null,null,"MSV-C с ИД-DN50","MSV-C без ИД-DN50",{"$nulls":11},40,0.9,2.1,4.2,5.9,7.4,8.7,9.7,10,{"$nulls":9},4,18.1,19,19.2,21.8,24.6,33,69,410,560,677,945]
[{"$nulls":20},50,1.7,4.1,7.6,0.5,2.7,14,5.2,16,{"$nulls":9},5,28,29.1,28.1,35.7,32.3,43,87.6,513,696,851,1182]
["DN15","MSV-C без ИД",null,"MSV-C без ИД-DN15",{"$nulls":10},"MSV-F- DN15","MSV-F- DN20","MSV-F- DN25","MSV-F- DN32","MSV-F- DN40","MSV-F- DN50","MSV-F- DN65","MSV-F- DN80","MSV-F- DN100","MSV-F- DN125","MSV-F- DN150","MSV-F- DN200","MSV-F- DN250","MSV-F- DN300","MSV-F- DN350","MSV-F- DN400",{"$nulls":8},6,39.3,41.3,40.4,62.4,44.9,54.5,115,587,825,1019,1409]
["DN20","MSV-C без ИД",null,"MSV-C без ИД-DN20",{"$nulls":34},7,45.6,52.1,55.4,96.6,72.5,67.8,153.2,649,944,1163,1612]
["DN25","MSV-C без ИД",null,"MSV-C без ИД-DN25",{"$nulls":34},8,"-",61.3,70.9,121,120,92.9,208,731,1044,1272,1752]
["DN32","MSV-C без ИД",null,"MSV-C без ИД-DN32",{"$nulls":34},9,"-",68.8,84.6,137,162,139.6,284,800,1138,1386,1874]
["DN40","MSV-C без ИД",null,"MSV-C без ИД-DN40",{"$nulls":34},10,"-",74.4,96,148,192,193,364,817,1226,1513,1991]
["DN50","MSV-C без ИД",null,"MSV-C без ИД-DN50",{"$nulls":31},"      USV-I - DN15",null,null,11,"-","-",105.3,157,217,238,432,812,1291,1606,2093]
[{"$nulls":35},"      USV-I - DN20",null,null,12,"-","-",111,165,233,274,489,"-",1324,1651,2256]
[null,null,1,"MSV-C с ИД-DN15",null,"003Z3020",{"$nulls":29},"      USV-I - DN25",null,null,13,"-","-","-","-",241,301,537,"-",1345,"-",2389]
[null,null,3,"MSV-C без ИД-DN15",null,"003Z3030",{"$nulls":29},"      USV-I - DN32",null,null,13.5,"-","-","-","-",242,312,557,"-",1359,"-","-"]
[null,null,5,"MSV-C с ИД-DN20",null,"003Z3021",{"$nulls":29},"      USV-I - DN40",null,null,14,"-","-","-","-","-",320,575,"-",1380,"-","-"]
[null,null,7,"MSV-C без ИД-DN20",null,"003Z3031",{"$nulls":29},"      USV-I - DN50",null,null,15,"-","-","-","-","-",336,606,"-","-","-","-"]
[null,null,9,"MSV-C с ИД-DN25",null,"003Z3022",{"$nulls":32},16,"-","-","-","-","-",350,640,"-","-","-","-"]
[null,null,11,"MSV-C без ИД-DN25",null,"003Z3032",{"$nulls":32},17,"-","-","-","-","-",364,671,"-","-","-","-"]
[null,null,13,"MSV-C с ИД-DN32",null,"003Z3023",{"$nulls":32},18,"-","-","-","-","-","-",704,"-","-","-","-"]
[null,null,15,"MSV-C без ИД-DN32",null,"003Z3033",{"$nulls":32},"-","-","-","-","-","-","-","-","-","-","-","-"]
[null,null,17,"MSV-C с ИД-DN40",null,"003Z3024"]
[null,null,19,"MSV-C без ИД-DN40",null,"003Z3034"]
[null,null,21,"MSV-C с ИД-DN50",null,"003Z3025"]
[null,null,23,"MSV-C без ИД-DN50",null,"003Z3035"]
[null,null,null,"MSV-BD- DN15 LF",null,"003Z4000",null,null,null,"DN15 LF","MSV-BD"]
[null,null,null,"MSV-BD- DN15",null,"003Z4001",null,null,null,"DN15","MSV-BD"]
[null,null,null,"MSV-BD- DN20",null,"003Z4002",null,null,null,"DN20","MSV-BD"]
[null,null,null,"MSV-BD- DN25",null,"003Z4003",null,null,null,"DN25","MSV-BD"]
[null,null,null,"MSV-BD- DN32",null,"003Z4004",null,null,null,"DN32","MSV-BD"]
[null,null,null,"MSV-BD- DN40",null,"003Z4005",null,null,null,"DN40","MSV-BD"]
[null,null,null,"MSV-BD- DN50",null,"003Z4006",null,null,null,"DN50","MSV-BD"]
[null,null,null,"MSV-F- DN50",null,"003Z0029"]
[null,null,null,"MSV-F- DN65",null,"003Z0030"]
[null,null,null,"MSV-F- DN80",null,"003Z0031"]
[null,null,null,"MSV-F- DN100",null,"003Z0032"]
[null,null,null,"MSV-F- DN125",null,"003Z0033"]
[null,null,null,"MSV-F- DN150",null,"003Z0034"]
[null,null,null,"MSV-F- DN200",null,"003Z0035"]
[null,null,null,"MSV-F- DN250",null,"003Z0036"]
[null,null,null,"MSV-F- DN300",null,"003Z0037"]
[null,null,null,"MSV-F- DN350",null,"003Z0038"]
[null,null,null,"MSV-F- DN400",null,"003Z0039"]
[]
[]
[]
[]
[]
[null,null,"Исходник","MSV-BD",{"$nulls":8},"Исходник","MSV-BD",{"$nulls":8},"Исходник","MSV-BD",{"$nulls":8},"Исходник","MSV-BD"]
[]
[null,null,"Настр   Ду15LF","Ду15","Ду20","Ду25","Ду32","Ду40","Ду50",null,null,null,"Настр   Ду15LF","Ду15","Ду20","Ду25","Ду32","Ду40","Ду50",null,null,null,"Настр   Ду15LF","Ду15","Ду20","Ду25","Ду32","Ду40","Ду50",null,null,"-","Настр   Ду15LF","Ду15","Ду20","Ду25","Ду32","Ду40","Ду50"]
[null,0,0.07,0.1,0.12,0.34,0.51,1.05,1.75,null,null,0,0.07,0.1,0.12,0.34,0.51,1.05,1.75,1,null,0,0.07,0.1,0.12,0.34,0.51,1.05,1.75,1,null,0,0.07,0.1,0.12,0.34,0.51,1.05,1.75,1]
[null,0.1,0.08,0.11,0.16,0.44,0.73,1.2,2.01,null,null,0.2,0.09,0.12,0.2,0.53,0.92,1.36,2.25,2,null,0.3,0.11,0.13,0.26,0.61,1.1,1.55,2.47,4,null,0.4,0.12,0.14,0.32,0.67,1.26,1.74,2.69,3]
[null,0.2,0.09,0.12,0.2,0.53,0.92,1.36,2.25,null,null,0.4,0.12,0.14,0.32,0.67,1.26,1.74,2.69,3,null,0.6,0.15,0.19,0.45,0.79,1.6,2.17,3.12,7,null,0.8,0.17,0.24,0.6,0.9,1.97,2.64,3.58,5]
[null,0.3,0.11,0.13,0.26,0.61,1.1,1.55,2.47,null,null,0.6,0.15,0.19,0.45,0.79,1.6,2.17,3.12,4,null,0.9,0.19,0.26,0.67,0.95,2.18,2.88,3.82,10,null,1.2,0.23,0.34,0.89,1.14,2.87,3.64,4.6,7]
[null,0.4,0.12,0.14,0.32,0.67,1.26,1.74,2.69,null,null,0.8,0.17,0.24,0.6,0.9,1.97,2.64,3.58,5,null,1.2,0.23,0.34,0.89,1.14,2.87,3.64,4.6,13,null,1.6,0.32,0.47,1.16,1.46,3.92,4.69,5.8,9]
[null,0.5,0.13,0.16,0.38,0.73,1.43,1.95,2.91,null,null,1,0.2,0.29,0.74,1.01,2.39,3.13,4.07,6,null,1.5,0.3,0.44,1.09,1.37,3.64,4.43,5.49,16,null,2,0.43,0.61,1.45,1.85,5.05,5.8,7.14,11]
[null,0.6,0.15,0.19,0.45,0.79,1.6,2.17,3.12,null,null,1.2,0.23,0.34,0.89,1.14,2.87,3.64,4.6,7,null,1.8,0.37,0.54,1.3,1.65,4.48,5.24,6.46,19,null,2.4,0.56,0.77,1.78,2.29,6.27,6.99,8.55,13]
[null,0.7,0.16,0.21,0.53,0.84,1.78,2.4,3.35,null,null,1.4,0.27,0.4,1.03,1.29,3.38,4.16,5.18,8,null,2.1,0.46,0.65,1.53,1.96,5.35,6.08,7.49,22,null,2.8,0.69,0.93,2.17,2.77,7.67,8.33,10,15]
[null,0.8,0.17,0.24,0.6,0.9,1.97,2.64,3.58,null,null,1.6,0.32,0.47,1.16,1.46,3.92,4.69,5.8,9,null,2.4,0.56,0.77,1.78,2.29,6.27,6.99,8.55,25,null,3.2,0.83,1.08,2.65,3.25,9.38,9.9,11.49,17]
[null,0.9,0.19,0.26,0.67,0.95,2.18,2.88,3.82,null,null,1.8,0.37,0.54,1.3,1.65,4.48,5.24,6.46,10,null,2.7,0.66,0.89,2.07,2.65,7.29,7.98,9.64,28,null,3.6,0.97,1.25,3.19,3.74,11.46,11.74,13.09,19]
[null,1,0.2,0.29,0.74,1.01,2.39,3.13,4.07,null,null,2,0.43,0.61,1.45,1.85,5.05,5.8,7.14,11,null,3,0.76,1.01,2.4,3.01,8.48,9.08,10.74,31,null,4,1.14,1.47,3.75,4.26,13.64,13.85,14.88,21]
[null,1.1,0.21,0.32,0.82,1.08,2.62,3.39,4.33,null,null,2.2,0.49,0.69,1.61,2.07,5.65,6.38,7.84,12,null,3.3,0.87,1.12,2.78,3.37,9.87,10.33,11.88,34,null,4.4,1.31,1.73,4.28,4.82,"-",16.13,17,23]
[null,1.2,0.23,0.34,0.89,1.14,2.87,3.64,4.6,null,null,2.4,0.56,0.77,1.78,2.29,6.27,6.99,8.55,13,null,3.6,0.97,1.25,3.19,3.74,11.46,11.74,13.09,37,null,4.8,1.47,2.08,4.72,5.46,"-",18.32,19.54,25]
[null,1.3,0.25,0.37,0.96,1.22,3.12,3.9,4.89,null,null,2.6,0.62,0.85,1.97,2.53,6.94,7.63,9.27,14,null,3.9,1.1,1.41,3.61,4.13,13.12,13.3,14.41,40,null,5.2,1.66,2.36,5.04,6.19,"-",19.98,22.51,27]
[null,1.4,0.27,0.4,1.03,1.29,3.38,4.16,5.18,null,null,2.8,0.69,0.93,2.17,2.77,7.67,8.33,10,15,null,4.2,1.23,1.59,4.02,4.53,14.52,14.98,15.89,43,null,5.6,1.93,2.54,5.21,6.96,"-","-",25.76,29]
[null,1.5,0.3,0.44,1.09,1.37,3.64,4.43,5.49,null,null,3,0.76,1.01,2.4,3.01,8.48,9.08,10.74,16,null,4.5,1.35,1.81,4.4,4.98,null,16.69,17.59,46,null,6,2.14,"-","-",7.69,"-","-",28.9,31]
[null,1.6,0.32,0.47,1.16,1.46,3.92,4.69,5.8,null,null,3.2,0.83,1.08,2.65,3.25,9.38,9.9,11.49,17,null,4.8,1.47,2.08,4.72,5.46,null,18.32,19.54,49,null,6.4,"-","-","-",8.17,"-","-",31.17,33]
[null,1.7,0.35,0.51,1.23,1.55,4.19,4.96,6.13,null,null,3.4,0.9,1.16,2.91,3.49,10.38,10.79,12.27,18,null,5.1,1.6,2.3,4.97,6,null,19.65,21.73,52,null,6.6,"-","-","-","-","-","-",31.61,34]
[null,1.8,0.37,0.54,1.3,1.65,4.48,5.24,6.46,null,null,3.6,0.97,1.25,3.19,3.74,11.46,11.74,13.09,19,null,5.4,1.79,2.46,5.14,6.57,null,20.41,24.12,55]
[null,1.9,0.4,0.58,1.38,1.75,4.76,5.51,6.8,null,null,3.8,1.06,1.35,3.47,4,12.58,12.77,13.95,20,null,5.7,1.99,2.57,5.24,7.15,null,null,26.58,58]
[null,2,0.43,0.61,1.45,1.85,5.05,5.8,7.14,null,null,4,1.14,1.47,3.75,4.26,13.64,13.85,14.88,21,null,6,2.14,null,null,7.69,null,null,28.9,61]
[null,2.1,0.46,0.65,1.53,1.96,5.35,6.08,7.49,null,null,4.2,1.23,1.59,4.02,4.53,14.52,14.98,15.89,22,null,6.3,2.26,null,null,8.09,null,null,30.74,64]
[null,2.2,0.49,0.69,1.61,2.07,5.65,6.38,7.84,null,null,4.4,1.31,1.73,4.28,4.82,null,16.13,17,23,null,6.6,{"$nulls":6},31.61,67]
[null,2.3,0.52,0.73,1.69,2.18,5.96,6.68,8.19,null,null,4.6,1.39,1.91,4.52,5.13,null,17.25,18.21,24]
[null,2.4,0.56,0.77,1.78,2.29,6.27,6.99,8.55,null,null,4.8,1.47,2.08,4.72,5.46,null,18.32,19.54,25]
[null,2.5,0.59,0.8,1.87,2.41,6.6,7.3,8.91,null,null,5,1.54,2.23,4.9,5.81,null,19.25,20.97,26]
[null,2.6,0.62,0.85,1.97,2.53,6.94,7.63,9.27,null,null,5.2,1.66,2.36,5.04,6.19,null,19.98,22.51,27]
[null,2.7,0.66,0.89,2.07,2.65,7.29,7.98,9.64,null,null,5.4,1.79,2.46,5.14,6.57,null,20.41,24.12,28]
[null,2.8,0.69,0.93,2.17,2.77,7.67,8.33,10,null,null,5.6,1.93,2.54,5.21,6.96,null,null,25.76,29]
[null,2.9,0.73,0.97,2.29,2.89,8.06,8.7,10.37,null,null,5.8,2.04,null,5.27,7.34,null,null,27.38,30]
[null,3,0.76,1.01,2.4,3.01,8.48,9.08,10.74,null,null,6,2.14,null,null,7.69,null,null,28.9,31]
[null,3.1,0.8,1.04,2.52,3.13,8.92,9.48,11.11,null,null,6.2,2.22,null,null,7.98,null,null,30.21,32]
[null,3.2,0.83,1.08,2.65,3.25,9.38,9.9,11.49,null,null,6.4,null,null,null,8.17,null,null,31.17,33]
[null,3.3,0.87,1.12,2.78,3.37,9.87,10.33,11.88,null,null,6.6,{"$nulls":6},31.61,34]
[null,3.4,0.9,1.16,2.91,3.49,10.38,10.79,12.27]
[null,3.5,0.94,1.2,3.05,3.62,10.91,11.26,12.67]
[null,3.6,0.97,1.25,3.19,3.74,11.46,11.74,13.09]
[null,3.7,1.01,1.3,3.33,3.87,12.02,12.25,13.51]
[null,3.8,1.06,1.35,3.47,4,12.58,12.77,13.95]
[null,3.9,1.1,1.41,3.61,4.13,13.12,13.3,14.41]
[null,4,1.14,1.47,3.75,4.26,13.64,13.85,14.88]
[null,4.1,1.18,1.53,3.89,4.39,14.12,14.41,15.38]
[null,4.2,1.23,1.59,4.02,4.53,14.52,14.98,15.89]
[null,4.3,1.27,1.66,4.15,4.68,14.84,15.55,16.44]
[null,4.4,1.31,1.73,4.28,4.82,null,16.13,17]
[null,4.5,1.35,1.81,4.4,4.98,null,16.69,17.59]
[null,4.6,1.39,1.91,4.52,5.13,null,17.25,18.21]
[null,4.7,1.43,2,4.62,5.29,null,17.8,18.86]
[null,4.8,1.47,2.08,4.72,5.46,null,18.32,19.54]
[null,4.9,1.51,2.16,4.82,5.64,null,18.8,20.24]
[null,5,1.54,2.23,4.9,5.81,null,19.25,20.97]
[null,5.1,1.6,2.3,4.97,6,null,19.65,21.73]
[null,5.2,1.66,2.36,5.04,6.19,null,19.98,22.51]
[null,5.3,1.72,2.41,5.09,6.38,null,20.24,23.3]
[null,5.4,1.79,2.46,5.14,6.57,null,20.41,24.12]
[null,5.5,1.87,2.5,5.18,6.77,null,20.48,24.94]
[null,5.6,1.93,2.54,5.21,6.96,null,null,25.76]
[null,5.7,1.99,2.57,5.24,7.15,null,null,26.58]
[null,5.8,2.04,null,5.27,7.34,null,null,27.38]
[null,5.9,2.09,null,null,7.52,null,null,28.16]
[null,6,2.14,null,null,7.69,null,null,28.9]
[null,6.1,2.18,null,null,7.85,null,null,29.59]
[null,6.2,2.22,null,null,7.98,null,null,30.21]
[null,6.3,2.26,null,null,8.09,null,null,30.74]
[null,6.4,null,null,null,8.17,null,null,31.17]
[null,6.5,null,null,null,8.22,null,null,31.47]
[null,6.6,{"$nulls":6},31.61]
[]
[]
[null,"DN15","MSV-F",null,"MSV-F- DN15",null,"MSV-F- DN15"]
[null,"DN20","MSV-F",null,"MSV-F- DN20",null,"MSV-F- DN20"]
[null,"DN25","MSV-F",null,"MSV-F- DN25",null,"MSV-F- DN25"]
[null,"DN32","MSV-F",null,"MSV-F- DN32",null,"MSV-F- DN32"]
[null,"DN40","MSV-F",null,"MSV-F- DN40",null,"MSV-F- DN40"]
[null,"DN50","MSV-F",null,"MSV-F- DN50",null,"MSV-F- DN50"]
[null,"DN65","MSV-F",null,"MSV-F- DN65",null,"MSV-F- DN65"]
[null,"DN80","MSV-F",null,"MSV-F- DN80",null,"MSV-F- DN80"]
[null,"DN100","MSV-F",null,"MSV-F- DN100",null,"MSV-F- DN100"]
[null,"DN125","MSV-F",null,"MSV-F- DN125",null,"MSV-F- DN125"]
[null,"DN150","MSV-F",null,"MSV-F- DN150",null,"MSV-F- DN150"]
[null,"DN200","MSV-F",null,"MSV-F- DN200",null,"MSV-F- DN200"]
[null,"DN250","MSV-F",null,"MSV-F- DN250",null,"MSV-F- DN250"]
[null,"DN300","MSV-F",null,"MSV-F- DN300",null,"MSV-F- DN300"]
[null,"DN350","MSV-F",null,"MSV-F- DN350",null,"MSV-F- DN350"]
[null,"DN400","MSV-F",null,"MSV-F- DN400",null,"MSV-F- DN400"]
[]
[]
[]
[null,null,50,65,80,100,125,150,200,250,300,350,400,null,null,50,65,80,100,125,150,200,250,300,350,400]
[null,1,2.2,5.3,6.6,{"$nulls":9},1,2.2,5.3,6.6]
[null,1.25,2.8,5.8,7.5,{"$nulls":9},2,5.1,7.8,10,6.2,11.3,20.4,41.3]
[null,1.5,3.5,6.4,8.4,{"$nulls":9},3,10.3,12.1,13.7,13.4,18.7,26.1,54.7,297,411,495,690]
[null,1.75,4.2,7,9.2,{"$nulls":9},4,18.1,19,19.2,21.8,24.6,33,69,410,560,677,945]
[null,2,5.1,7.8,10,6.2,11.3,20.4,41.3,{"$nulls":5},5,28,29.1,28.1,35.7,32.3,43,87.6,513,696,851,1182]
[null,2.25,6.1,8.7,10.8,8.1,13.4,21.8,44.5,{"$nulls":5},6,39.3,41.3,40.4,62.4,44.9,54.5,115,587,825,1019,1409]
[null,2.5,7.4,9.7,11.7,9.9,15.4,23.2,48.1,{"$nulls":5},7,45.6,52.1,55.4,96.6,72.5,67.8,153.2,649,944,1163,1612]
[null,2.75,8.7,10.8,12.7,11.7,17.1,24.6,51.4,{"$nulls":5},8,"-",61.3,70.9,121,120,92.9,208,731,1044,1272,1752]
[null,3,10.3,12.1,13.7,13.4,18.7,26.1,54.7,297,411,495,690,null,9,"-",68.8,84.6,137,162,139.6,284,800,1138,1386,1874]
[null,3.25,12.1,13.5,14.8,15.3,20.2,27.7,58,326,449,542,755,null,10,"-",74.4,96,148,192,193,364,817,1226,1513,1991]
[null,3.5,13.9,15.2,16.1,17.3,21.6,29.3,61.5,354,487,588,820,null,11,"-","-",105.3,157,217,238,432,812,1291,1606,2093]
[null,3.75,15.9,17,17.6,19,23.1,31.1,65.1,382,524,633,883,null,12,"-","-",111,165,233,274,489,"-",1324,1651,2256]
[null,4,18.1,19,19.2,21.8,24.6,33,69,410,560,677,945,null,13,"-","-","-","-",241,301,537,"-",1345,"-",2389]
[null,4.25,19.3,21.2,21.1,24.4,26.4,35.4,73,438,595,721,1006,null,13.5,"-","-","-","-",242,312,557,"-",1359,"-","-"]
[null,4.5,22.7,23.7,23.2,27.5,28.3,37.9,77.5,464,629,765,1065,null,14,"-","-","-","-","-",320,575,"-",1380,"-","-"]
[null,4.75,25.2,26.3,25.5,31.2,30.2,40.4,82.3,490,663,808,1124,null,15,"-","-","-","-","-",336,606,"-","-","-","-"]
[null,5,28,29.1,28.1,35.7,32.3,43,87.6,513,696,851,1182,null,16,"-","-","-","-","-",350,640,"-","-","-","-"]
[null,5.25,31,32.1,30.9,41.2,34.6,45.7,93.5,535,729,894,1240,null,17,"-","-","-","-","-",364,671,"-","-","-","-"]
[null,5.5,34.1,35.1,33.9,47.5,37.3,48.5,100,554,762,937,1297,null,18,"-","-","-","-","-","-",704,"-","-","-","-"]
[null,5.75,36.9,38.2,37,54.6,40.7,51.4,107,571,794,979,1354,null,"-","-","-","-","-","-","-","-","-","-","-","-"]
[null,6,39.3,41.3,40.4,62.4,44.9,54.5,115,587,825,1019,1409]
[null,6.25,41.3,44.2,44,70.9,50,57.2,123,602,856,1059,1464]
[null,6.5,42.8,47,47.7,79.6,56.3,60.2,132.3,617,886,1096,1517]
[null,6.75,44.2,49.6,51.5,88.3,63.7,63.6,142.2,632,916,1131,1566]
[null,7,45.6,52.1,55.4,96.6,72.5,67.8,153.2,649,944,1163,1612]
[null,7.25,47,54.6,59.3,103.8,82.9,72.6,165.2,668,970,1192,1652]
[null,7.5,48.5,56.9,63.2,110.3,94.5,78.4,178.3,688,995,1220,1688]
[null,7.75,"-",59.2,67,116,106.8,85.1,192.6,710,102,1246,1721]
[null,8,"-",61.3,70.9,121,120,92.9,208,731,1044,1272,1752]
[null,8.25,"-",63.4,74.3,125.7,131.5,103.3,225,751,1068,1299,1783]
[null,8.5,"-",65.3,78.1,130,143,114.6,244,770,1091,1327,1814]
[null,8.75,"-",67.1,81.5,133.9,154,126.8,263,787,1115,1356,1844]
[null,9,"-",68.8,84.6,137,162,139.6,284,800,1138,1386,1874]
[null,9.25,"-",70.4,87.7,140.5,172,152.8,303.9,809,1161,1418,1905]
[null,9.5,"-",71.9,90.6,143,180,166.3,324.2,815,1184,1451,1935]
[null,9.75,"-",73.2,93.4,146,187,179.7,344.3,817,1206,1483,1964]
[null,10,"-",74.4,96,148,192,193,364,817,1226,1513,1991]
[null,10.25,"-","-",98.6,151,199,205,382,816,1246,1541,2014]
[null,10.5,"-","-",101,153,205,216.5,399.5,815,1263,1566,2038]
[null,10.75,"-","-",103.3,155,211,228,416,812,1278,1587,2063]
[null,11,"-","-",105.3,157,217,238,432,812,1291,1606,2093]
[null,11.25,"-","-",107,159,222,248,448,"-",1302,1622,2130]
[null,11.5,"-","-",109,161,226,257,462,"-",1311,1635,2170]
[null,11.75,"-","-",109.9,163,230,266,476,"-",1318,1645,2213]
[null,12,"-","-",111,165,233,274,489,"-",1324,1651,2256]
[null,12.5,"-","-","-","-",238,288,514,"-",1335,"-",2333]
[null,13,"-","-","-","-",241,301,537,"-",1345,"-",2389]
[null,13.5,"-","-","-","-",242,312,557,"-",1359,"-","-"]
[null,14,"-","-","-","-","-",320,575,"-",1380,"-","-"]
[null,15,"-","-","-","-","-",336,606,"-","-","-","-"]
[null,16,"-","-","-","-","-",350,640,"-","-","-","-"]
[null,17,"-","-","-","-","-",364,671,"-","-","-","-"]
[null,17.5,"-","-","-","-","-",372,687,"-","-","-","-"]
[null,18,"-","-","-","-","-","-",704,"-","-","-","-"]
[null,"-","-","-","-","-","-","-","-","-","-","-","-"]

{"sheet":"Лист1","index":10,"n_rows":262,"n_cols":256,"rows_kept":262,"cut":false,"hidden":true,"merged":[],"flags":["formulas_cached_only"]}
[]
[]
[]
[null,null,"AV6 , 1к",0,"AV6 , 2к",0,"AV6 , 3к",0,"Combi 2,3  - внутр рез, DN10",0,"Combi 2,3  - внутр рез, DN15",0,"Combi 2,3  - внутр рез, DN20",0,"Hycocon VTZ, (ВР)  DN15",0,"Hycocon VTZ, (ВР) DN20",0,"Hycocon VTZ, (ВР) DN25",0,"Hycocon VTZ, (ВР) DN32",0,"Hycocon VTZ, (ВР) DN40",0,"Hycocon VTZ, (ВР) DN50",0,"Hydrocontrol VTR, (ВР+КИП), DN10",0,"Hydrocontrol VTR, (ВР+КИП), DN15",0,"Hydrocontrol VTR, (ВР+КИП), DN20",0,"Hydrocontrol VTR, (ВР+КИП), DN25",0,"Hydrocontrol VTR, (ВР+КИП), DN32",0,"Hydrocontrol VTR, (ВР+КИП), DN40",0,"Hydrocontrol VTR, (ВР+КИП), DN50",0,"Hydrocontrol R , DN65",0,"Hydrocontrol VFC+КИП , DN20",0,"Hydrocontrol VFC+КИП , DN25",0,"Hydrocontrol VFC+КИП , DN32",0,"Hydrocontrol VFC+КИП , DN40",0,"Hydrocontrol VFC+КИП , DN50",0,"Hydrocontrol VFC+КИП , DN65",0,"Hydrocontrol VFC+КИП , DN80",0,"Hydrocontrol VFC+КИП , DN100",0,"Hydrocontrol VFC+КИП , DN125",0,"Hydrocontrol VFC+КИП , DN150",0,"Hydrocontrol VFC+КИП , DN200",0,"Hydrocontrol VFC+КИП , DN250",0,"Hydrocontrol VFC+КИП , DN300",0,"Hydrocontrol VFC+КИП , DN350",0,"Hydrocontrol VFC+КИП , DN400",0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,16,17,18,19,20,21,22,23,24,25,26,27,28,29,30,31,32,33,34,35,36,37,38,39,40,41,42,43,44,45,46,47,48,49,50,51,52,53,54,55,56,57,58,59,60,61,62,63,64,65,66,67,68,69,70,71,72,73,74,75,76,77,78,79,80,81,82,83,84,85,86,87,88,89,90,91,92,93,94,95,96,97,98,99,100,101,102,103,104,105,106,107,108,109,110,111,112,113,114,115,116,117,118,119,120,121,122,123,124,125,126,127,128,129,130,131,132,133,134,135,136,137,138,139,140,141,142,143,144,145,146,147,148,149,150,151,152,153,154,155,156,157,158,159,160,161,162,163,164,165,166,167,168,169,170,171,172,173,174,175,176,177,178,179,180,181,182,183,184,185,186,187,188,189,190,191,192,193,194,195,196,197,198,199,200,201,202,203,204,205,206,207,208,209,210,211,212,213,214,215,216,217,218,219,220,221,222,223,224,225,226,227,228,229,230,231,232,233,234,235,236,237,238,239,240,241,242,243,244,245,246,247,248,249,250,251,252,253,254]
[null,null,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0]
[null,null,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0,1,0]
[null,null,1,0,3,0,5,0,7,0,9,0,11,0,13,0,15,0,17,0,19,0,21,0,23,0,25,0,27,0,29,0,31,0,33,0,35,0,37,0,39,0,41,0,43,0,45,0,47,0,49,0,51,0,53,0,55,0,57,0,59,0,61,0,63,0,65,0,67,0,69,0,71,0,73,0,75,0,77,0,79,0,81,0,83,0,85,0,87,0,89,0,91,0,93,0,95,0,97,0,99,0,101,0,103,0,105,0,107,0,109,0,111,0,113,0,115,0,117,0,119,0,121,0,123,0,125,0,127,0,129,0,131,0,133,0,135,0,137,0,139,0,141,0,143,0,145,0,147,0,149,0,151,0,153,0,155,0,157,0,159,0,161,0,163,0,165,0,167,0,169,0,171,0,173,0,175,0,177,0,179,0,181,0,183,0,185,0,187,0,189,0,191,0,193,0,195,0,197,0,199,0,201,0,203,0,205,0,207,0,209,0,211,0,213,0,215,0,217,0,219,0,221,0,223,0,225,0,227,0,229,0,231,0,233,0,235,0,237,0,239,0,241,0,243,0,245,0,247,0,249,0,251,0,253,0]
[null,null,"AV6 , 1к",1,1,1,1]
[null,null,0,2,0,0,0]
[null,null,"AV6 , 2к",3,1,1,3]
[null,null,0,4,0,0,0]
[null,null,"AV6 , 3к",5,1,1,5]
[null,null,0,6,0,0,0]
[null,null,"Combi 2,3  - внутр рез, DN10",7,1,1,7]
[null,null,0,8,0,0,0]
[null,null,"Combi 2,3  - внутр рез, DN15",9,1,1,9]
[null,null,0,10,0,0,0]
[null,null,"Combi 2,3  - внутр рез, DN20",11,1,1,11]
[null,null,0,12,0,0,0]
[null,null,"Hycocon VTZ, (ВР)  DN15",13,1,1,13]
[null,null,0,14,0,0,0]
[null,null,"Hycocon VTZ, (ВР) DN20",15,1,1,15]
[null,null,0,16,0,0,0]
[null,null,"Hycocon VTZ, (ВР) DN25",17,1,1,17]
[null,null,0,18,0,0,0]
[null,null,"Hycocon VTZ, (ВР) DN32",19,1,1,19]
[null,null,0,20,0,0,0]
[null,null,"Hycocon VTZ, (ВР) DN40",21,1,1,21]
[null,null,0,22,0,0,0]
[null,null,"Hycocon VTZ, (ВР) DN50",23,1,1,23]
[null,null,0,24,0,0,0]
[null,null,"Hydrocontrol VTR, (ВР+КИП), DN10",25,1,1,25]
[null,null,0,26,0,0,0]
[null,null,"Hydrocontrol VTR, (ВР+КИП), DN15",27,1,1,27]
[null,null,0,28,0,0,0]
[null,null,"Hydrocontrol VTR, (ВР+КИП), DN20",29,1,1,29]
[null,null,0,30,0,0,0]
[null,null,"Hydrocontrol VTR, (ВР+КИП), DN25",31,1,1,31]
[null,null,0,32,0,0,0]
[null,null,"Hydrocontrol VTR, (ВР+КИП), DN32",33,1,1,33]
[null,null,0,34,0,0,0]
[null,null,"Hydrocontrol VTR, (ВР+КИП), DN40",35,1,1,35]
[null,null,0,36,0,0,0]
[null,null,"Hydrocontrol VTR, (ВР+КИП), DN50",37,1,1,37]
[null,null,0,38,0,0,0]
[null,null,"Hydrocontrol R , DN65",39,1,1,39]
[null,null,0,40,0,0,0]
[null,null,"Hydrocontrol VFC+КИП , DN20",41,1,1,41]
[null,null,0,42,0,0,0]
[null,null,"Hydrocontrol VFC+КИП , DN25",43,1,1,43]
[null,null,0,44,0,0,0]
[null,null,"Hydrocontrol VFC+КИП , DN32",45,1,1,45]
[null,null,0,46,0,0,0]
[null,null,"Hydrocontrol VFC+КИП , DN40",47,1,1,47]
[null,null,0,48,0,0,0]
[null,null,"Hydrocontrol VFC+КИП , DN50",49,1,1,49]
[null,null,0,50,0,0,0]
[null,null,"Hydrocontrol VFC+КИП , DN65",51,1,1,51]
[null,null,0,52,0,0,0]
[null,null,"Hydrocontrol VFC+КИП , DN80",53,1,1,53]
[null,null,0,54,0,0,0]
[null,null,"Hydrocontrol VFC+КИП , DN100",55,1,1,55]
[null,null,0,56,0,0,0]
[null,null,"Hydrocontrol VFC+КИП , DN125",57,1,1,57]
[null,null,0,58,0,0,0]
[null,null,"Hydrocontrol VFC+КИП , DN150",59,1,1,59]
[null,null,0,60,0,0,0]
[null,null,"Hydrocontrol VFC+КИП , DN200",61,1,1,61]
[null,null,0,62,0,0,0]
[null,null,"Hydrocontrol VFC+КИП , DN250",63,1,1,63]
[null,null,0,64,0,0,0]
[null,null,"Hydrocontrol VFC+КИП , DN300",65,1,1,65]
[null,null,0,66,0,0,0]
[null,null,"Hydrocontrol VFC+КИП , DN350",67,1,1,67]
[null,null,0,68,0,0,0]
[null,null,"Hydrocontrol VFC+КИП , DN400",69,1,1,69]
[null,null,0,70,0,0,0]
[null,null,0,71,1,1,71]
[null,null,0,72,0,0,0]
[null,null,0,73,1,1,73]
[null,null,0,74,0,0,0]
[null,null,0,75,1,1,75]
[null,null,0,76,0,0,0]
[null,null,0,77,1,1,77]
[null,null,0,78,0,0,0]
[null,null,0,79,1,1,79]
[null,null,0,80,0,0,0]
[null,null,0,81,1,1,81]
[null,null,0,82,0,0,0]
[null,null,0,83,1,1,83]
[null,null,0,84,0,0,0]
[null,null,0,85,1,1,85]
[null,null,0,86,0,0,0]
[null,null,0,87,1,1,87]
[null,null,0,88,0,0,0]
[null,null,0,89,1,1,89]
[null,null,0,90,0,0,0]
[null,null,0,91,1,1,91]
[null,null,0,92,0,0,0]
[null,null,0,93,1,1,93]
[null,null,0,94,0,0,0]
[null,null,0,95,1,1,95]
[null,null,0,96,0,0,0]
[null,null,0,97,1,1,97]
[null,null,0,98,0,0,0]
[null,null,0,99,1,1,99]
[null,null,0,100,0,0,0]
[null,null,0,101,1,1,101]
[null,null,0,102,0,0,0]
[null,null,0,103,1,1,103]
[null,null,0,104,0,0,0]
[null,null,0,105,1,1,105]
[null,null,0,106,0,0,0]
[null,null,0,107,1,1,107]
[null,null,0,108,0,0,0]
[null,null,0,109,1,1,109]
[null,null,0,110,0,0,0]
[null,null,0,111,1,1,111]
[null,null,0,112,0,0,0]
[null,null,0,113,1,1,113]
[null,null,0,114,0,0,0]
[null,null,0,115,1,1,115]
[null,null,0,116,0,0,0]
[null,null,0,117,1,1,117]
[null,null,0,118,0,0,0]
[null,null,0,119,1,1,119]
[null,null,0,120,0,0,0]
[null,null,0,121,1,1,121]
[null,null,0,122,0,0,0]
[null,null,0,123,1,1,123]
[null,null,0,124,0,0,0]
[null,null,0,125,1,1,125]
[null,null,0,126,0,0,0]
[null,null,0,127,1,1,127]
[null,null,0,128,0,0,0]
[null,null,0,129,1,1,129]
[null,null,0,130,0,0,0]
[null,null,0,131,1,1,131]
[null,null,0,132,0,0,0]
[null,null,0,133,1,1,133]
[null,null,0,134,0,0,0]
[null,null,0,135,1,1,135]
[null,null,0,136,0,0,0]
[null,null,0,137,1,1,137]
[null,null,0,138,0,0,0]
[null,null,0,139,1,1,139]
[null,null,0,140,0,0,0]
[null,null,0,141,1,1,141]
[null,null,0,142,0,0,0]
[null,null,0,143,1,1,143]
[null,null,0,144,0,0,0]
[null,null,0,145,1,1,145]
[null,null,0,146,0,0,0]
[null,null,0,147,1,1,147]
[null,null,0,148,0,0,0]
[null,null,0,149,1,1,149]
[null,null,0,150,0,0,0]
[null,null,0,151,1,1,151]
[null,null,0,152,0,0,0]
[null,null,0,153,1,1,153]
[null,null,0,154,0,0,0]
[null,null,0,155,1,1,155]
[null,null,0,156,0,0,0]
[null,null,0,157,1,1,157]
[null,null,0,158,0,0,0]
[null,null,0,159,1,1,159]
[null,null,0,160,0,0,0]
[null,null,0,161,1,1,161]
[null,null,0,162,0,0,0]
[null,null,0,163,1,1,163]
[null,null,0,164,0,0,0]
[null,null,0,165,1,1,165]
[null,null,0,166,0,0,0]
[null,null,0,167,1,1,167]
[null,null,0,168,0,0,0]
[null,null,0,169,1,1,169]
[null,null,0,170,0,0,0]
[null,null,0,171,1,1,171]
[null,null,0,172,0,0,0]
[null,null,0,173,1,1,173]
[null,null,0,174,0,0,0]
[null,null,0,175,1,1,175]
[null,null,0,176,0,0,0]
[null,null,0,177,1,1,177]
[null,null,0,178,0,0,0]
[null,null,0,179,1,1,179]
[null,null,0,180,0,0,0]
[null,null,0,181,1,1,181]
[null,null,0,182,0,0,0]
[null,null,0,183,1,1,183]
[null,null,0,184,0,0,0]
[null,null,0,185,1,1,185]
[null,null,0,186,0,0,0]
[null,null,0,187,1,1,187]
[null,null,0,188,0,0,0]
[null,null,0,189,1,1,189]
[null,null,0,190,0,0,0]
[null,null,0,191,1,1,191]
[null,null,0,192,0,0,0]
[null,null,0,193,1,1,193]
[null,null,0,194,0,0,0]
[null,null,0,195,1,1,195]
[null,null,0,196,0,0,0]
[null,null,0,197,1,1,197]
[null,null,0,198,0,0,0]
[null,null,0,199,1,1,199]
[null,null,0,200,0,0,0]
[null,null,0,201,1,1,201]
[null,null,0,202,0,0,0]
[null,null,0,203,1,1,203]
[null,null,0,204,0,0,0]
[null,null,0,205,1,1,205]
[null,null,0,206,0,0,0]
[null,null,0,207,1,1,207]
[null,null,0,208,0,0,0]
[null,null,0,209,1,1,209]
[null,null,0,210,0,0,0]
[null,null,0,211,1,1,211]
[null,null,0,212,0,0,0]
[null,null,0,213,1,1,213]
[null,null,0,214,0,0,0]
[null,null,0,215,1,1,215]
[null,null,0,216,0,0,0]
[null,null,0,217,1,1,217]
[null,null,0,218,0,0,0]
[null,null,0,219,1,1,219]
[null,null,0,220,0,0,0]
[null,null,0,221,1,1,221]
[null,null,0,222,0,0,0]
[null,null,0,223,1,1,223]
[null,null,0,224,0,0,0]
[null,null,0,225,1,1,225]
[null,null,0,226,0,0,0]
[null,null,0,227,1,1,227]
[null,null,0,228,0,0,0]
[null,null,0,229,1,1,229]
[null,null,0,230,0,0,0]
[null,null,0,231,1,1,231]
[null,null,0,232,0,0,0]
[null,null,0,233,1,1,233]
[null,null,0,234,0,0,0]
[null,null,0,235,1,1,235]
[null,null,0,236,0,0,0]
[null,null,0,237,1,1,237]
[null,null,0,238,0,0,0]
[null,null,0,239,1,1,239]
[null,null,0,240,0,0,0]
[null,null,0,241,1,1,241]
[null,null,0,242,0,0,0]
[null,null,0,243,1,1,243]
[null,null,0,244,0,0,0]
[null,null,0,245,1,1,245]
[null,null,0,246,0,0,0]
[null,null,0,247,1,1,247]
[null,null,0,248,0,0,0]
[null,null,0,249,1,1,249]
[null,null,0,250,0,0,0]
[null,null,0,251,1,1,251]
[null,null,0,252,0,0,0]
[null,null,0,253,1,1,253]
[null,null,0,254,0,0,0]