{"text_format":"2","workbook":"xlsx","n_sheets":1,"sheets":["Интер 3"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":0,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Интер 3","index":0,"n_rows":73,"n_cols":16,"rows_kept":73,"cut":false,"hidden":false,"merged":[[1,0,2,0]]}
[]
["Дaтa ","t1 ","t2 ","dt ","V1 ","M1 ","V2 ","M2 ","V3 ","Mг ","P1 ","P2 ","Qо ","BНP ","BOC ","НC "]
[null,"°C ","°C ","°C ","м3 ","т ","м3 ","т ","м3 ","т ","кг/см2 ","кг/см2 ","Гкал ","ч ","ч ","  "]
["2013-08-23",31.08,69.98,-38.9,0,0,8.6999999999999993,8.5399999999999991,0,-8.5399999999999991,7,4,-0.312,24,0,"*"]
["2013-08-24",30.91,69.06,-38.15,0,0,9.3000000000000007,9.1,0,-9.1,7,4,-0.32500000000000001,24,0,"*"]
["2013-08-25",30.48,70.11,-39.630000000000003,0,0,11,10.76,0,-10.76,7,4,-0.40400000000000003,24,0,"*"]
["2013-08-26",30.48,70.56,-40.08,0,0,11.7,11.45,0,-11.45,7,4,-0.437,24,0,"*"]
["2013-08-27",30.61,71,-40.39,0,0,12.4,12.11,0,-12.11,7,4,-0.46800000000000003,24,0,"*"]
["2013-08-28",29.07,71.09,-42.02,0,0,12.2,11.93,0,-11.93,7,4,-0.496,24,0,"*"]
["2013-08-29",26.79,70.23,-43.44,0,0,10.8,10.56,0,-10.56,7,4,-0.438,24,0,"*"]
["2013-08-30",28.1,69.900000000000006,-41.8,0,0,10.9,10.67,0,-10.67,7,4,-0.42,24,0,"*"]
["2013-08-31",29.66,68.45,-38.79,0,0,10.4,10.19,0,-10.19,7,4,-0.373,24,0,"*"]
["2013-09-01",29.75,70.27,-40.520000000000003,0,0,15.3,14.97,0,-14.97,7,4,-0.57799999999999996,24,0,"*"]
["2013-09-02",30.66,70.58,-39.92,0,0,13.7,13.41,0,-13.41,7,4,-0.51500000000000001,24,0,"*"]
["2013-09-03",30.26,69.489999999999995,-39.229999999999997,0,0,11.4,11.17,0,-11.17,7,4,-0.41599999999999998,24,0,"*"]
["2013-09-04",30.33,70.39,-40.06,0,0,11.9,11.64,0,-11.64,7,4,-0.443,24,0,"*"]
["2013-09-05",30.39,71.239999999999995,-40.85,0,0,12.1,11.82,0,-11.82,7,4,-0.45900000000000002,24,0,"*"]
["2013-09-06",30.5,70.62,-40.119999999999997,0,0,11.8,11.53,0,-11.53,7,4,-0.44400000000000001,24,0,"*"]
["2013-09-07",30.51,68.72,-38.21,0,0,11.1,10.88,0,-10.88,7,4,-0.39300000000000002,24,0,"*"]
["2013-09-08",30.1,69.8,-39.700000000000003,0,0,13.7,13.4,0,-13.4,7,4,-0.505,24,0,"*"]
["2013-09-09",30.45,69.680000000000007,-39.229999999999997,0,0,12.4,12.13,0,-12.13,7,4,-0.45500000000000002,24,0,"*"]
["2013-09-10",30.17,70.52,-40.35,0,0,12.2,11.95,0,-11.95,7,4,-0.46100000000000002,24,0,"*"]
["2013-09-11",30.01,70.3,-40.29,0,0,12.5,12.23,0,-12.23,7,4,-0.47,24,0,"*"]
["2013-09-12",29.78,69.58,-39.799999999999997,0,0,12.2,11.94,0,-11.94,7,4,-0.45400000000000001,24,0,"*"]
["2013-09-13",29.78,69.86,-40.08,0,0,11.9,11.66,0,-11.66,7,4,-0.44700000000000001,24,0,"*"]
["2013-09-14",29.43,68.67,-39.24,0,0,10.3,10.09,0,-10.09,7,4,-0.374,24,0,"*"]
["2013-09-15",29.28,71.05,-41.77,0,0,14.1,13.78,0,-13.78,7,4,-0.55000000000000004,24,0,"*"]
["2013-09-16",29.88,72.02,-42.14,0,0,11.7,11.47,0,-11.47,7,4,-0.46,24,0,"*"]
["2013-09-17",29.8,72.3,-42.5,0,0,11.3,11.05,0,-11.05,7,4,-0.44700000000000001,24,0,"*"]
["2013-09-18",29.97,73.3,-43.33,0,0,13.5,13.19,0,-13.19,7,4,-0.55100000000000005,24,0,"*"]
["2013-09-19",30.09,73.3,-43.21,0,0,13.3,12.99,0,-12.99,7,4,-0.54200000000000004,24,0,"*"]
["2013-09-20",27.93,72.73,-44.8,0,0,12.1,11.83,0,-11.83,7,4,-0.51400000000000001,24,0,"*"]
["2013-09-21",25.69,73.06,-47.37,0,0,11.1,10.83,0,-10.83,7,4,-0.49199999999999999,24,0,"*"]
["2013-09-22",25.6,73.81,-48.21,0,0,15.8,15.44,0,-15.44,7,4,-0.71799999999999997,24,0,"*"]
["2013-09-23",59.73,53.55,6.18,36.700000000000003,36.08,30.3,29.89,0,6.19,7,4,6.0999999999999999E-2,24,0,"*"]
["2013-09-24",59.99,30.1,29.89,14.5,14.27,0,0,0,14.27,7,4,0,24,0]
["2013-09-25",58.68,23.74,34.94,17.7,17.41,0,0,0,17.41,7,4,0,24,0]
["2013-09-26",57.27,23.2,34.07,15.9,15.64,0,0,0,15.64,7,4,0,24,0]
["2013-09-27",57.85,23.12,34.729999999999997,13.7,13.48,0,0,0,13.48,7,4,0,24,0]
["2013-09-28",57.6,22.76,34.840000000000003,15.3,15.06,0,0,0,15.06,7,4,0,24,0]
["2013-09-29",57.83,22.02,35.81,15.1,14.87,0,0,0,14.87,7,4,0,24,0]
["2013-09-30",59.44,53.39,6.05,65.3,64.23,51.4,50.71,0,13.52,7,4,0.32200000000000001,24,0]
["2013-10-01",60.75,49.58,11.17,159.19999999999999,156.52000000000001,147.5,145.78,0,10.74,7,4,1.63,24,0,"*"]
["2013-10-02",62,46.41,15.59,187.6,184.33,167.7,165.99,0,18.34,7,4,2.5750000000000002,24,0,"*"]
["2013-10-03",62.64,45.57,17.07,181,177.76,174.7,172.96,0,4.8,7,4,2.9529999999999998,24,0,"*"]
["2013-10-04",64.180000000000007,46.62,17.559999999999999,180.9,177.52,174.6,172.85,0,4.67,7,4,3.0449999999999999,24,0,"*"]
["2013-10-05",64.13,46.62,17.510000000000002,180.2,176.82,175.2,173.41,0,3.41,7,4,3.0539999999999998,24,0,"*"]
["2013-10-06",65.08,47.23,17.850000000000001,180.6,177.12,173.2,171.35,0,5.77,7,4,3.0649999999999999,24,0,"*"]
["2013-10-07",63.97,46.84,17.13,177.9,174.58,174.1,172.28,0,2.2999999999999998,7,4,2.9540000000000002,24,0,"*"]
["2013-10-08",57.24,43.54,13.7,186,183.19,180.7,179.06,0,4.13,7,4,2.4630000000000001,24,0,"*"]
["2013-10-09",65.760000000000005,48.25,17.510000000000002,190.8,187.06,186,183.95,0,3.11,7,4,3.2149999999999999,24,0,"*"]
["2013-10-10",62.49,46.78,15.71,190.4,187,184.4,182.48,0,4.5199999999999996,7,4,2.8759999999999999,24,0,"*"]
["2013-10-11",60.75,45.9,14.85,192.3,189.03,186.7,184.81,0,4.22,7,4,2.7440000000000002,24,0,"*"]
["2013-10-12",59.75,45.55,14.2,192.7,189.53,185.8,183.97,0,5.56,7,4,2.62,24,0,"*"]
["2013-10-13",62.63,46.8,15.83,190.4,187,182.1,180.19,0,6.81,7,4,2.8460000000000001,24,0,"*"]
["2013-10-14",67.23,49.52,17.71,190.2,186.32,186.9,184.74,0,1.58,7,4,3.2719999999999998,24,0,"*"]
["2013-10-15",66.290000000000006,49.04,17.25,191,187.21,185.3,183.17,0,4.04,7,4,3.1629999999999998,24,0,"*"]
["2013-10-16",63.46,47.59,15.87,191.9,188.4,184.9,182.93,0,5.47,7,4,2.907,24,0,"*"]
["2013-10-17",64.83,48.12,16.71,188.5,184.9,182.4,180.43,0,4.47,7,4,3.02,24,0,"*"]
["2013-10-18",69.31,50.73,18.579999999999998,193.4,189.25,187.6,185.31,0,3.94,7,4,3.4460000000000002,24,0,"*"]
["2013-10-19",63.26,47.53,15.73,195.5,191.92,186.6,184.61,0,7.31,7,4,2.915,24,0,"*"]
["2013-10-20",62.48,46.92,15.56,195.3,191.8,184,182.06,0,9.74,7,4,2.8380000000000001,24,0,"*"]
["2013-10-21",69.02,50.48,18.54,192.7,188.58,186.4,184.17,0,4.41,7,4,3.4129999999999998,24,0,"*"]
["2013-10-22",68.8,50.2,18.600000000000001,190.1,186.07,183.7,181.52,0,4.55,7,4,3.383,24,0,"*"]
["2013-10-23",68.150000000000006,49.28,18.87,188,184.06,181.8,179.7,0,4.3600000000000003,7,4,3.399,24,0,"*"]
["Итого:",null,null,null,4500.8,4417.01,4596.8,4543.03,0,-126.02,null,null,53.817999999999998,1488,0,"*"]
["Средние:",46.13,57.08,-10.95,{"$nulls":6},7,4]
[]
["Период нормальной работы 1488ч   "]
["Период отсутств.счета тепл.энергии 0ч     "]
["Время работы прибора после сброса 15097ч       "]
[]
["   Представитель абонента          Представитель теплоснабж.организации"]