{"text_format":"2","workbook":"xlsx","n_sheets":3,"sheets":["Лист1","Лист2","Лист3"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":6,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Лист1","index":0,"n_rows":19,"n_cols":24,"rows_kept":19,"cut":false,"hidden":false,"merged":[[12,3,14,3],[0,7,0,21],[2,22,6,22],[5,3,7,3],[8,0,10,0]]}
["Расчет потерь напора на клапане",null,null,"Расчет настройки клапана",null,null,null,"Настроики"]
["при известной настройке",null,null,"для нужного падения давления",null,null,null,1,1.5,2,2.5,3,3.5,4,4.5,5,5.5,6,6.5,7,"N","без т/э"]
["Q",800,"Вт","Q",1150,"Вт","RA-10",0.04,0.06,0.08,0.1,0.12,0.16,0.19,0.22,0.25,0.28999999999999998,0.33,0.36,0.38,0.56000000000000005,0.65,"Kv"]
["Δt",20,"С","Δt",10,"С","RA-15",0.04,7.0000000000000007E-2,0.09,0.13,0.16,0.21,0.25,1,0.36,0.4,0.43,0.49,0.52,0.73,0.9]
["Клапан",{"$f":"INDEX(G3:G7,X18,1)","v":"RA-25"},"мм","Клапан",{"$f":"INDEX(G3:G7,X17,1)","v":"RA-15"},"мм","RA-20",0.1,0.13,0.15,0.16,0.17,0.22,0.26,0.31,0.35,0.41,0.46,0.6,0.73,1.04,1.4]
["N",{"$f":"INDEX(H11:V11,1,X19)","v":1},"настройка","ΔРтреб",0.03,"бар","RA-20(UK)",0.16,0.18,0.2,0.23,0.25,0.3,0.35,0.41,0.47,0.54,0.6,0.67,0.73,0.8,1]
["G",{"$f":"B3*0.86/B4","v":34.4},"кг/ч",null,{"$f":"E6/0.09806","v":0.30593514174994901},"м.в.ст.","RA-25",0.1,0.13,0.15,0.16,0.17,0.22,0.26,0.31,0.35,0.41,0.46,0.6,0.73,1.04,1.4]
["Kv",{"$f":"HLOOKUP(B6,Tab,X18+1)","v":0.1},null,null,{"$f":"E7*9.8064*1000","v":3000.1223740567002},"Па"]
["ΔP",{"$f":"POWER((B7/B8/1000),2)","v":0.11833599999999994},"бар","G",{"$f":"E3*0.86/E4","v":98.9},"кг/ч"]
[null,{"$f":"B9/0.09806","v":1.2067713644707316},"м.в.ст.","N",{"$f":"HLOOKUP(E11,IF(X17=1,tab_10,IF(X17=2,tab_15,IF(X17=3,tab_20,IF(X17=4,tab_20UK,IF(X17=5,tab_25))))),2)","v":7},"настройка","RA-10",0.04,0.06,0.08,0.1,0.12,0.16,0.19,0.22,0.25,0.28999999999999998,0.33,0.36,0.38,0.56000000000000005,0.65]
[null,{"$f":"B10*9.8064*1000","v":11834.082708545782},"Па","Kv треб",{"$f":"ROUNDUP(E9/1000/(POWER(E6,0.5)),2)","v":0.57999999999999996},null,"Настройка",1,1.5,2,2.5,3,3.5,4,4.5,5,5.5,6,6.5,7,"N","без т/э"]
[null,null,null,"Kv факт",{"$f":"HLOOKUP(E10,Tab,X17+1)","v":0.52},null,"RA-15",0.04,7.0000000000000007E-2,0.09,0.13,0.16,0.21,0.25,0.31,0.36,0.4,0.43,0.49,0.52,0.73,0.9]
[null,null,null,"ΔРрасч",{"$f":"POWER((E9/E12/1000),2)","v":3.6173113905325453E-2},"бар","Настройка",1,1.5,2,2.5,3,3.5,4,4.5,5,5.5,6,6.5,7,"N","без т/э"]
[{"$nulls":4},{"$f":"E13/0.09806","v":0.36888755767209314},"м.в.ст.","RA-20",0.1,0.13,0.15,0.16,0.17,0.22,0.26,0.31,0.35,0.41,0.46,0.6,0.73,1.04,1.4]
[{"$nulls":4},{"$f":"E14*9.8064*1000","v":3617.4589455556143},"Па","Настройка",1,1.5,2,2.5,3,3.5,4,4.5,5,5.5,6,6.5,7,"N","без т/э"]
[{"$nulls":6},"RA-20(UK)",0.16,0.18,0.2,0.23,0.25,0.3,0.35,0.41,0.47,0.54,0.6,0.67,0.73,0.8,1]
[{"$nulls":6},"Настройка",1,1.5,2,2.5,3,3.5,4,4.5,5,5.5,6,6.5,7,"N","без т/э",null,2]
[{"$nulls":6},"RA-25",0.1,0.13,0.15,0.16,0.17,0.22,0.26,0.31,0.35,0.41,0.46,0.6,0.73,1.04,1.4,null,5]
[{"$nulls":6},"Настройка",1,1.5,2,2.5,3,3.5,4,4.5,5,5.5,6,6.5,7,"N","без т/э",null,1]

{"sheet":"Лист2","index":1,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[]}

{"sheet":"Лист3","index":2,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[]}