{"text_format":"2","workbook":"xlsx","n_sheets":3,"sheets":["Лист1","Лист2","Лист3"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":1,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Лист1","index":0,"n_rows":31,"n_cols":15,"rows_kept":31,"cut":false,"hidden":false,"merged":[[0,0,0,8]]}
["гидравлический расчет системы отопления"]
[]
[]
[]
[]
["№ уч","Q вт","G кг/ч","L  м","D мм","V м/с","R, Па/м","Rl, Па","Рд, Па","∑ξ","Z, Па","RL+Z, Па","∑RL+Z, Па"]
[1,{"$f":"38959+38568","v":77527},{"$f":"B7*0.86/(95-70)","v":2666.9288000000001},28,70,0.19600000000000001,29.43,{"$f":"D7*G7","v":824.04},17.75,9.1999999999999993,{"$f":"J7*I7","v":163.29999999999998},{"$f":"H7+K7","v":987.33999999999992},{"$f":"L7","v":987.33999999999992}]
[2,{"$f":"38959","v":38959},{"$f":"B8*0.86/(95-70)","v":1340.1895999999999},{"$f":"5.5+1.5","v":7},50,0.17100000000000001,8,{"$f":"D8*G8","v":56},14.24,9,{"$f":"J8*I8","v":128.16},{"$f":"H8+K8","v":184.16},{"$f":"M7+L8","v":1171.5}]
[3,{"$f":"B8-4653","v":34306},1180.1264000000001,{"$f":"3.3*5+1+0.6+1.7","v":19.8},40,0.252,22,435.6,30.44,8.6999999999999993,264.82799999999997,700.428,{"$f":"M8+L9","v":1871.9279999999999}]
[4,{"$f":"B9-2647","v":31659},1089.0695999999998,{"$f":"3.3*5+1+0.6+5.8","v":23.900000000000002},40,0.23300000000000001,19,454.1,26.48,8.6999999999999993,230.37599999999998,684.476,{"$f":"M9+L10","v":2556.404}]
[5,{"$f":"B10-4852","v":26807},922.16079999999999,{"$f":"3.3*5+1+0.6+5.1","v":23.200000000000003},40,0.19700000000000001,14,324.80000000000007,17.75,8.6999999999999993,154.42499999999998,479.22500000000002,{"$f":"M10+L11","v":3035.6289999999999}]
[6,{"$f":"B11-4894","v":21913},753.80719999999997,{"$f":"5*3.3+1+0.6+5.6","v":23.700000000000003},32,0.21,19,450.30000000000007,21.57,8.6999999999999993,187.65899999999999,637.95900000000006,3673.5879999999997]
[7,{"$f":"B12-2494","v":19419},668.0136,{"$f":"5*3.3+1+0.6+0.9","v":19},32,0.186,15,285,15.89,8.6999999999999993,138.24299999999999,423.24299999999999,4096.8310000000001]
[8,{"$f":"B13-2494","v":16925},582.22,{"$f":"5*3.3+1+0.6+5.2","v":23.3},32,0.16200000000000001,12,279.60000000000002,38.25,8.6999999999999993,332.77499999999998,612.375,4709.2060000000001]
[9,{"$f":"B14-4893","v":12032},413.9008,{"$f":"5*3.3+1+0.6+5.7","v":23.8},25,0.20200000000000001,26,618.80000000000007,19.61,8.6999999999999993,170.60699999999997,789.40700000000004,5498.6130000000003]
[10,{"$f":"B15-4852","v":7180},246.99200000000002,{"$f":"5*3.3+1+0.6+5.8","v":23.900000000000002},25,0.121,9.5,227.05,7.06,9.1999999999999993,64.951999999999998,292.00200000000001,5790.6150000000007]
[11,{"$f":"B16-2647","v":4533},155.93520000000001,{"$f":"3.3*5+1+3.2","v":20.7},20,0.124,14,289.8,7.06,5.2,36.711999999999996,326.512,6117.1270000000004]
[12,{"$f":"B17-[1]Лист2!D87","v":3508.0949817600003},120.67846737254401,{"$f":"3.3*5-(3.3*4)","v":3.3000000000000007},15,0.17599999999999999,40,132.00000000000003,14.24,5.4,76.896000000000001,208.89600000000002,6326.0230000000001]
[13,{"$f":"B18-[1]Лист2!D88","v":2672.0819635200005},91.919619545088011,3.3,15,0.13400000000000001,24,79.199999999999989,8.34,5.4,45.036000000000001,124.23599999999999,6450.259]
[14,{"$f":"B19-[1]Лист2!D89","v":1836.0819635200005},{"$f":"B20*0.86/(95-70)","v":63.161219545088017},{"$f":"3.3","v":3.3},15,9.2200000000000004E-2,12,39.599999999999994,4.0199999999999996,5.4,21.707999999999998,{"$f":"H20+K20","v":61.307999999999993},{"$f":"M19+L20","v":6511.567}]
[15,{"$f":"B20-[1]Лист2!D89","v":1000.0819635200005},{"$f":"B21*0.86/(95-70)","v":34.402819545088022},1.1000000000000001,15,0.05,3,{"$f":"D21*G21","v":3.3000000000000003},1.23,5.4,{"$f":"J21*I21","v":6.6420000000000003},{"$f":"H21+K21","v":9.9420000000000002},{"$f":"M20+L21","v":6521.509}]
[16,4528,{"$f":"B22*0.86/(95-70)","v":155.76319999999998},{"$f":"3.3*5+1.6+4.3+1","v":23.400000000000002},20,0.124,14,{"$f":"D22*G22","v":327.60000000000002},7.06,5.4,{"$f":"J22*I22","v":38.124000000000002},{"$f":"H22+K22","v":365.72400000000005},{"$f":"L22","v":365.72400000000005}]
[17,{"$f":"B22+4472","v":9000},{"$f":"B23*0.86/(95-70)","v":309.60000000000002},{"$f":"3.3*5+5.3+1","v":22.8},25,0.151,16,{"$f":"D23*G23","v":364.8},11.08,5.4,{"$f":"J23*I23","v":59.832000000000008},{"$f":"H23+K23","v":424.63200000000001},{"$f":"M22+L23","v":790.35599999999999}]
[18,{"$f":"B23+1278","v":10278},{"$f":"B24*0.86/(95-70)","v":353.56319999999999},{"$f":"3.3*5+3+1","v":20.5},25,0.17299999999999999,20,{"$f":"D24*G24","v":410},14.24,9.1999999999999993,{"$f":"J24*I24","v":131.00799999999998},{"$f":"H24+K24","v":541.00800000000004},{"$f":"M23+L24","v":1331.364}]
[19,{"$f":"B24+5635","v":15913},547.40719999999999,{"$f":"3.3*5+5.7+1","v":23.2},32,0.152,12,278.39999999999998,11.08,9.1999999999999993,101.93599999999999,380.33599999999996,{"$f":"M24+L25","v":1711.7}]
[20,{"$f":"B25+2809","v":18722},644.03679999999997,{"$f":"3.3*5+3+1","v":20.5},32,0.17899999999999999,15,307.5,14.24,9.1999999999999993,131.00799999999998,438.50799999999998,2150.2080000000001]
[21,{"$f":"B26+2809","v":21531},740.66639999999995,{"$f":"3.3*5+3.5+1","v":21},32,0.2,19,399,19.61,{"$f":"1.6*5+1.1+1.1","v":10.199999999999999},200.02199999999999,599.02199999999993,2749.23]
[22,{"$f":"B27+5443","v":26974},927.90559999999994,{"$f":"3.3*5+5.1+1","v":22.6},40,0.19800000000000001,15,339,17.75,{"$f":"1.6*5+1.1+1.1","v":10.199999999999999},181.04999999999998,520.04999999999995,3269.2799999999997]
[23,{"$f":"B28+1278","v":28252},971.86880000000008,{"$f":"3.3*5+3.2+1","v":20.7},40,0.20799999999999999,16,331.2,19.61,{"$f":"1.6*5+1.1+1.1","v":10.199999999999999},200.02199999999999,531.22199999999998,3800.5019999999995]
[24,{"$f":"B29+5593","v":33845},1164.268,{"$f":"3.3*5+4.1+2.5+1.6","v":24.700000000000003},40,0.249,24,592.80000000000007,28.44,{"$f":"1.6*5+0.6+0.6","v":9.1999999999999993},261.64799999999997,854.44800000000009,4654.95]
[25,{"$f":"B30+4723","v":38568},{"$f":"B31*0.86/(95-70)","v":1326.7391999999998},{"$f":"3.3*5+4.1+2.5+1.6","v":24.700000000000003},50,0.16900000000000001,8,{"$f":"D31*G31","v":197.60000000000002},12.56,10.199999999999999,{"$f":"J31*I31","v":128.11199999999999},{"$f":"H31+K31","v":325.71199999999999},{"$f":"M30+L31","v":4980.6620000000003},null,{"$f":"(M21-M31)/M21","v":0.2362715439018791}]

{"sheet":"Лист2","index":1,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[]}

{"sheet":"Лист3","index":2,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[]}