{"text_format":"2","workbook":"xls","n_sheets":3,"sheets":["2теплосп, 1технол","1теплосп, 1технол","1теплосп, 2технол"],"not_rendered":{"charts":0,"images":6,"macros":0,"external_links":1,"defined_names":3,"comments":1,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"2теплосп, 1технол","index":0,"n_rows":20,"n_cols":12,"rows_kept":20,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
[null,"Расчет теплового сопровождения"]
[]
[null,"Температура наружного воздуха",{"$nulls":4},-55,"С"]
[null,"Температура сточной жидкости (по зад. технологов)",{"$nulls":4},7,"С"]
[null,"Температура подающей воды",{"$nulls":4},95,"С"]
[null,"Температура обратной воды",{"$nulls":4},70,"С",null,null,"в(угол)",83.62062979155719]
[null,"Скорость ветра",{"$nulls":4},1.6,"м/с",null,null,"Uвн",0.4204614567722998]
[null,"Наружный диаметр нагреваемой трубы",{"$nulls":4},108,"мм",null,0.108,"Uиз",0.797452575203075]
[null,"Наруж. диаметр труб тепл. сопровожд.(теплосети)",{"$nulls":4},38,"мм",null,0.038,"Uнар",0.9231162813466667]
[null,"Толщина теплоизоляции",{"$nulls":4},60,"мм",null,0.06,"dвн",0.13383703844986158]
[null,"Толщина защитного слоя кожуха",{"$nulls":4},20,"мм",null,0.02,"dиз",0.2538370384498616]
[null,"Коэффициент теплопроводности теплоизоляции",{"$nulls":4},0.065,"ккал/м*ч*град",null,null,"dнар",0.2938370384498616]
[null,"Коэффициент теплопроводности защитн слоя кожуха",{"$nulls":4},0.8,"ккал/м*ч*град",null,null,"коэ теплоп нар пов труб",5.3]
[null,"а -расстояние между теплоспутниками (см. рисунок)",{"$nulls":4},100,"мм",null,0.1,"Ккан",0.5724]
[null,"m - расстояние между теплоспутником и ",{"$nulls":4},75,"мм",null,0.075,"Ксп",0.2014]
[null,"       обогреваемым трубопроводом (см. рисунок)",{"$nulls":8},"Кк",0.18017938961997662]
[{"$nulls":10},"коэ теплоп нар пов труб",6.3617515566227585]
[]
[null,"Температура внутри кожуха",{"$nulls":4},23.652779179218257,"С",null,null,23.652779179218257]
[null,"Расход тепла на обогрев 1м трубы",{"$nulls":4},74.46724583641898,"ккал/м*ч",null,null,74.46724583641898]

{"sheet":"1теплосп, 1технол","index":1,"n_rows":29,"n_cols":12,"rows_kept":29,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
[null,"Расчет теплового сопровождения"]
[]
[null,"Температура наружного воздуха",{"$nulls":4},-41,"С"]
[null,"Температура сточной жидкости (по зад. технологов)",{"$nulls":4},5,"С"]
[null,"Температура воды в теплоспутнике",{"$nulls":4},70,"С",null,null,null,27.74827254032531]
[null,"Скорость ветра",{"$nulls":4},3,"м/с",null,null,"в(угол)",124.50345491934938]
[null,"Наружный диаметр нагреваемой трубы",{"$nulls":4},159,"мм",null,0.159,"Uвн",0.5980470212044929]
[null,"Наруж. диаметр труб тепл. сопровожд.(теплосети)",{"$nulls":4},38,"мм",null,0.038,"Uиз",0.9122062865634722]
[null,"Толщина теплоизоляции",{"$nulls":4},50,"мм",null,0.05,"Uнар",0.9153478792170621]
[null,"Толщина защитного слоя кожуха",{"$nulls":4},0.5,"мм",null,0.0005,"dвн",0.1903642792521572]
[null,"Коэффициент теплопроводности теплоизоляции",{"$nulls":4},0.0301,"ккал/м*ч*град",null,null,"dиз",0.2903642792521572]
[null,"Коэффициент теплопроводности защитн слоя кожуха",{"$nulls":4},190,"ккал/м*ч*град",null,null,"dнар",0.2913642792521572]
[null,"m - расстояние между теплоспутником и ",{"$nulls":4},115,"мм",null,0.115,"коэ теплоп нар пов труб",5.3]
[null,"       обогреваемым трубопроводом (см. рисунок)",{"$nulls":8},"Ккан",0.8427]
[{"$nulls":9},0.115,"Ксп",0.2014]
[{"$nulls":10},"Кк",0.13546496116839926]
[{"$nulls":10},"коэ теплоп нар пов труб",9.307768228938672]
[]
[null,"Температура внутри кожуха",{"$nulls":4},10.815374321952524,"С",null,null,10.815374321952524]
[null,"Расход тепла на обогрев 1м трубы",{"$nulls":4},37.44710462645302,"ккал/м*ч",null,null,37.44710462645302]
[]
[null,"dвн",0.1903642792521572]
[null,"dиз",0.2903642792521572]
[]
[]
[]
[null,"Коэффициент теплопроводности:"]
[null,"Базальтовое волокно",null,null,null,0.0385,"ккал/м*ч*град"]
[null,"URSA",null,null,null,0.0301,"ккал/м*ч*град"]

{"sheet":"1теплосп, 2технол","index":2,"n_rows":22,"n_cols":12,"rows_kept":22,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
[null,"Расчет теплового сопровождения"]
[]
[null,"Температура наружного воздуха",{"$nulls":4},-39,"С"]
[null,"Температура жидкости в 1 трубе (по зад. технологов)",{"$nulls":4},7,"С"]
[null,"Температура жидкости во 2 трубе (по зад. технологов)",{"$nulls":4},10,"С"]
[null,"Температура воды в теплоспутнике",{"$nulls":4},95,"С",null,null,null,9.648045316098157]
[null,"Скорость ветра",{"$nulls":4},1.6,"м/с",null,null,"в(угол)",160.70390936780367]
[null,"Наружный диаметр нагреваемой 1 трубы",{"$nulls":4},108,"мм",null,0.108,"Uвн",0.5677692919356819]
[null,"Наружный диаметр нагреваемой 2 трубы",{"$nulls":4},57,"мм",null,0.057]
[null,"Наруж. диаметр труб тепл. сопровожд.(теплосети)",{"$nulls":4},38,"мм",null,0.038,"Uиз",0.9447604103664571]
[null,"Толщина теплоизоляции",{"$nulls":4},60,"мм",null,0.06,"Uнар",1.0704241165100488]
[null,"Толщина защитного слоя кожуха",{"$nulls":4},20,"мм",null,0.02,"dвн",0.18072657869469835]
[null,"Коэффициент теплопроводности теплоизоляции",{"$nulls":4},0.065,"ккал/м*ч*град",null,null,"dиз",0.3007265786946983]
[null,"Коэффициент теплопроводности защитн слоя кожуха",{"$nulls":4},0.8,"ккал/м*ч*град",null,null,"dнар",0.3407265786946983]
[null,"m - расстояние между теплоспутником и ",{"$nulls":4},75,"мм",null,0.075,"коэ теплоп нар пов труб",5.3]
[null,"       обогреваемым трубопроводом (см. рисунок)",{"$nulls":8},"Ккан1",0.5724]
[{"$nulls":10},"Ккан2",0.3021]
[{"$nulls":10},"Ксп",0.2014]
[{"$nulls":10},"Кк",0.2229863528771112]
[{"$nulls":10},"коэ теплоп нар пов труб",5.99593498448622]
[null,"Температура внутри кожуха",{"$nulls":4},13.445619933651717,"С",null,null,13.445619933651717]
[null,"Расход тепла на обогрев 1м трубы",{"$nulls":4},51.60082315470024,"ккал/м*ч",null,null,51.60082315470024]