{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Лист1"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":0,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Лист1","index":0,"n_rows":40,"n_cols":5,"rows_kept":40,"cut":false,"hidden":false,"merged":[[2,2,2,4],[33,3,33,4]],"flags":["formulas_cached_only"]}
[null,null,null,"Приложение  ","№ 2"]
[]
[null,null,"Аэродинамический  расчет  дымовой трубы"]
[null,null,"для 3-х котлов КВ-ГМ-11,63-150 на газе"]
[]
[]
[null,"№ п/п","Наименование","ед.измер","Значение"]
[null,1,"мощность котла ","кВт",34890]
[null,2,"низшая теплота сгорания ","ккал/нм3",8600]
[null,3,"кпд котла",null,0.912]
[null,4,"расход газа на котёл","м3/ч",3825.6578947368416]
[null,5,"теор. объём воздуха на горение   "," м3/м3",9.546]
[null,6," Коэффициент расчёта п.г.         ",null,1.24]
[null,7,"K = 1000",null,1000]
[null,8,"Теор. объём продуктов сгорания                  "," м3/м3",10.664]
[null,9,"Действительный объём продуктов      "]
[null,null,"сгорания","м3/ч",73665.18681318678]
[null,10,"Диаметр трубы","м",1.3]
[null,11,"Площадь сечения газохода","м2",1.3182]
[null,12,"Скорость продуктов сгорания ","м/с",15.523101117092915]
[null,null,"в газоходе"]
[null,13,"Падение т-ры на 1м газохода","0С/м",0.7452007615279501]
[null,14,"Падение т-ры по всей длине ","0С",37.26003807639751]
[null,15,"Т-ра в конце газохода","0С",107.7399619236025]
[]
[null,16,"L (высота трубы ориентировочно)","м",50]
[null,17,"Cредняя т-ра прод.горения","0С",126.36998096180125]
[null,18,"Плотность газов при ср.т-ре","кг/м3",0.915992732150266]
[null,19,"Сопр. дымовой трубы","кг/м2",10.31389224526308]
[null,20,"Мест.сопр.(повороты 450 и 900)","кг/м2",11.249934599667178]
[null,21,"Сопр. на выходе трубы","кг/м2",12.374928059633895]
[null,22,"Сумма сопротивлений","кг/м2",33.93875490456415]
[null,23,"Самотяга дымовой трубы","кг/м2",21.241626794258366]
[null,24,"Расчет выполнен правильно если:","E33>D32 при ест. тяге"]
[null,25,"Коэф. избытка в-ха за котлом",null,1.2]
[null,26,"Т-ра продуктов сгорания за котлом","0С",145]
[null,27,"Поворот 90˚","ξ",1]
[null,28,"Сопр. на выходе трубы","ξвых",1.1]
[null,null,"Высота трубы считается от врезки"]
[null,null," газохода котла"]