{"text_format":"2","workbook":"xls","n_sheets":3,"sheets":["Лист1","Лист2","Лист3"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":0,"defined_names":0,"comments":165,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Лист1","index":0,"n_rows":326,"n_cols":22,"rows_kept":326,"cut":false,"hidden":false,"merged":[[324,11,324,13],[314,0,314,2],[317,11,317,13],[320,0,320,16],[321,0,321,2],[306,0,306,16],[307,0,307,2],[310,11,310,13],[313,0,313,16],[296,11,296,13],[299,0,299,16],[300,0,300,2],[303,11,303,13],[286,0,286,2],[289,11,289,13],[292,0,292,16],[293,0,293,2],[278,0,278,16],[279,0,279,2],[282,11,282,13],[285,0,285,16],[264,0,264,16],[275,11,275,13],[265,0,265,2],[268,11,268,13],[271,0,271,16],[272,0,272,2],[254,11,254,13],[257,0,257,16],[258,0,258,2],[261,11,261,13],[244,0,244,2],[247,11,247,13],[250,0,250,16],[251,0,251,2],[236,0,236,16],[237,0,237,2],[240,11,240,13],[243,0,243,16],[226,11,226,13],[229,0,229,16],[230,0,230,2],[233,11,233,13],[216,0,216,2],[219,11,219,13],[222,0,222,16],[223,0,223,2],[208,0,208,16],[209,0,209,2],[212,11,212,13],[215,0,215,16],[6,5,7,13],[201,0,201,16],[202,0,202,2],[205,11,205,13],[90,0,90,16],[91,0,91,2],[94,11,94,13],[14,0,14,16],[15,0,15,2],[97,0,97,16],[50,29,50,31],[54,0,54,2],[87,11,87,13],[53,0,53,16],[50,11,50,13],[98,0,98,2],[101,11,101,13],[104,0,104,16],[105,0,105,2],[108,11,108,13],[111,0,111,16],[112,0,112,2],[115,11,115,13],[118,0,118,16],[119,0,119,2],[122,11,122,13],[124,0,124,16],[125,0,125,2],[128,11,128,13],[131,0,131,16],[132,0,132,2],[135,11,135,13],[138,0,138,16],[139,0,139,2],[142,11,142,13],[145,0,145,16],[146,0,146,2],[149,11,149,13],[152,0,152,16],[153,0,153,2],[156,11,156,13],[159,0,159,16],[160,0,160,2],[163,11,163,13],[166,0,166,16],[167,0,167,2],[170,11,170,13],[173,0,173,16],[174,0,174,2],[177,11,177,13],[180,0,180,16],[181,0,181,2],[184,11,184,13],[187,0,187,16],[198,11,198,13],[188,0,188,2],[191,11,191,13],[194,0,194,16],[195,0,195,2]],"flags":["formulas_cached_only"]}
["d","l/d ","G / V","A * 10 -4","D мм"]
[1,2,3,4,15]
[15,2.69,685,10.5,20]
[20,1.79,1250,3.15,25]
[25,1.3,2040,1.18,32]
[32,0.895,3580,0.383,40]
[40,0.753,4670,0.225,50,"Гидравлический Расчет однотрубной системы "]
[50,0.54,7810,0.0806,70]
[70,0.377,13600,0.0265,80]
[80,0.304,19200,0.0134,null,null,"для стальных труб D от 15 до 80 мм."]
[100,0.237,28400,0.00611,null,null,"в температурном диапазоне от 60 до 130 С"]
[120,0.181,43400,0.00261,null,null,"t вх",95]
[150,0.144,62600,0.00126,null,null,"t вых",70]
[]
["Расчет системы отопления"]
["№ уч",null,null,"Q вт","G кг/ч","G л/сек","L  м","D мм","l/d ","G / V","A * 10 -4","V м/с","S z","S *10 -4","D P Па","S D P Па","S D P м.в.ст."]
[0,"-",0,90174.2,3747.387341772151,1.040940928270042,10,50,0.0806,7810,0.0806,0.4798191218658324,0,6.496360000000001e-06,91.22781108100502,91.22781108100502,0.0091227811081005]
[1,"-",0,44325.3,1842.0353952710768,0.5116764986864102,2,32,0.383,3580,0.383,0.5145350266120327,0,2.9337800000000002e-05,99.54592481296505,99.54592481296505,0.009954592481296506]
[2,"-",0,42454.5,1764.290183902555,0.4900806066395986,1.2,32,0.383,3580,0.383,0.49281848712361875,0,1.7602680000000002e-05,54.79221150226853,154.33813631523358,0.015433813631523359]
[3,"-",0,41554.5,1726.8887031287313,0.4796913064246476,0.5,32,0.383,3580,0.383,0.48237114612534393,0,7.3344500000000006e-06,21.872390410082144,176.21052672531573,0.017621052672531574]
[4,"-",0,39995.5,1662.1010269882968,0.46169472971897135,4,32,0.383,3580,0.383,0.4642740298849991,0,5.8675600000000005e-05,162.0960287161393,338.30655544145503,0.0338306555441455]
[5,"-",0,35162.6,1461.259230952949,0.40590534193137473,6,32,0.383,3580,0.383,0.40817296953992993,0,8.801340000000001e-05,187.9331242564146,526.2396796978696,0.05262396796978697]
[6,"-",0,31421,1305.7688082159061,0.3627135578377517,4.5,25,1.18,2040,1.18,0.6400827491254442,0,0.00062658,1068.3390636636975,1594.5787433615671,0.1594578743361567]
[7,null,null,28926.6,1202.1085263912105,0.3339190351086696,5,25,1.18,2040,1.18,0.5892688854858875,0,0.0006961999999999999,1006.0541898006678,2600.632933162235,0.2600632933162235]
[8,null,null,24873.2,1033.6605684260805,0.28712793567391126,4,25,1.18,2040,1.18,0.5066963570716081,0,0.0005569599999999999,595.0862349236139,3195.719168085849,0.31957191680858493]
[9,null,null,23002.4,955.915357057559,0.26553204362709976,2,25,1.18,2040,1.18,0.4685859593419407,0,0.00027847999999999995,254.46783082218963,3450.1869989080387,0.34501869989080386]
[10,null,null,22102.4,918.5138762837353,0.2551427434121487,3.7,25,1.18,2040,1.18,0.4502519001390859,0,0.000515188,434.6474961120671,3884.834495020106,0.3884834495020106]
[11,null,null,17425.4,724.1508478624313,0.2011530132951198,4.8,25,1.18,2040,1.18,0.3549759058149173,0,0.000668352,350.48007975376044,4235.314574773866,0.42353145747738663]
[12,null,null,13683.8,568.660425125388,0.15796122920149666,1,25,1.18,2040,1.18,0.2787551103555823,0,0.00013923999999999997,45.02669031841129,4280.341265092277,0.42803412650922773]
[13,null,null,11033.5,458.5213756866491,0.12736704880184696,3,20,1.79,1250,3.15,0.36681710054931926,0,0.0016915500000000002,355.63460468560595,4635.975869777883,0.46359758697778836]
[14,null,null,8383.2,348.38232624791016,0.09677286840219726,2.8,20,1.79,1250,3.15,0.2787058609983281,0,0.00157878,191.61691578301526,4827.592785560899,0.4827592785560899]
[15,null,null,3706.2,154.01929782660613,0.04278313828516837,3.8,20,1.79,1250,3.15,0.12321543826128491,0,0.00214263,50.82734909341261,4878.420134654311,0.48784201346543116]
["16 п/с",null,"ст.17",900,37.401480773823735,0.010389300214951037,21.8,15,2.69,685,10.5,0.054600701859596694,12.7,0.0749091,104.78814995314862,4983.20828460746,0.498320828460746]
[17,null,null,3706.2,154.01929782660613,0.04278313828516837,3.8,20,1.79,1250,3.15,0.12321543826128491,0,0.00214263,50.82734909341261,5034.0356337008725,0.5034035633700873]
[18,null,null,8383.2,348.38232624791016,0.09677286840219726,2.8,25,1.18,2040,1.18,0.1707756501215246,0,0.00038987199999999993,47.3188602529521,5081.354493953824,0.5081354493953825]
[19,null,null,11033.5,458.5213756866491,0.12736704880184696,3,25,1.18,2040,1.18,0.22476538023855347,0,0.00041772,87.82222640139003,5169.1767203552145,0.5169176720355214]
[20,null,null,13683.8,568.660425125388,0.15796122920149666,1,25,1.18,2040,1.18,0.2787551103555823,0,0.00013923999999999997,45.02669031841129,5214.2034106736255,0.5214203410673626]
[21,null,null,17425.4,724.1508478624313,0.2011530132951198,4.8,25,1.18,2040,1.18,0.3549759058149173,0,0.000668352,350.48007975376044,5564.683490427386,0.5564683490427386]
[22,null,null,22102.4,918.5138762837353,0.2551427434121487,3.7,25,1.18,2040,1.18,0.4502519001390859,0,0.000515188,434.6474961120671,5999.330986539453,0.5999330986539453]
[23,null,null,23002.4,955.915357057559,0.26553204362709976,2,25,1.18,2040,1.18,0.4685859593419407,0,0.00027847999999999995,254.46783082218963,6253.798817361643,0.6253798817361643]
[24,null,null,24873.2,1033.6605684260805,0.28712793567391126,4,25,1.18,2040,1.18,0.5066963570716081,0,0.0005569599999999999,595.0862349236139,6848.885052285257,0.6848885052285257]
[25,null,null,28926.6,1202.1085263912105,0.3339190351086696,5,25,1.18,2040,1.18,0.5892688854858875,0,0.0006961999999999999,1006.0541898006678,7854.939242085925,0.7854939242085925]
[26,null,null,31421,1305.7688082159061,0.3627135578377517,4.5,25,1.18,2040,1.18,0.6400827491254442,0,0.00062658,1068.3390636636975,8923.278305749622,0.8923278305749621]
[27,null,null,35162.6,1461.259230952949,0.40590534193137473,6,32,0.383,3580,0.383,0.40817296953992993,0,8.801340000000001e-05,187.9331242564146,9111.211430006037,0.9111211430006037]
[28,null,null,39995.5,1662.1010269882968,0.46169472971897135,4,32,0.383,3580,0.383,0.4642740298849991,0,5.8675600000000005e-05,162.0960287161393,9273.307458722176,0.9273307458722176]
[29,null,null,41554.5,1726.8887031287313,0.4796913064246476,0.5,32,0.383,3580,0.383,0.48237114612534393,0,7.3344500000000006e-06,21.872390410082144,9295.179849132259,0.9295179849132259]
[30,null,null,42454.5,1764.290183902555,0.4900806066395986,1.2,32,0.383,3580,0.383,0.49281848712361875,0,1.7602680000000002e-05,54.79221150226853,9349.972060634527,0.9349972060634527]
[31,null,null,88303.4,3669.642130403629,1.0193450362232304,2,32,0.383,3580,0.383,1.025039701230064,0,2.9337800000000002e-05,395.07083473454105,9745.042895369068,0.9745042895369068]
[32,null,null,88615.2,3682.599665631716,1.0229443515643657,5,50,0.0806,7810,0.0806,0.47152364476718517,0,3.2481800000000004e-06,44.05032396291909,9789.093219331988,0.9789093219331988]
[{"$nulls":13},"Сумма",9880.321030412992,"Па"]
[{"$nulls":11},"Местн. Сопротивления",null,null,3952.128412165197,0.4,null,"%","∆Р","dш."]
[{"$nulls":13},"Сумма",13832.449442578189,"Па",null,3.001385469930357,0.04280113996641703,4.804619591531766]
[]
["Расчет системы "]
["№ уч",null,null,"Q вт","G кг/ч","G л/сек","L  м","D мм","l/d ","G / V","A * 10 -4","V м/с","S z","S *10 -4","D P Па","S D P Па","S D P м.в.ст."]
[33,"-",0,45848.9,1905.3519465010745,0.5292644295836318,1,32,0.383,3580,0.383,0.5322212141064454,0,1.4668900000000001e-05,53.25347640467577,53.25347640467577,0.005325347640467578]
[34,"-",0,43078.1,1790.205254358729,0.4972792373218692,2.8,32,0.383,3580,0.383,0.5000573336197567,0,4.107292e-05,131.631925519539,184.8854019242148,0.01848854019242148]
[35,"-",0,41051.4,1705.9812753761641,0.47388368760449007,5.2,32,0.383,3580,0.383,0.4765310825073084,0,7.627828e-05,221.99817885829935,406.8835807825142,0.04068835807825142]
[36,"-",0,38557,1602.3209935514685,0.4450891648754079,1,32,0.383,3580,0.383,0.4475756965227566,0,1.4668900000000001e-05,37.661411572909465,444.54499235542363,0.044454499235542365]
[37,"-",0,35750.8,1485.7031764986864,0.41269532680519067,3.5,32,0.383,3580,0.383,0.41500088729013584,0,5.134115e-05,113.32603550833441,557.8710278637581,0.0557871027863758]
[38,"-",0,32788.7,1362.6065918318602,0.3785018310644056,4.5,25,1.18,2040,1.18,0.6679444077607158,0,0.00062658,1163.3690333888574,1721.2400612526153,0.17212400612526152]
[39,null,null,30762,1278.3826128492951,0.35510628134702643,0.5,25,1.18,2040,1.18,0.6266581435535761,0,6.961999999999999e-05,113.77732773863988,1835.0173889912553,0.18350173889912552]
[40,null,null,29862,1240.9811320754714,0.3447169811320754,0.7,25,1.18,2040,1.18,0.6083240843507213,0,9.746799999999998e-05,150.10405049786817,1985.1214394891235,0.19851214394891234]
[41,null,null,27991.2,1163.2359207069499,0.3231210890852638,2.8,25,1.18,2040,1.18,0.5702136866210539,0,0.00038987199999999993,527.542745737624,2512.6641852267476,0.2512664185226748]
[43,null,null,24285,1009.2166228803437,0.2803379508000955,6.5,25,1.18,2040,1.18,0.4947140308236979,0,0.00090506,921.8200747592092,3434.4842599859567,0.34344842599859565]
[44,null,null,17893.1,743.5871507045615,0.20655198630682264,3.5,25,1.18,2040,1.18,0.36450350524733405,0,0.00048733999999999995,269.46093471669167,3703.945194702648,0.3703945194702648]
[45,null,null,14619.2,607.5330308096488,0.16875917522490244,2.6,25,1.18,2040,1.18,0.29781030922041607,0,0.000362024,133.62174914916687,3837.5669438518153,0.3837566943851815]
[46,null,null,10098.1,419.6487700023883,0.1165691027784412,5,20,1.79,1250,3.15,0.3357190160019106,0,0.0028192499999999997,496.48427544631556,4334.0512192981305,0.43340512192981306]
[47,null,null,5732.9,238.2432768091712,0.06617868800254756,4.1,20,1.79,1250,3.15,0.19059462144733696,0,0.002311785,131.21659051063827,4465.267809808769,0.4465267809808769,null,"пр-лев"]
[48,null,null,2926.7,121.62545975638879,0.03378484993233022,2.8,20,1.79,1250,3.15,0.09730036780511103,0,0.00157878,23.354501730303298,4488.622311539072,0.4488622311539072,null,-10.445097243668664]
["49 п/с",null,"ст.36",900,37.401480773823735,0.010389300214951037,21.8,15,2.69,685,10.5,0.054600701859596694,12.7,0.0749091,104.78814995314862,4593.410461492221,0.45934104614922205]
[50,null,null,2926.7,121.62545975638879,0.03378484993233022,2.8,25,1.18,2040,1.18,0.059620323409994506,0,0.00038987199999999993,5.767279987456647,4599.177741479677,0.4599177741479677]
[51,null,null,5732.9,238.2432768091712,0.06617868800254756,4.1,25,1.18,2040,1.18,0.11678592000449568,0,0.0005708839999999999,32.40329531382685,4631.581036793504,0.4631581036793504]
[52,null,null,10098.1,419.6487700023883,0.1165691027784412,5,25,1.18,2040,1.18,0.20571018137371974,0,0.0006961999999999999,122.60436377253697,4754.185400566041,0.47541854005660406]
[53,null,null,14619.2,607.5330308096488,0.16875917522490244,2.6,25,1.18,2040,1.18,0.29781030922041607,0,0.000362024,133.62174914916687,4887.807149715208,0.48878071497152076]
[42,null,null,17893.1,743.5871507045615,0.20655198630682264,3.5,25,1.18,2040,1.18,0.36450350524733405,0,0.00048733999999999995,269.46093471669167,5157.268084431899,0.51572680844319]
[54,null,null,24285,1009.2166228803437,0.2803379508000955,6.5,25,1.18,2040,1.18,0.4947140308236979,0,0.00090506,921.8200747592092,6079.088159191108,0.6079088159191108]
[55,null,null,27991.2,1163.2359207069499,0.3231210890852638,2.8,25,1.18,2040,1.18,0.5702136866210539,0,0.00038987199999999993,527.542745737624,6606.630904928732,0.6606630904928732]
[56,null,null,29862,1240.9811320754714,0.3447169811320754,0.7,25,1.18,2040,1.18,0.6083240843507213,0,9.746799999999998e-05,150.10405049786817,6756.7349554266,0.67567349554266]
[57,null,null,30762,1278.3826128492951,0.35510628134702643,0.5,25,1.18,2040,1.18,0.6266581435535761,0,6.961999999999999e-05,113.77732773863988,6870.51228316524,0.687051228316524]
[58,null,null,32788.7,1362.6065918318602,0.3785018310644056,4.5,25,1.18,2040,1.18,0.6679444077607158,0,0.00062658,1163.3690333888574,8033.881316554097,0.8033881316554097]
[59,null,null,35750.8,1485.7031764986864,0.41269532680519067,3.5,32,0.383,3580,0.383,0.41500088729013584,0,5.134115e-05,113.32603550833441,8147.207352062432,0.8147207352062432]
[60,null,null,38557,1602.3209935514685,0.4450891648754079,1,32,0.383,3580,0.383,0.4475756965227566,0,1.4668900000000001e-05,37.661411572909465,8184.868763635342,0.8184868763635341]
[61,null,null,41051.4,1705.9812753761641,0.47388368760449007,5.2,32,0.383,3580,0.383,0.4765310825073084,0,7.627828e-05,221.99817885829935,8406.866942493642,0.8406866942493642]
[62,null,null,43078.1,1790.205254358729,0.4972792373218692,2.8,32,0.383,3580,0.383,0.5000573336197567,0,4.107292e-05,131.631925519539,8538.498868013181,0.8538498868013181]
[63,null,null,45848.9,1905.3519465010745,0.5292644295836318,1,32,0.383,3580,0.383,0.5322212141064454,0,1.4668900000000001e-05,53.25347640467577,8591.752344417857,0.8591752344417857]
[{"$nulls":13},"Сумма",9122.101314196323,"Па"]
[{"$nulls":11},"Местн. Сопротивления",null,null,3648.8405256785295,0.4,null,"%","∆Р","dш."]
[{"$nulls":13},"Сумма",12770.941839874853,"Па",null,{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"}]
[]
["Расчет системы "]
["№ уч",null,null,"Q вт","G кг/ч","G л/сек","L  м","D мм","l/d ","G / V","A * 10 -4","V м/с","S z","S *10 -4","D P Па","S D P Па","S D P м.в.ст."]
[64,"-","ст.16",2806.2,116.61781705278239,0.032393838070217326,6,20,1.79,1250,3.15,0.0932942536422259,32.3,0.0135576,184.3794995297484,184.3794995297484,0.01843794995297484]
[{"$nulls":13},"Сумма",9959.912379989591,"Па"]
[{"$nulls":11},"Местн. Сопротивления",null,null,3983.9649519958366,0.4,null,"%","∆Р","dш."]
[{"$nulls":13},"Сумма",13943.877331985428,"Па",null,2.220008972775597,0.03165835102569308,9.1482668608884]
[]
["Расчет системы "]
["№ уч",null,null,"Q вт","G кг/ч","G л/сек","L  м","D мм","l/d ","G / V","A * 10 -4","V м/с","S z","S *10 -4","D P Па","S D P Па","S D P м.в.ст."]
[65,"-","ст.15",4677,194.363028421304,0.053989730117028886,6,20,1.79,1250,3.15,0.1554904227370432,32.3,0.0135576,512.1652764715234,512.1652764715234,0.051216527647152336]
[{"$nulls":13},"Сумма",10186.043458744542,"Па"]
[{"$nulls":11},"Местн. Сопротивления",null,null,4074.417383497817,0.4]
[{"$nulls":13},"Сумма",14260.460842242359,"Па"]
[]
["Расчет системы "]
["№ уч",null,null,"Q вт","G кг/ч","G л/сек","L  м","D мм","l/d ","G / V","A * 10 -4","V м/с","S z","S *10 -4","D P Па","S D P Па","S D P м.в.ст."]
[66,"-","ст.14",2650.3,110.13904943873895,0.030594180399649708,6,20,1.79,1250,3.15,0.08811123955099116,32.3,0.0135576,164.46196100030033,164.46196100030033,0.016446196100030033]
[{"$nulls":13},"Сумма",9599.404367237352,"Па"]
[{"$nulls":11},"Местн. Сопротивления",null,null,3839.761746894941,0.4,null,"%","∆Р","dш."]
[{"$nulls":13},"Сумма",13439.166114132293,"Па",null,5.759243948675385,0.0821294728110066,7.0052614185045305]
[]
["Расчет системы "]
["№ уч",null,null,"Q вт","G кг/ч","G л/сек","L  м","D мм","l/d ","G / V","A * 10 -4","V м/с","S z","S *10 -4","D P Па","S D P Па","S D P м.в.ст."]
[67,"-","ст.13",2650.3,110.13904943873895,0.030594180399649708,6,20,1.79,1250,3.15,0.08811123955099116,32.3,0.0135576,164.46196100030033,164.46196100030033,0.016446196100030033]
[{"$nulls":13},"Сумма",9155.947536150356,"Па"]
[{"$nulls":11},"Местн. Сопротивления",null,null,3662.3790144601426,0.4,null,"%","∆Р","dш."]
[{"$nulls":13},"Сумма",12818.326550610498,"Па",null,10.112816882887603,0.14421342916318608,6.08551979607995]
[]
["Расчет системы "]
["№ уч",null,null,"Q вт","G кг/ч","G л/сек","L  м","D мм","l/d ","G / V","A * 10 -4","V м/с","S z","S *10 -4","D P Па","S D P Па","S D P м.в.ст."]
[68,"-","ст.12",3741.6,155.4904227370432,0.043191784093623106,6,20,1.79,1250,3.15,0.12439233818963455,32.3,0.0135576,327.785776941775,327.785776941775,0.032778577694177496]
[{"$nulls":13},"Сумма",9229.217971455008,"Па"]
[{"$nulls":11},"Местн. Сопротивления",null,null,3691.6871885820033,0.4,null,"%","∆Р","dш."]
[{"$nulls":13},"Сумма",12920.905160037011,"Па",null,9.393495042161007,0.13395556822053478,7.365293756903091]
["Расчет системы "]
["№ уч",null,null,"Q вт","G кг/ч","G л/сек","L  м","D мм","l/d ","G / V","A * 10 -4","V м/с","S z","S *10 -4","D P Па","S D P Па","S D P м.в.ст."]
["68а","-","ст.11",1650.3,68.58184857893478,0.01905051349414855,6,20,1.79,1250,3.15,0.054865478863147826,32.3,0.0135576,63.76776425518259,63.76776425518259,0.006376776425518259]
[{"$nulls":13},"Сумма",8264.239799260895,"Па"]
[{"$nulls":11},"Местн. Сопротивления",null,null,3305.695919704358,0.4,null,"%","∆Р","dш."]
[{"$nulls":13},"Сумма",11569.935718965253,"Па",null,18.8670278824877,0.12105251232771061,5.016947833180355,0.148,4.771089990831494]
[]
["Расчет системы "]
["№ уч",null,null,"Q вт","G кг/ч","G л/сек","L  м","D мм","l/d ","G / V","A * 10 -4","V м/с","S z","S *10 -4","D P Па","S D P Па","S D P м.в.ст."]
[69,"-","ст.10",2026.7,84.22397898256506,0.023395549717379182,6,20,1.79,1250,3.15,0.06737918318605204,32.3,0.0135576,96.17325747076382,96.17325747076382,0.009617325747076381]
[{"$nulls":13},"Сумма",8296.645292476476,"Па"]
[{"$nulls":11},"Местн. Сопротивления",null,null,3318.6581169905908,0.4,null,"%","∆Р","dш."]
[{"$nulls":13},"Сумма",11615.303409467067,"Па",null,18.54889166652877,0.26451574327752914,4.572812977503199]
[]
["Расчет системы "]
["№ уч",null,null,"Q вт","G кг/ч","G л/сек","L  м","D мм","l/d ","G / V","A * 10 -4","V м/с","S z","S *10 -4","D P Па","S D P Па","S D P м.в.ст."]
[70,"-","ст.9",900,37.401480773823735,0.010389300214951037,21.8,15,2.69,685,10.5,0.054600701859596694,12.7,0.0749091,104.78814995314862,104.78814995314862,0.010478814995314861]
[{"$nulls":13},"Сумма",7435.965192734726,"Па"]
[{"$nulls":11},"Местн. Сопротивления",null,null,2974.3860770938904,0.4,null,"%","∆Р","dш."]
[{"$nulls":13},"Сумма",10410.351269828616,"Па",null,26.998493351694098,0.3850109572413743,2.7743073312220403,0.03,5.251006165524857]
[]
["Расчет системы "]
["№ уч",null,null,"Q вт","G кг/ч","G л/сек","L  м","D мм","l/d ","G / V","A * 10 -4","V м/с","S z","S *10 -4","D P Па","S D P Па","S D P м.в.ст."]
[71,"-","ст.8",1870.8,77.7452113685216,0.021595892046811553,6,20,1.79,1250,3.15,0.062196169094817275,32.3,0.0135576,81.94644423544375,81.94644423544375,0.008194644423544374]
[{"$nulls":13},"Сумма",6904.187825372643,"Па"]
[{"$nulls":11},"Местн. Сопротивления",null,null,2761.675130149057,0.4,null,"%","∆Р","dш."]
[{"$nulls":13},"Сумма",9665.8629555217,"Па",null,32.21914030373082,0.45945978867206594,3.8269553097944935]
[]
["Расчет системы "]
["№ уч",null,null,"Q вт","G кг/ч","G л/сек","L  м","D мм","l/d ","G / V","A * 10 -4","V м/с","S z","S *10 -4","D P Па","S D P Па","S D P м.в.ст."]
[72,"-","ст.7",4053.4,168.44795796513012,0.046791099434758364,6,20,1.79,1250,3.15,0.1347583663721041,32.3,0.0135576,384.69302988305526,384.69302988305526,0.038469302988305525]
[{"$nulls":13},"Сумма",6016.761941173025,"Па"]
[{"$nulls":11},"Местн. Сопротивления",null,null,2406.70477646921,0.4,null,"%","∆Р","dш."]
[{"$nulls":13},"Сумма",8423.466717642235,"Па",null,40.93131483738429,0.5836994124600123,5.305960404069032]
[]
["Расчет системы "]
["№ уч",null,null,"Q вт","G кг/ч","G л/сек","L  м","D мм","l/d ","G / V","A * 10 -4","V м/с","S z","S *10 -4","D P Па","S D P Па","S D P м.в.ст."]
[73,"-","ст.6",2494.4,103.66028182469547,0.028794522729082075,6,20,1.79,1250,3.15,0.08292822545975638,32.3,0.0135576,145.6825675296778,145.6825675296778,0.014568256752967782]
[{"$nulls":13},"Сумма",3765.643099218312,"Па"]
[{"$nulls":11},"Местн. Сопротивления",null,null,1506.2572396873247,0.4,null,"%","∆Р","dш."]
[{"$nulls":13},"Сумма",5271.900338905636,"Па",null,63.03134662177814,0.8988560503336723,3.7364751613926925]
[]
["Расчет системы "]
["№ уч",null,null,"Q вт","G кг/ч","G л/сек","L  м","D мм","l/d ","G / V","A * 10 -4","V м/с","S z","S *10 -4","D P Па","S D P Па","S D P м.в.ст."]
[74,"-","ст.5",3741.6,155.4904227370432,0.043191784093623106,6,20,1.79,1250,3.15,0.12439233818963455,32.3,0.0135576,327.785776941775,327.785776941775,0.032778577694177496]
[{"$nulls":13},"Сумма",1811.0681813030142,"Па"]
[{"$nulls":11},"Местн. Сопротивления",null,null,724.4272725212057,0.4,null,"%","∆Р","dш."]
[{"$nulls":13},"Сумма",2535.49545382422,"Па",null,82.2201015670295,0.6274965388418139,5.006421743060764,0.545,5.185983612234819]
[]
["Расчет системы "]
["№ уч",null,null,"Q вт","G кг/ч","G л/сек","L  м","D мм","l/d ","G / V","A * 10 -4","V м/с","S z","S *10 -4","D P Па","S D P Па","S D P м.в.ст."]
[75,"-","ст.4",4832.9,200.84179603534747,0.05578938778759652,6,20,1.79,1250,3.15,0.16067343682827798,32.3,0.0135576,546.8787007657045,546.8787007657045,0.05468787007657045]
[{"$nulls":13},"Сумма",1654.2948566141145,"Па"]
[{"$nulls":11},"Местн. Сопротивления",null,null,661.7179426456458,0.4,null,"%","∆Р","dш."]
[{"$nulls":13},"Сумма",2316.0127992597604,"Па",null,83.75920087800203,1.1944448042982598,4.844109707093081]
[]
["Расчет системы "]
["№ уч",null,null,"Q вт","G кг/ч","G л/сек","L  м","D мм","l/d ","G / V","A * 10 -4","V м/с","S z","S *10 -4","D P Па","S D P Па","S D P м.в.ст."]
[76,"-","ст.3",1559,64.78767614043467,0.017996576705676295,6,20,1.79,1250,3.15,0.051830140912347736,32.3,0.0135576,56.90725294128038,56.90725294128038,0.0056907252941280385]
[{"$nulls":13},"Сумма",840.1313513574119,"Па"]
[{"$nulls":11},"Местн. Сопротивления",null,null,336.0525405429648,0.4,null,"%","∆Р","dш."]
[{"$nulls":13},"Сумма",1176.1838919003767,"Па",null,91.75213266308839,1.3084276950341982,2.6892873731278497]
[]
["Расчет системы "]
["№ уч",null,null,"Q вт","G кг/ч","G л/сек","L  м","D мм","l/d ","G / V","A * 10 -4","V м/с","S z","S *10 -4","D P Па","S D P Па","S D P м.в.ст."]
[77,"-","ст.2",900,37.401480773823735,0.010389300214951037,21.8,15,2.69,685,10.5,0.054600701859596694,12.7,0.0749091,104.78814995314862,104.78814995314862,0.010478814995314861]
[{"$nulls":13},"Сумма",844.2674675491157,"Па"]
[{"$nulls":11},"Местн. Сопротивления",null,null,337.7069870196463,0.4,null,"%","∆Р","dш."]
[{"$nulls":13},"Сумма",1181.974454568762,"Па",null,91.71152694401351,0.027848638767359626,5.349606636203295,1.28,2.0545671948831785]
[]
["Расчет системы "]
["№ уч",null,null,"Q вт","G кг/ч","G л/сек","L  м","D мм","l/d ","G / V","A * 10 -4","V м/с","S z","S *10 -4","D P Па","S D P Па","S D P м.в.ст."]
[78,"-","ст.1",1870.8,77.7452113685216,0.021595892046811553,6,20,1.79,1250,3.15,0.062196169094817275,32,0.0134631,81.3752561947692,81.3752561947692,0.008137525619476919]
[{"$nulls":13},"Сумма",316.19931605165834,"Па"]
[{"$nulls":11},"Местн. Сопротивления",null,null,126.47972642066334,0.4,null,"%","∆Р","dш."]
[{"$nulls":13},"Сумма",442.67904247232167,"Па",null,96.89575920883975,1.3817781799770037,2.9060674174223964]
[]
["Расчет системы "]
["№ уч",null,null,"Q вт","G кг/ч","G л/сек","L  м","D мм","l/d ","G / V","A * 10 -4","V м/с","S z","S *10 -4","D P Па","S D P Па","S D P м.в.ст."]
[79,"-","ст.35",900,37.401480773823735,0.010389300214951037,6,20,1.79,1250,3.15,0.029921184619058988,13,0.0074781000000000005,10.460895460827064,10.460895460827064,0.0010460895460827064]
[{"$nulls":13},"Сумма",8936.546248622995,"Па"]
[{"$nulls":11},"Местн. Сопротивления",null,null,3574.618499449198,0.4,null,"%","∆Р","dш."]
[{"$nulls":13},"Сумма",12511.164748072193,"Па",null,2.034126339778285,0.02597770918026599,5.443429834415696]
[]
["Расчет системы "]
["№ уч",null,null,"Q вт","G кг/ч","G л/сек","L  м","D мм","l/d ","G / V","A * 10 -4","V м/с","S z","S *10 -4","D P Па","S D P Па","S D P м.в.ст."]
[80,"-","ст.34",2806.2,116.61781705278239,0.032393838070217326,6,20,1.79,1250,3.15,0.0932942536422259,32,0.0134631,183.09432643823064,183.09432643823064,0.018309432643823065]
[{"$nulls":13},"Сумма",9080.057897882642,"Па"]
[{"$nulls":11},"Местн. Сопротивления",null,null,3632.023159153057,0.4,null,"%","∆Р","dш."]
[{"$nulls":13},"Сумма",12712.081057035699,"Па",null,0.4608961780357691,0.005886078283915412,13.931708818823855]
[]
["Расчет системы "]
["№ уч",null,null,"Q вт","G кг/ч","G л/сек","L  м","D мм","l/d ","G / V","A * 10 -4","V м/с","S z","S *10 -4","D P Па","S D P Па","S D P м.в.ст."]
[81,"-","ст.33",3273.9,136.0541198949128,0.037792811081920216,6,20,1.79,1250,3.15,0.10884329591593023,32,0.0134631,249.2117220964806,249.2117220964806,0.02492117220964806]
[{"$nulls":13},"Сумма",8982.555407716423,"Па"]
[{"$nulls":11},"Местн. Сопротивления",null,null,3593.0221630865694,0.4,null,"%","∆Р","dш."]
[{"$nulls":13},"Сумма",12575.577570802992,"Па",null,1.5297561567610674,0.01953642690718607,11.14866864898285]
[]
["Расчет системы "]
["№ уч",null,null,"Q вт","G кг/ч","G л/сек","L  м","D мм","l/d ","G / V","A * 10 -4","V м/с","S z","S *10 -4","D P Па","S D P Па","S D P м.в.ст."]
["81а","-","ст.32",1091.3,45.35137329830427,0.012597603693973407,6,20,1.79,1250,3.15,0.036281098638643414,32,0.0134631,27.690191344053407,27.690191344053407,0.0027690191344053408]
[{"$nulls":13},"Сумма",8761.033876963997,"Па"]
[{"$nulls":11},"Местн. Сопротивления",null,null,3504.413550785599,0.4]
[{"$nulls":13},"Сумма",12265.447427749596,"Па"]
[]
["Расчет системы "]
["№ уч",null,null,"Q вт","G кг/ч","G л/сек","L  м","D мм","l/d ","G / V","A * 10 -4","V м/с","S z","S *10 -4","D P Па","S D P Па","S D P м.в.ст."]
[82,"-","ст.31",4521.1,187.88426080726055,0.05219007244646126,6,20,1.79,1250,3.15,0.15030740864580844,32,0.0134631,475.25410041528403,475.25410041528403,0.0475254100415284]
[{"$nulls":13},"Сумма",8589.509146816376,"Па"]
[{"$nulls":11},"Местн. Сопротивления",null,null,3435.8036587265506,0.4,null,"%","∆Р","dш."]
[{"$nulls":13},"Сумма",12025.312805542926,"Па",null,5.838481168270935,0.07456290343319269,9.37330914728182]
[]
["Расчет системы "]
["№ уч",null,null,"Q вт","G кг/ч","G л/сек","L  м","D мм","l/d ","G / V","A * 10 -4","V м/с","S z","S *10 -4","D P Па","S D P Па","S D P м.в.ст."]
[83,"-","ст.30",3273.9,136.0541198949128,0.037792811081920216,6,20,1.79,1250,3.15,0.10884329591593023,32,0.0134631,249.2117220964806,249.2117220964806,0.02492117220964806]
[{"$nulls":13},"Сумма",8096.223270199238,"Па"]
[{"$nulls":11},"Местн. Сопротивления",null,null,3238.4893080796955,0.4,null,"%","∆Р","dш."]
[{"$nulls":13},"Сумма",11334.712578278934,"Па",null,11.246071586604248,0.14362292615959196,6.770618591932204]
[]
["Расчет системы "]
["№ уч",null,null,"Q вт","G кг/ч","G л/сек","L  м","D мм","l/d ","G / V","A * 10 -4","V м/с","S z","S *10 -4","D P Па","S D P Па","S D P м.в.ст."]
[84,"-","ст.29",2806.2,116.61781705278239,0.032393838070217326,6,20,1.79,1250,3.15,0.0932942536422259,32,0.0134631,183.09432643823064,183.09432643823064,0.018309432643823065]
[{"$nulls":13},"Сумма",7491.184005107604,"Па"]
[{"$nulls":11},"Местн. Сопротивления",null,null,2996.473602043042,0.4,null,"%","∆Р","dш."]
[{"$nulls":13},"Сумма",10487.657607150646,"Па",null,17.878745838424255,0.2283284232724207,5.582399367728503]
[]
["Расчет системы "]
["№ уч",null,null,"Q вт","G кг/ч","G л/сек","L  м","D мм","l/d ","G / V","A * 10 -4","V м/с","S z","S *10 -4","D P Па","S D P Па","S D P м.в.ст."]
["84а","-","ст.28",3585.7,149.01165512299974,0.04139212642305548,6,20,1.79,1250,3.15,0.1192093240983998,32,0.0134631,298.94104532661737,298.94104532661737,0.029894104532661735]
[{"$nulls":13},"Сумма",7607.030723995991,"Па"]
[{"$nulls":11},"Местн. Сопротивления",null,null,3042.8122895983965,0.4,null,"%","∆Р","dш."]
[{"$nulls":13},"Сумма",10649.843013594387,"Па",null,16.60878933500218,0.2121098826280466,6.427592522855897]
[]
["Расчет системы "]
["№ уч",null,null,"Q вт","G кг/ч","G л/сек","L  м","D мм","l/d ","G / V","A * 10 -4","V м/с","S z","S *10 -4","D P Па","S D P Па","S D P м.в.ст."]
[85,"-","ст.27",2806.2,116.61781705278239,0.032393838070217326,6,20,1.79,1250,3.15,0.0932942536422259,32,0.0134631,183.09432643823064,183.09432643823064,0.018309432643823065]
[{"$nulls":13},"Сумма",5647.543855589186,"Па"]
[{"$nulls":11},"Местн. Сопротивления",null,null,2259.0175422356747,0.4,null,"%","∆Р","dш."]
[{"$nulls":13},"Сумма",7906.56139782486,"Па",null,38.08944166405867,0.48643804420499925,4.620660007615752]
[]
["Расчет системы "]
["№ уч",null,null,"Q вт","G кг/ч","G л/сек","L  м","D мм","l/d ","G / V","A * 10 -4","V м/с","S z","S *10 -4","D P Па","S D P Па","S D P м.в.ст."]
[86,"-","ст.26",900,37.401480773823735,0.010389300214951037,21.8,15,2.69,685,10.5,0.054600701859596694,13,0.0752241,105.22879424383214,105.22879424383214,0.010522879424383215]
[{"$nulls":13},"Сумма",5569.678323394788,"Па"]
[{"$nulls":11},"Местн. Сопротивления",null,null,2227.8713293579153,0.4,null,"%","∆Р","dш."]
[{"$nulls":13},"Сумма",7797.549652752703,"Па",null,38.94303372045492,0.497339218712215,2.6023138010427163]
[]
["Расчет системы "]
["№ уч",null,null,"Q вт","G кг/ч","G л/сек","L  м","D мм","l/d ","G / V","A * 10 -4","V м/с","S z","S *10 -4","D P Па","S D P Па","S D P м.в.ст."]
[87,"-","ст.25",1870.8,77.7452113685216,0.021595892046811553,8,20,1.79,1250,3.15,0.062196169094817275,32,0.0145908,88.19143348015228,88.19143348015228,0.00881914334801523]
[{"$nulls":13},"Сумма",4497.555471155859,"Па"]
[{"$nulls":11},"Местн. Сопротивления",null,null,1799.0221884623436,0.4,null,"%","∆Р","dш."]
[{"$nulls":13},"Сумма",6296.577659618202,"Па",null,50.69605876711201,0.6474364180256651,3.512497199390941]
[]
["Расчет системы "]
["№ уч",null,null,"Q вт","G кг/ч","G л/сек","L  м","D мм","l/d ","G / V","A * 10 -4","V м/с","S z","S *10 -4","D P Па","S D P Па","S D P м.в.ст."]
[88,"-","ст.24",900,37.401480773823735,0.010389300214951037,21.8,15,2.69,685,10.5,0.054600701859596694,13,0.0752241,105.22879424383214,105.22879424383214,0.010522879424383215]
[{"$nulls":13},"Сумма",4214.3847309238035,"Па"]
[{"$nulls":11},"Местн. Сопротивления",null,null,1685.7538923695215,0.4,null,"%","∆Р","dш."]
[{"$nulls":13},"Сумма",5900.1386232933255,"Па",null,53.800285857764564,0.6870803216581528,2.400330062050183]
[]
["Расчет системы "]
["№ уч",null,null,"Q вт","G кг/ч","G л/сек","L  м","D мм","l/d ","G / V","A * 10 -4","V м/с","S z","S *10 -4","D P Па","S D P Па","S D P м.в.ст."]
[89,"-","ст.23",2026.7,84.22397898256506,0.023395549717379182,6,20,1.79,1250,3.15,0.06737918318605204,32,0.0134631,95.50290483969438,95.50290483969438,0.009550290483969439]
[{"$nulls":13},"Сумма",3977.1041860423857,"Па"]
[{"$nulls":11},"Местн. Сопротивления",null,null,1590.8416744169544,0.4,null,"%","∆Р","dш."]
[{"$nulls":13},"Сумма",5567.94586045934,"Па",null,56.40144689192397,0.7202995979415513,3.5597379439510064]
[]
["Расчет системы "]
["№ уч",null,null,"Q вт","G кг/ч","G л/сек","L  м","D мм","l/d ","G / V","A * 10 -4","V м/с","S z","S *10 -4","D P Па","S D P Па","S D P м.в.ст."]
[90,"-","ст.22",2962.1,123.09658466682586,0.03419349574078496,6,20,1.79,1250,3.15,0.09847726773346069,32,0.0134631,204.00324643271998,204.00324643271998,0.020400324643272]
[{"$nulls":13},"Сумма",1758.866460857696,"Па"]
[{"$nulls":11},"Местн. Сопротивления",null,null,703.5465843430784,0.4,null,"%","∆Р","dш."]
[{"$nulls":13},"Сумма",2462.4130452007744,"Па",null,80.7186261117222,1.030852879467408,3.934615270600862]
[]
["Расчет системы "]
["№ уч",null,null,"Q вт","G кг/ч","G л/сек","L  м","D мм","l/d ","G / V","A * 10 -4","V м/с","S z","S *10 -4","D P Па","S D P Па","S D P м.в.ст."]
[91,"-","ст.21",2806.2,116.61781705278239,0.032393838070217326,6,20,1.79,1250,3.15,0.0932942536422259,32,0.0134631,183.09432643823064,183.09432643823064,0.018309432643823065]
[{"$nulls":13},"Сумма",1511.305469846538,"Па"]
[{"$nulls":11},"Местн. Сопротивления",null,null,604.5221879386153,0.4,null,"%","∆Р","dш."]
[{"$nulls":13},"Сумма",2115.8276577851534,"Па",null,83.43248536941198,1.06551141820897,3.798143510965561]
[]
["Расчет системы "]
["№ уч",null,null,"Q вт","G кг/ч","G л/сек","L  м","D мм","l/d ","G / V","A * 10 -4","V м/с","S z","S *10 -4","D P Па","S D P Па","S D P м.в.ст."]
[92,"-","ст.20",2494.4,103.66028182469547,0.028794522729082075,6,20,1.79,1250,3.15,0.08292822545975638,32,0.0134631,144.66712212403414,144.66712212403414,0.014466712212403414]
[{"$nulls":13},"Сумма",1397.5554423865226,"Па"]
[{"$nulls":11},"Местн. Сопротивления",null,null,559.0221769546091,0.4,null,"%","∆Р","dш."]
[{"$nulls":13},"Сумма",1956.5776193411316,"Па",null,84.6794571310936,1.081436422053372,3.5676676305682378]
[]
["Расчет системы "]
["№ уч",null,null,"Q вт","G кг/ч","G л/сек","L  м","D мм","l/d ","G / V","A * 10 -4","V м/с","S z","S *10 -4","D P Па","S D P Па","S D P м.в.ст."]
[93,"-","ст.19",2026.7,84.22397898256506,0.023395549717379182,6,20,1.79,1250,3.15,0.06737918318605204,32,0.0134631,95.50290483969438,95.50290483969438,0.009550290483969439]
[{"$nulls":13},"Сумма",904.394867385584,"Па"]
[{"$nulls":11},"Местн. Сопротивления",null,null,361.7579469542336,0.4,null,"%","∆Р","dш."]
[{"$nulls":13},"Сумма",1266.1528143398177,"Па",null,90.08567394468517,1.1504789025535036,3.1664793210496294]
[]
["Расчет системы "]
["№ уч",null,null,"Q вт","G кг/ч","G л/сек","L  м","D мм","l/d ","G / V","A * 10 -4","V м/с","S z","S *10 -4","D P Па","S D P Па","S D P м.в.ст."]
[94,"-","ст.18",1870.8,77.7452113685216,0.021595892046811553,6,20,1.79,1250,3.15,0.062196169094817275,32,0.0134631,81.3752561947692,81.3752561947692,0.008137525619476919]
[{"$nulls":13},"Сумма",627.0033677015809,"Па"]
[{"$nulls":11},"Местн. Сопротивления",null,null,250.80134708063238,0.4,null,"%","∆Р","dш."]
[{"$nulls":13},"Сумма",877.8047147822133,"Па",null,93.12654676696253,1.189313712509264,3.0171101177664696]

{"sheet":"Лист2","index":1,"n_rows":28,"n_cols":5,"rows_kept":28,"cut":false,"hidden":false,"merged":[[0,0,0,1],[0,3,0,4]],"flags":["formulas_cached_only"]}
[null,null,null,"Ведомость дроссельных шайб"]
[null,null,null,"№ стояка","d шайбы"]
[null,null,null,13,6.1]
[null,null,null,12,7.4]
[null,null,null,11,4.1]
[null,null,null,10,4.6]
[null,null,null,9,2.8]
[null,null,null,8,3.8]
[null,null,null,7,5.3]
[null,null,null,6,3.7]
[null,null,null,5,4.3]
[null,null,null,4,4.8]
[null,null,null,3,2.7]
[null,null,null,2,2]
[null,null,null,1,2.9]
[null,null,null,30,6.8]
[null,null,null,29,5.6]
[null,null,null,28,6.4]
[null,null,null,27,4.6]
[null,null,null,26,2.6]
[null,null,null,25,3.5]
[null,null,null,24,2.4]
[null,null,null,23,3.6]
[null,null,null,22,3.9]
[null,null,null,21,3.8]
[null,null,null,20,3.6]
[null,null,null,19,3.2]
[null,null,null,18,3]

{"sheet":"Лист3","index":2,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}