{"text_format":"2","workbook":"xls","n_sheets":3,"sheets":["Лист1","Лист2","Лист3"],"not_rendered":{"charts":0,"images":1,"macros":1,"external_links":1,"defined_names":1,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Лист1","index":0,"n_rows":821,"n_cols":25,"rows_kept":821,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["Tпод",95]
["Tобр",70]
["Гидравлический расчет системы отпления 2 (трубы Обыкновенные температура 95-70 С)"]
["N участка","Q, Вт","G, кг/ч","l, м","d, мм","dвн, мм","F, м2","v, м/с","R, Па/м","Rl, Па","Сум s.","Рд, Па","Z, Па","Р, Па","Сум Р, Па","Характеристика местный сопротивлений ",null,"Кинематическая вязкость, м2/сек","Re","kэ","d/kэ","Reпр1","Reпр2","Плотность воды, кг/м3","l "]
["0",90174,3574.5344030570814,10,50,44.4,0.0015482568600000003,0.6611533964182913,142.27064195237864,1422.7064195237863,0,212.00504959378947,0,1422.7064195237863,1422.7064195237863,null,null,4.79e-07,61284.36492896062,0.2,221.99999999999997,1678.7139693011175,33299.99999999999,983.25,0.029394077523160436]
["1",44325,1757.0612085025075,2,32,35.9,0.00101219915375,0.49710334534234707,106.07759933357384,212.1551986671477,0,119.8491919360181,0,212.1551986671477,1634.861618190934,null,null,4.79e-07,37256.80604966651,0.2,179.49999999999997,74972.39960709562,26924.999999999996,983.25,0.03134662584008899]
["2",42455,1682.9336403152613,1.2,32,35.9,0.00101219915375,0.47613135987612737,97.31591814725704,116.77910177670844,0,109.9500198508828,0,116.77910177670844,1751.6407199676423,null,null,4.79e-07,35685.00171096654,0.2,179.49999999999997,74972.39960709562,26924.999999999996,983.25,0.03134662584008899]
["3",41555,1647.2572705994744,0.5,32,35.9,0.00101219915375,0.466037890935166,93.23366729707577,46.616833648537884,0,105.33778815683938,0,46.616833648537884,1798.2575536161803,null,null,4.79e-07,34928.51833939971,0.2,179.49999999999997,74972.39960709562,26924.999999999996,983.25,0.03134662584008899]
["4",39996,1585.4578701695723,4,32,35.9,0.00101219915375,0.44855375973632294,86.36928282789081,345.47713131156326,0,97.5822305561916,0,345.47713131156326,2143.7346849277437,null,null,4.79e-07,33618.121032430055,0.2,179.49999999999997,74972.39960709562,26924.999999999996,983.25,0.03134662584008899]
["5",35163,1393.8757647957964,6,32,35.9,0.00101219915375,0.39435183152336045,66.75718809924044,400.5431285954426,0,75.423983007527,0,400.5431285954426,2544.2778135231865,null,null,4.79e-07,29555.80532711616,0.2,179.49999999999997,74972.39960709562,26924.999999999996,983.25,0.03134662584008899]
["6",31421,1245.5413475997134,4.5,25,27.1,0.0005767872537500001,0.6183982610378925,237.56913785982815,1069.0611203692267,0,185.4719584885244,0,1069.0611203692267,3613.3389338924135,null,null,4.79e-07,34986.62395433588,0.2,135.5,54639.98971373989,20325,983.25,0.03424434263477065]
["7",28927,1146.678163076188,5,25,27.1,0.0005767872537500001,0.5693137232119637,201.35239855240965,1006.7619927620483,0,157.1972859871722,0,1006.7619927620483,4620.100926654462,null,null,4.79e-07,32209.607304893987,0.2,135.5,54639.98971373989,20325,983.25,0.03424434263477065]
["8",24873,985.9759377119655,4,25,27.1,0.0005767872537500001,0.4895267479327678,148.86971465209524,595.478858608381,0,116.22367191669132,0,595.478858608381,5215.579785262842,null,null,4.79e-07,27695.56340078916,0.2,135.5,54639.98971373989,20325,983.25,0.03424434263477065]
["9",23002,911.8087291139241,2,25,27.1,0.0005767872537500001,0.45270350403849663,127.3154807868676,254.6309615737352,0,99.39612434583557,0,254.6309615737352,5470.2107468365775,null,null,4.79e-07,25612.24417420305,0.2,135.5,54639.98971373989,20325,983.25,0.03424434263477065]
["10","22102",876.132359398137,3.7,25,27.1,0.0005767872537500001,0.43499055935391934,120.09713780555425,444.35940988055074,0,91.77014156261228,0,444.35940988055074,5914.570156717128,null,null,4.79e-07,24610.113065743662,0.2,135.5,54639.98971373989,20325,984.25,0.03424434263477065]
["11","17425",690.7341581084307,4.8,25,27.1,0.0005767872537500001,0.34294229014306593,74.64746806544645,358.30784671414295,0,57.04056596875685,0,358.30784671414295,6272.878003431271,null,null,4.79e-07,19402.371738783066,0.2,135.5,54639.98971373989,20325,985.25,0.03466301926608277]
["12","13684",542.439381323143,1,25,27.1,0.0005767872537500001,0.269315483404173,46.03579411976502,46.03579411976502,0,35.17745235659334,0,46.03579411976502,6318.913797551037,null,null,4.79e-07,15236.846764620228,0.2,135.5,54639.98971373989,20325,986.25,0.03611682302925961]
["13","11034",437.3922927155481,3,20,21.2,0.00035297894000000003,0.35485268563793404,108.6328002517152,325.8984007551456,0,61.07140782466041,0,325.8984007551456,6644.812198306182,null,null,4.79e-07,15705.37982364134,0.2,105.99999999999999,41452.23964306845,15899.999999999998,987.25,0.03705123183084877]
["14","8383",332.3055636971578,2.8,20,21.2,0.00035297894000000003,0.2695967068789923,62.70381252489672,175.5706750697108,0,35.25095641459868,0,175.5706750697108,6820.382873375893,null,null,4.79e-07,11932.04631698254,0.2,105.99999999999999,41452.23964306845,15899.999999999998,988.25,0.038823022953756656]
["15","3706",146.90736240745164,3.8,20,21.2,0.00035297894000000003,0.11918470663170054,12.254789204107226,46.56819897560746,0,6.889422233018994,0,46.56819897560746,6866.9510723515,null,null,4.79e-07,5274.980752801778,0.2,105.99999999999999,41452.23964306845,15899.999999999998,989.25,0.04460189771450519]
["17 (16пс)","900",35.676369715786954,21.8,15,15.7,0.00019358708375,0.05277521889650863,3.4975999088255216,76.24767801239638,13,1.3508335088435848,17.560835614966603,93.80851362736298,6960.7595859788635,null,null,4.79e-07,1729.7931872133306,0.2,78.49999999999999,29567.00029547899,11774.999999999998,990.25,0.05597271870518401]
["17","3706",146.90736240745164,3.8,20,21.2,0.00035297894000000003,0.11918470663170054,12.254789204107226,46.56819897560746,0,6.889422233018994,0,46.56819897560746,7007.327784954471,null,null,4.79e-07,5274.980752801778,0.2,105.99999999999999,41452.23964306845,15899.999999999998,991.25,0.04460189771450519]
["18","8383",332.3055636971578,2.8,20,21.2,0.00035297894000000003,0.2695967068789923,62.70381252489672,175.5706750697108,0,35.25095641459868,0,175.5706750697108,7182.898460024182,null,null,4.79e-07,11932.04631698254,0.2,105.99999999999999,41452.23964306845,15899.999999999998,992.25,0.038823022953756656]
["19","11034",437.3922927155481,3,20,21.2,0.00035297894000000003,0.35485268563793404,108.6328002517152,325.8984007551456,0,61.07140782466041,0,325.8984007551456,7508.796860779327,null,null,4.79e-07,15705.37982364134,0.2,105.99999999999999,41452.23964306845,15899.999999999998,993.25,0.03705123183084877]
["20","13684",542.439381323143,1,25,27.1,0.0005767872537500001,0.269315483404173,46.03579411976502,46.03579411976502,0,35.17745235659334,0,46.03579411976502,7554.832654899093,null,null,4.79e-07,15236.846764620228,0.2,135.5,54639.98971373989,20325,994.25,0.03611682302925961]
["21","17425",690.7341581084307,4.8,25,27.1,0.0005767872537500001,0.34294229014306593,74.64746806544645,358.30784671414295,0,57.04056596875685,0,358.30784671414295,7913.140501613236,null,null,4.79e-07,19402.371738783066,0.2,135.5,54639.98971373989,20325,995.25,0.03466301926608277]
["22","22102",876.132359398137,3.7,25,27.1,0.0005767872537500001,0.43499055935391934,120.09713780555425,444.35940988055074,0,91.77014156261228,0,444.35940988055074,8357.499911493787,null,null,4.79e-07,24610.113065743662,0.2,135.5,54639.98971373989,20325,996.25,0.03424434263477065]
["23","23002",911.8087291139241,2,25,27.1,0.0005767872537500001,0.45270350403849663,135.98965172991188,271.97930345982377,0,99.39612434583557,0,271.97930345982377,8629.479214953612,null,null,4.79e-07,25612.24417420305,0.2,135.5,54639.98971373989,20325,999.25,0.03424434263477065]
["24","24873",985.9759377119655,4,25,27.1,0.0005767872537500001,0.4895267479327678,159.0124038612436,636.0496154449744,0,116.22367191669132,0,636.0496154449744,9265.528830398585,null,null,4.79e-07,27695.56340078916,0.2,135.5,54639.98971373989,20325,1000.25,0.03424434263477065]
["25","28927",1146.678163076188,5,25,27.1,0.0005767872537500001,0.5693137232119637,215.0708019550518,1075.3540097752589,0,157.1972859871722,0,1075.3540097752589,10340.882840173845,null,null,4.79e-07,32209.607304893987,0.2,135.5,54639.98971373989,20325,1001.25,0.03424434263477065]
["26","31421",1245.5413475997134,4.5,25,27.1,0.0005767872537500001,0.6183982610378925,253.75503528449048,1141.8976587802072,0,185.4719584885244,0,1141.8976587802072,11482.780498954053,null,null,4.79e-07,34986.62395433588,0.2,135.5,54639.98971373989,20325,1002.25,0.03424434263477065]
["27","35163",1393.8757647957964,6,32,35.9,0.00101219915375,0.39435183152336045,72.608827994033,435.65296796419807,0,75.423983007527,0,435.65296796419807,11918.43346691825,null,null,4.79e-07,29555.80532711616,0.2,179.49999999999997,74972.39960709562,26924.999999999996,1003.25,0.03134662584008899]
["28","39996",1585.4578701695723,4,32,35.9,0.00101219915375,0.44855375973632294,93.94003221788887,375.7601288715555,0,97.5822305561916,0,375.7601288715555,12294.193595789806,null,null,4.79e-07,33618.121032430055,0.2,179.49999999999997,74972.39960709562,26924.999999999996,1004.25,0.03134662584008899]
["29","41555",1647.2572705994744,0.5,32,35.9,0.00101219915375,0.466037890935166,101.40611827392561,50.70305913696281,0,105.33778815683938,0,50.70305913696281,12344.896654926768,null,null,4.79e-07,34928.51833939971,0.2,179.49999999999997,74972.39960709562,26924.999999999996,1005.25,0.03134662584008899]
["30","42455",1682.9336403152613,1.2,32,35.9,0.00101219915375,0.47613135987612737,105.84620118108266,127.01544141729919,0,109.9500198508828,0,127.01544141729919,12471.912096344067,null,null,4.79e-07,35685.00171096654,0.2,179.49999999999997,74972.39960709562,26924.999999999996,1006.25,0.03134662584008899]
["31","88303",3500.3671944590396,2,32,35.9,0.00101219915375,0.9903150976596792,457.8977425156913,915.7954850313826,0,475.65113643655945,0,915.7954850313826,13387.707581375449,null,null,4.79e-07,74221.94573274005,0.2,179.49999999999997,74972.39960709562,26924.999999999996,1006.25,0.03134662584008899]
["32","88615",3512.7350026271797,5,50,44.4,0.0015482568600000003,0.6497228494200866,151.1183945019763,755.5919725098815,0,204.73779381339992,0,755.5919725098815,14143.29955388533,null,null,4.79e-07,60224.83197129822,0.2,221.99999999999997,95219.52223366837,33299.99999999999,1006.25,0.029394077523160436]
[null,null,null,111.59999999999998,{"$nulls":4},81.54121863799284,{"$nulls":8},4.79e-07,0,0.2,0,0,0,1009.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1010.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1011.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1012.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1013.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1014.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1015.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1016.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1017.25,{"$error":"#NUM!"}]
[{"$nulls":13},"Невязка %",{"$error":"#REF!"},null,null,4.79e-07,{"$error":"#VALUE!"},0.2,0,0,0,1018.25,{"$error":"#VALUE!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1019.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1020.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1021.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1022.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1023.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1024.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1025.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1026.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1027.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1028.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1029.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1030.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1031.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1032.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1033.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1034.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1035.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1036.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1037.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1038.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1039.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1040.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1041.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1042.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1043.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1044.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1045.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1046.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1047.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1048.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1049.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1050.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1051.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1052.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1053.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1054.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1055.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1056.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1057.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1058.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1059.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1060.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1061.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1062.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1063.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1064.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1065.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1066.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1067.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1068.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1069.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1070.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1071.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1072.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1073.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1074.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1075.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1076.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1077.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1078.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1079.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1080.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1081.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1082.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1083.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1084.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1085.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1086.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1087.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1088.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1089.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1090.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1091.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1092.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1093.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1094.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1095.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1096.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1097.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1098.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1099.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1100.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1101.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1102.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1103.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1104.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1105.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1106.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1107.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1108.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1109.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1110.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1111.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1112.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1113.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1114.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1115.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1116.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1117.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1118.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1119.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1120.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1121.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1122.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1123.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1124.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1125.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1126.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1127.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1128.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1129.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1130.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1131.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1132.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1133.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1134.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1135.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1136.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1137.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1138.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1139.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1140.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1141.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1142.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1143.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1144.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1145.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1146.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1147.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1148.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1149.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1150.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1151.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1152.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1153.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1154.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1155.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1156.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1157.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1158.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1159.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1160.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1161.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1162.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1163.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1164.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1165.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1166.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1167.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1168.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1169.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1170.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1171.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1172.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1173.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1174.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1175.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1176.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1177.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1178.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1179.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1180.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1181.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1182.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1183.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1184.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1185.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1186.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1187.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1188.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1189.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1190.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1191.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1192.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1193.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1194.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1195.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1196.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1197.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1198.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1199.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1200.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1201.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1202.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1203.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1204.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1205.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1206.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1207.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1208.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1209.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1210.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1211.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1212.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1213.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1214.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1215.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1216.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1217.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1218.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1219.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1220.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1221.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1222.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1223.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1224.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1225.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1226.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1227.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1228.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1229.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1230.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1231.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1232.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1233.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1234.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1235.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1236.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1237.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1238.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1239.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1240.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1241.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1242.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1243.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1244.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1245.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1246.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1247.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1248.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1249.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1250.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1251.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1252.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1253.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1254.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1255.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1256.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1257.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1258.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1259.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1260.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1261.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1262.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1263.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1264.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1265.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1266.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1267.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1268.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1269.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1270.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1271.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1272.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1273.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1274.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1275.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1276.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1277.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1278.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1279.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1280.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1281.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1282.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1283.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1284.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1285.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1286.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1287.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1288.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1289.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1290.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1291.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1292.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1293.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1294.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1295.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1296.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1297.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1298.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1299.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1300.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1301.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1302.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1303.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1304.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1305.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1306.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1307.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1308.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1309.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1310.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1311.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1312.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1313.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1314.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1315.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1316.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1317.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1318.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1319.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1320.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1321.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1322.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1323.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1324.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1325.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1326.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1327.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1328.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1329.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1330.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1331.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1332.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1333.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1334.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1335.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1336.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1337.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1338.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1339.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1340.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1341.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1342.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1343.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1344.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1345.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1346.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1347.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1348.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1349.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1350.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1351.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1352.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1353.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1354.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1355.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1356.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1357.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1358.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1359.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1360.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1361.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1362.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1363.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1364.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1365.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1366.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1367.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1368.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1369.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1370.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1371.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1372.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1373.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1374.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1375.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1376.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1377.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1378.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1379.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1380.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1381.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1382.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1383.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1384.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1385.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1386.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1387.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1388.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1389.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1390.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1391.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1392.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1393.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1394.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1395.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1396.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1397.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1398.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1399.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1400.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1401.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1402.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1403.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1404.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1405.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1406.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1407.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1408.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1409.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1410.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1411.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1412.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1413.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1414.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1415.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1416.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1417.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1418.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1419.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1420.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1421.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1422.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1423.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1424.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1425.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1426.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1427.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1428.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1429.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1430.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1431.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1432.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1433.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1434.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1435.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1436.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1437.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1438.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1439.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1440.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1441.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1442.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1443.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1444.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1445.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1446.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1447.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1448.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1449.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1450.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1451.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1452.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1453.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1454.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1455.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1456.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1457.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1458.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1459.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1460.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1461.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1462.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1463.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1464.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1465.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1466.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1467.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1468.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1469.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1470.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1471.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1472.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1473.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1474.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1475.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1476.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1477.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1478.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1479.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1480.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1481.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1482.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1483.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1484.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1485.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1486.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1487.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1488.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1489.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1490.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1491.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1492.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1493.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1494.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1495.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1496.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1497.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1498.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1499.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1500.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1501.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1502.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1503.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1504.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1505.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1506.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1507.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1508.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1509.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1510.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1511.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1512.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1513.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1514.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1515.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1516.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1517.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1518.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1519.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1520.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1521.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1522.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1523.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1524.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1525.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1526.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1527.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1528.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1529.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1530.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1531.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1532.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1533.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1534.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1535.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1536.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1537.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1538.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1539.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1540.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1541.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1542.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1543.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1544.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1545.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1546.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1547.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1548.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1549.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1550.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1551.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1552.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1553.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1554.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1555.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1556.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1557.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1558.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1559.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1560.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1561.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1562.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1563.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1564.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1565.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1566.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1567.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1568.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1569.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1570.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1571.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1572.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1573.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1574.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1575.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1576.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1577.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1578.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1579.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1580.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1581.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1582.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1583.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1584.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1585.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1586.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1587.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1588.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1589.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1590.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1591.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1592.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1593.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1594.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1595.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1596.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1597.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1598.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1599.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1600.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1601.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1602.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1603.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1604.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1605.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1606.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1607.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1608.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1609.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1610.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1611.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1612.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1613.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1614.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1615.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1616.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1617.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1618.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1619.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1620.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1621.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1622.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1623.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1624.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1625.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1626.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1627.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1628.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1629.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1630.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1631.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1632.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1633.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1634.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1635.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1636.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1637.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1638.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1639.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1640.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1641.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1642.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1643.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1644.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1645.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1646.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1647.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1648.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1649.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1650.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1651.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1652.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1653.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1654.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1655.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1656.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1657.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1658.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1659.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1660.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1661.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1662.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1663.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1664.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1665.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1666.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1667.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1668.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1669.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1670.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1671.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1672.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1673.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1674.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1675.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1676.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1677.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1678.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1679.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1680.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1681.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1682.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1683.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1684.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1685.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1686.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1687.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1688.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1689.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1690.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1691.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1692.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1693.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1694.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1695.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1696.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1697.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1698.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1699.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1700.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1701.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1702.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1703.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1704.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1705.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1706.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1707.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1708.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1709.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1710.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1711.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1712.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1713.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1714.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1715.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1716.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1717.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1718.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1719.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1720.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1721.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1722.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1723.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1724.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1725.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1726.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1727.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1728.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1729.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1730.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1731.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1732.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1733.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1734.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1735.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1736.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1737.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1738.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1739.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1740.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1741.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1742.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1743.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1744.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1745.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1746.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1747.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1748.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1749.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1750.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1751.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1752.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1753.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1754.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1755.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1756.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1757.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1758.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1759.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1760.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1761.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1762.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1763.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1764.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1765.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1766.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1767.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1768.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1769.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1770.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1771.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1772.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1773.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1774.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1775.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1776.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1777.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1778.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1779.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1780.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1781.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1782.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1783.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1784.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1785.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1786.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1787.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1788.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1789.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1790.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1791.25,{"$error":"#NUM!"}]
[{"$nulls":17},4.79e-07,0,0.2,0,0,0,1792.25,{"$error":"#NUM!"}]

{"sheet":"Лист2","index":1,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}

{"sheet":"Лист3","index":2,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}