{"text_format":"2","workbook":"xls","n_sheets":3,"sheets":["Лист1","Лист2","Лист3"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":0,"defined_names":0,"comments":165,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Лист1","index":0,"n_rows":326,"n_cols":22,"rows_kept":326,"cut":false,"hidden":false,"merged":[[181,0,181,2],[184,11,184,13],[187,0,187,16],[198,11,198,13],[188,0,188,2],[191,11,191,13],[194,0,194,16],[195,0,195,2],[173,0,173,16],[174,0,174,2],[177,11,177,13],[180,0,180,16],[163,11,163,13],[166,0,166,16],[167,0,167,2],[170,11,170,13],[153,0,153,2],[156,11,156,13],[159,0,159,16],[160,0,160,2],[145,0,145,16],[146,0,146,2],[149,11,149,13],[152,0,152,16],[135,11,135,13],[138,0,138,16],[139,0,139,2],[142,11,142,13],[125,0,125,2],[128,11,128,13],[131,0,131,16],[132,0,132,2],[118,0,118,16],[119,0,119,2],[122,11,122,13],[124,0,124,16],[108,11,108,13],[111,0,111,16],[112,0,112,2],[115,11,115,13],[98,0,98,2],[101,11,101,13],[104,0,104,16],[105,0,105,2],[50,29,50,31],[54,0,54,2],[87,11,87,13],[53,0,53,16],[50,11,50,13],[6,5,7,13],[201,0,201,16],[202,0,202,2],[205,11,205,13],[90,0,90,16],[91,0,91,2],[94,11,94,13],[14,0,14,16],[15,0,15,2],[97,0,97,16],[208,0,208,16],[209,0,209,2],[212,11,212,13],[215,0,215,16],[216,0,216,2],[219,11,219,13],[222,0,222,16],[223,0,223,2],[226,11,226,13],[229,0,229,16],[230,0,230,2],[233,11,233,13],[236,0,236,16],[237,0,237,2],[240,11,240,13],[243,0,243,16],[244,0,244,2],[247,11,247,13],[250,0,250,16],[251,0,251,2],[254,11,254,13],[257,0,257,16],[258,0,258,2],[261,11,261,13],[264,0,264,16],[275,11,275,13],[265,0,265,2],[268,11,268,13],[271,0,271,16],[272,0,272,2],[278,0,278,16],[279,0,279,2],[282,11,282,13],[285,0,285,16],[286,0,286,2],[289,11,289,13],[292,0,292,16],[293,0,293,2],[296,11,296,13],[299,0,299,16],[300,0,300,2],[303,11,303,13],[306,0,306,16],[307,0,307,2],[310,11,310,13],[313,0,313,16],[324,11,324,13],[314,0,314,2],[317,11,317,13],[320,0,320,16],[321,0,321,2]],"flags":["formulas_cached_only"]}
["d","l/d ","G / V","A * 10 -4","D мм"]
[1,2,3,4,15]
[15,2.69,685,10.5,20]
[20,1.79,1250,3.15,25]
[25,1.3,2040,1.18,32]
[32,0.895,3580,0.383,40]
[40,0.753,4670,0.225,50,"Гидравлический Расчет однотрубной системы "]
[50,0.54,7810,0.0806,70]
[70,0.377,13600,0.0265,80]
[80,0.304,19200,0.0134,null,null,"для стальных труб D от 15 до 80 мм."]
[100,0.237,28400,0.00611,null,null,"в температурном диапазоне от 60 до 130 С"]
[120,0.181,43400,0.00261,null,null,"t вх",95]
[150,0.144,62600,0.00126,null,null,"t вых",70]
[]
["Расчет системы отопления"]
["№ уч",null,null,"Q вт","G кг/ч","G л/сек","L  м","D мм","l/d ","G / V","A * 10 -4","V м/с","S z","S *10 -4","D P Па","S D P Па","S D P м.в.ст."]
[0,"-",0,90174,3616.091544303797,1.0044698734177213,10,50,0.55,7800,0.082,0.46360148003894835,0,4.51e-05,589.7329243610224,589.7329243610224,0.058973292436102234]
[1,"-",0,44325.3,1842.0353952710768,0.5116764986864102,2,32,1,3500,0.39,0.5262958272203077,0,7.8e-05,264.66136299965484,264.66136299965484,0.026466136299965484]
[2,"-",0,42454.5,1764.290183902555,0.4900806066395986,1.2,32,1,3500,0.39,0.5040829096864443,0,4.68e-05,145.67528912109785,410.33665212075266,0.041033665212075264]
[3,"-",0,41554.5,1726.8887031287313,0.4796913064246476,0.5,32,1,3500,0.39,0.4933967723224947,0,1.95e-05,58.15181956337581,468.48847168412846,0.046848847168412845]
[4,"-",0,39995.5,1662.1010269882968,0.46169472971897135,4,32,1,3500,0.39,0.4748860077109419,0,0.000156,430.96245253082594,899.4509242149544,0.08994509242149544]
[5,"-",0,35162.6,1461.259230952949,0.40590534193137473,6,32,1,3500,0.39,0.41750263741512833,0,0.000234,499.65517837057774,1399.1061025855322,0.13991061025855323]
[6,"-",0,31421,1305.7688082159061,0.3627135578377517,4.5,25,1.4,2000,1.23,0.652884404107953,0,0.0007748999999999999,1321.2294366768795,2720.3355392624117,0.2720335539262412]
[7,null,null,28926.6,1202.1085263912105,0.3339190351086696,5,25,1.4,2000,1.23,0.6010542631956053,0,0.0008609999999999999,1244.2008868405271,3964.536426102939,0.3964536426102939]
[8,null,null,24873.2,1033.6605684260805,0.28712793567391126,4,25,1.4,2000,1.23,0.5168302842130402,0,0.0006887999999999999,735.9512327911974,4700.487658894136,0.47004876588941363]
[9,null,null,23002.4,955.915357057559,0.26553204362709976,2,25,1.4,2000,1.23,0.4779576785287795,0,0.00034439999999999997,314.70382409926066,5015.191482993397,0.5015191482993396]
[10,null,null,22102.4,918.5138762837353,0.2551427434121487,3.7,25,1.4,2000,1.23,0.45925693814186763,0,0.0006371399999999999,537.5344644534468,5552.725947446844,0.5552725947446844]
[11,null,null,17425.4,724.1508478624313,0.2011530132951198,4.8,25,1.4,2000,1.23,0.36207542393121567,0,0.00082656,433.4434769721168,5986.16942441896,0.598616942441896]
[12,null,null,13683.8,568.660425125388,0.15796122920149666,1,25,1.4,2000,1.23,0.284330212562694,0,0.00017219999999999998,55.68511974167212,6041.854544160632,0.6041854544160632]
[13,null,null,11033.5,458.5213756866491,0.12736704880184696,3,20,1.8,1250,3.19,0.36681710054931926,0,0.0017226,362.16261418901286,6404.017158349645,0.6404017158349645]
[14,null,null,8383.2,348.38232624791016,0.09677286840219726,2.8,20,1.8,1250,3.19,0.2787058609983281,0,0.00160776,195.1342254901257,6599.1513838397705,0.6599151383839771]
[15,null,null,3706.2,154.01929782660613,0.04278313828516837,3.8,20,1.8,1250,3.19,0.12321543826128491,0,0.0021819599999999997,51.76033315498362,6650.911716994754,0.6650911716994754]
["16 п/с",null,"ст.17",900,37.401480773823735,0.010389300214951037,21.8,15,2.7,690,10.6,0.054205044599744547,12.7,0.0758536,106.10938338981715,6757.021100384572,0.6757021100384571]
[17,null,null,3706.2,154.01929782660613,0.04278313828516837,3.8,20,1.8,1250,3.19,0.12321543826128491,0,0.0021819599999999997,51.76033315498362,6808.781433539555,0.6808781433539555]
[18,null,null,8383.2,348.38232624791016,0.09677286840219726,2.8,25,1.4,2000,1.23,0.17419116312395508,0,0.0004821599999999999,58.51987744583706,6867.301310985392,0.6867301310985392]
[19,null,null,11033.5,458.5213756866491,0.12736704880184696,3,25,1.4,2000,1.23,0.22926068784332454,0,0.0005166,108.61094072335078,6975.912251708743,0.6975912251708742]
[20,null,null,13683.8,568.660425125388,0.15796122920149666,1,25,1.4,2000,1.23,0.284330212562694,0,0.00017219999999999998,55.68511974167212,7031.597371450414,0.7031597371450414]
[21,null,null,17425.4,724.1508478624313,0.2011530132951198,4.8,25,1.4,2000,1.23,0.36207542393121567,0,0.00082656,433.4434769721168,7465.040848422531,0.7465040848422531]
[22,null,null,22102.4,918.5138762837353,0.2551427434121487,3.7,25,1.4,2000,1.23,0.45925693814186763,0,0.0006371399999999999,537.5344644534468,8002.575312875978,0.8002575312875978]
[23,null,null,23002.4,955.915357057559,0.26553204362709976,2,25,1.4,2000,1.23,0.4779576785287795,0,0.00034439999999999997,314.70382409926066,8317.27913697524,0.831727913697524]
[24,null,null,24873.2,1033.6605684260805,0.28712793567391126,4,25,1.4,2000,1.23,0.5168302842130402,0,0.0006887999999999999,735.9512327911974,9053.230369766437,0.9053230369766437]
[25,null,null,28926.6,1202.1085263912105,0.3339190351086696,5,25,1.4,2000,1.23,0.6010542631956053,0,0.0008609999999999999,1244.2008868405271,10297.431256606964,1.0297431256606964]
[26,null,null,31421,1305.7688082159061,0.3627135578377517,4.5,25,1.4,2000,1.23,0.652884404107953,0,0.0007748999999999999,1321.2294366768795,11618.660693283844,1.1618660693283844]
[27,null,null,35162.6,1461.259230952949,0.40590534193137473,6,32,1,3500,0.39,0.41750263741512833,0,0.000234,499.65517837057774,12118.315871654422,1.2118315871654421]
[28,null,null,39995.5,1662.1010269882968,0.46169472971897135,4,32,1,3500,0.39,0.4748860077109419,0,0.000156,430.96245253082594,12549.278324185248,1.254927832418525]
[29,null,null,41554.5,1726.8887031287313,0.4796913064246476,0.5,32,1,3500,0.39,0.4933967723224947,0,1.95e-05,58.15181956337581,12607.430143748625,1.2607430143748624]
[30,null,null,42454.5,1764.290183902555,0.4900806066395986,1.2,32,1,3500,0.39,0.5040829096864443,0,4.68e-05,145.67528912109785,12753.105432869723,1.2753105432869722]
[31,null,null,88303.4,3669.642130403629,1.0193450362232304,2,32,1,3500,0.39,1.0484691801153225,0,7.8e-05,1050.369322488196,13803.474755357918,1.3803474755357918]
[32,null,null,88615.2,3682.599665631716,1.0229443515643657,5,50,0.55,7800,0.082,0.47212816226047644,0,2.255e-05,305.8127337043591,14109.287489062277,1.4109287489062277]
[{"$nulls":13},"Сумма",14699.020413423297,"Па"]
[{"$nulls":11},"Местн. Сопротивления",null,null,5879.608165369319,0.4,null,"%","∆Р","dш."]
[{"$nulls":13},"Сумма",20578.628578792617,"Па",null,2.0638713824552695,0.04336667500897893,4.78887841155284]
[]
["Расчет системы "]
["№ уч",null,null,"Q вт","G кг/ч","G л/сек","L  м","D мм","l/d ","G / V","A * 10 -4","V м/с","S z","S *10 -4","D P Па","S D P Па","S D P м.в.ст."]
[33,"-",0,45848.9,1905.3519465010745,0.5292644295836318,1,32,1,3500,0.39,0.5443862704288784,0,3.9e-05,141.5842755613819,141.5842755613819,0.01415842755613819]
[34,"-",0,43078.1,1790.205254358729,0.4972792373218692,2.8,32,1,3500,0.39,0.5114872155310655,0,0.00010919999999999998,349.96796591850926,491.55224147989117,0.04915522414798912]
[35,"-",0,41051.4,1705.9812753761641,0.47388368760449007,5.2,32,1,3500,0.39,0.4874232215360469,0,0.0002028,590.2234643002321,1081.7757057801232,0.10817757057801232]
[36,"-",0,38557,1602.3209935514685,0.4450891648754079,1,32,1,3500,0.39,0.45780599815756245,0,3.9e-05,100.12987008865484,1181.905575868778,0.1181905575868778]
[37,"-",0,35750.8,1485.7031764986864,0.41269532680519067,3.5,32,1,3500,0.39,0.42448662185676755,0,0.0001365,301.2983512618562,1483.2039271306342,0.1483203927130634]
[38,"-",0,32788.7,1362.6065918318602,0.3785018310644056,4.5,25,1.4,2000,1.23,0.6813032959159301,0,0.0007748999999999999,1438.7542915079086,2921.958218638543,0.2921958218638543]
[39,null,null,30762,1278.3826128492951,0.35510628134702643,0.5,25,1.4,2000,1.23,0.6391913064246476,0,8.609999999999999e-05,140.70996722632714,3062.66818586487,0.30626681858648697]
[40,null,null,29862,1240.9811320754714,0.3447169811320754,0.7,25,1.4,2000,1.23,0.6204905660377357,0,0.00012053999999999998,185.63571887196855,3248.3039047368384,0.32483039047368384]
[41,null,null,27991.2,1163.2359207069499,0.3231210890852638,2.8,25,1.4,2000,1.23,0.5816179603534749,0,0.0004821599999999999,652.4192819306153,3900.723186667454,0.39007231866674535]
[43,null,null,24285,1009.2166228803437,0.2803379508000955,6.5,25,1.4,2000,1.23,0.5046083114401718,0,0.0011193,1140.0274121914379,5040.750598858892,0.5040750598858892]
[44,null,null,17893.1,743.5871507045615,0.20655198630682264,3.5,25,1.4,2000,1.23,0.37179357535228075,0,0.0006027,333.24599941262784,5373.996598271519,0.537399659827152]
[45,null,null,14619.2,607.5330308096488,0.16875917522490244,2.6,25,1.4,2000,1.23,0.3037665154048244,0,0.00044772,165.25183283170452,5539.248431103224,0.5539248431103224]
[46,null,null,10098.1,419.6487700023883,0.1165691027784412,5,20,1.8,1250,3.19,0.3357190160019106,0,0.0028710000000000003,505.59771386232944,6044.846144965553,0.6044846144965553]
[47,null,null,5732.9,238.2432768091712,0.06617868800254756,4.1,20,1.8,1250,3.19,0.19059462144733696,0,0.0023542199999999998,133.62519512495965,6178.471340090513,0.6178471340090513,null,"пр-лев"]
[48,null,null,2926.7,121.62545975638879,0.03378484993233022,2.8,20,1.8,1250,3.19,0.09730036780511103,0,0.00160776,23.783195696621714,6202.254535787135,0.6202254535787135,null,-6.772184908712056]
["49 п/с",null,"ст.36",900,37.401480773823735,0.010389300214951037,21.8,15,2.7,690,10.6,0.054205044599744547,12.7,0.0758536,106.10938338981715,6308.363919176953,0.6308363919176952]
[50,null,null,2926.7,121.62545975638879,0.03378484993233022,2.8,25,1.4,2000,1.23,0.060812729878194395,0,0.0004821599999999999,7.132473526573073,6315.496392703526,0.6315496392703526]
[51,null,null,5732.9,238.2432768091712,0.06617868800254756,4.1,25,1.4,2000,1.23,0.11912163840458559,0,0.0007060199999999999,40.073595612187475,6355.569988315713,0.6355569988315714]
[52,null,null,10098.1,419.6487700023883,0.1165691027784412,5,25,1.4,2000,1.23,0.20982438500119416,0,0.0008609999999999999,151.62648263164945,6507.196470947362,0.6507196470947362]
[53,null,null,14619.2,607.5330308096488,0.16875917522490244,2.6,25,1.4,2000,1.23,0.3037665154048244,0,0.00044772,165.25183283170452,6672.448303779067,0.6672448303779067]
[42,null,null,17893.1,743.5871507045615,0.20655198630682264,3.5,25,1.4,2000,1.23,0.37179357535228075,0,0.0006027,333.24599941262784,7005.694303191694,0.7005694303191694]
[54,null,null,24285,1009.2166228803437,0.2803379508000955,6.5,25,1.4,2000,1.23,0.5046083114401718,0,0.0011193,1140.0274121914379,8145.7217153831325,0.8145721715383133]
[55,null,null,27991.2,1163.2359207069499,0.3231210890852638,2.8,25,1.4,2000,1.23,0.5816179603534749,0,0.0004821599999999999,652.4192819306153,8798.140997313747,0.8798140997313747]
[56,null,null,29862,1240.9811320754714,0.3447169811320754,0.7,25,1.4,2000,1.23,0.6204905660377357,0,0.00012053999999999998,185.63571887196855,8983.776716185715,0.8983776716185715]
[57,null,null,30762,1278.3826128492951,0.35510628134702643,0.5,25,1.4,2000,1.23,0.6391913064246476,0,8.609999999999999e-05,140.70996722632714,9124.486683412042,0.9124486683412042]
[58,null,null,32788.7,1362.6065918318602,0.3785018310644056,4.5,25,1.4,2000,1.23,0.6813032959159301,0,0.0007748999999999999,1438.7542915079086,10563.24097491995,1.056324097491995]
[59,null,null,35750.8,1485.7031764986864,0.41269532680519067,3.5,32,1,3500,0.39,0.42448662185676755,0,0.0001365,301.2983512618562,10864.539326181806,1.0864539326181806]
[60,null,null,38557,1602.3209935514685,0.4450891648754079,1,32,1,3500,0.39,0.45780599815756245,0,3.9e-05,100.12987008865484,10964.66919627046,1.096466919627046]
[61,null,null,41051.4,1705.9812753761641,0.47388368760449007,5.2,32,1,3500,0.39,0.4874232215360469,0,0.0002028,590.2234643002321,11554.892660570693,1.1554892660570693]
[62,null,null,43078.1,1790.205254358729,0.4972792373218692,2.8,32,1,3500,0.39,0.5114872155310655,0,0.00010919999999999998,349.96796591850926,11904.860626489202,1.1904860626489202]
[63,null,null,45848.9,1905.3519465010745,0.5292644295836318,1,32,1,3500,0.39,0.5443862704288784,0,3.9e-05,141.5842755613819,12046.444902050584,1.2046444902050584]
[{"$nulls":13},"Сумма",13992.35988260416,"Па"]
[{"$nulls":11},"Местн. Сопротивления",null,null,5596.943953041664,0.4,null,"%","∆Р","dш."]
[{"$nulls":13},"Сумма",19589.303835645824,"Па",null,{"$error":"#VALUE!"},{"$error":"#VALUE!"},{"$error":"#VALUE!"}]
[]
["Расчет системы "]
["№ уч",null,null,"Q вт","G кг/ч","G л/сек","L  м","D мм","l/d ","G / V","A * 10 -4","V м/с","S z","S *10 -4","D P Па","S D P Па","S D P м.в.ст."]
[64,"-","ст.16",2806.2,116.61781705278239,0.032393838070217326,6,20,1.8,1250,3.19,0.0932942536422259,32.3,0.013748899999999998,186.98112505786847,186.98112505786847,0.018698112505786846]
[{"$nulls":13},"Сумма",14779.892155091347,"Па"]
[{"$nulls":11},"Местн. Сопротивления",null,null,5911.956862036539,0.4,null,"%","∆Р","dш."]
[{"$nulls":13},"Сумма",20691.849017127886,"Па",null,1.525041918262263,0.03204463117545201,9.120572039269934]
[]
["Расчет системы "]
["№ уч",null,null,"Q вт","G кг/ч","G л/сек","L  м","D мм","l/d ","G / V","A * 10 -4","V м/с","S z","S *10 -4","D P Па","S D P Па","S D P м.в.ст."]
[65,"-","ст.15",4677,194.363028421304,0.053989730117028886,6,20,1.8,1250,3.19,0.1554904227370432,32.3,0.013748899999999998,519.3920140496347,519.3920140496347,0.05193920140496347]
[{"$nulls":13},"Сумма",15008.782377773146,"Па"]
[{"$nulls":11},"Местн. Сопротивления",null,null,6003.512951109259,0.4]
[{"$nulls":13},"Сумма",21012.295328882406,"Па"]
[]
["Расчет системы "]
["№ уч",null,null,"Q вт","G кг/ч","G л/сек","L  м","D мм","l/d ","G / V","A * 10 -4","V м/с","S z","S *10 -4","D P Па","S D P Па","S D P м.в.ст."]
[66,"-","ст.14",2650.3,110.13904943873895,0.030594180399649708,6,20,1.8,1250,3.19,0.08811123955099116,32.3,0.013748899999999998,166.7825467337161,166.7825467337161,0.01667825467337161]
[{"$nulls":13},"Сумма",14402.518807521266,"Па"]
[{"$nulls":11},"Местн. Сопротивления",null,null,5761.007523008507,0.4,null,"%","∆Р","dш."]
[{"$nulls":13},"Сумма",20163.526330529774,"Па",null,4.039392103850544,0.08487689983526325,6.947870711876243]
[]
["Расчет системы "]
["№ уч",null,null,"Q вт","G кг/ч","G л/сек","L  м","D мм","l/d ","G / V","A * 10 -4","V м/с","S z","S *10 -4","D P Па","S D P Па","S D P м.в.ст."]
[67,"-","ст.13",2650.3,110.13904943873895,0.030594180399649708,6,20,1.8,1250,3.19,0.08811123955099116,32.3,0.013748899999999998,166.7825467337161,166.7825467337161,0.01667825467337161]
[{"$nulls":13},"Сумма",13931.745252608902,"Па"]
[{"$nulls":11},"Местн. Сопротивления",null,null,5572.698101043561,0.4,null,"%","∆Р","dш."]
[{"$nulls":13},"Сумма",19504.443353652463,"Па",null,7.17604598464466,0.15078519752299435,6.018100391001407]
[]
["Расчет системы "]
["№ уч",null,null,"Q вт","G кг/ч","G л/сек","L  м","D мм","l/d ","G / V","A * 10 -4","V м/с","S z","S *10 -4","D P Па","S D P Па","S D P м.в.ст."]
[68,"-","ст.12",3741.6,155.4904227370432,0.043191784093623106,6,20,1.8,1250,3.19,0.12439233818963455,32.3,0.013748899999999998,332.4108889917662,332.4108889917662,0.033241088899176624]
[{"$nulls":13},"Сумма",13986.00335538361,"Па"]
[{"$nulls":11},"Местн. Сопротивления",null,null,5594.401342153444,0.4,null,"%","∆Р","dш."]
[{"$nulls":13},"Сумма",19580.40469753705,"Па",null,6.8145369600681045,0.14318906313453553,7.243572374255173]
["Расчет системы "]
["№ уч",null,null,"Q вт","G кг/ч","G л/сек","L  м","D мм","l/d ","G / V","A * 10 -4","V м/с","S z","S *10 -4","D P Па","S D P Па","S D P м.в.ст."]
["68а","-","ст.11",1650.3,68.58184857893478,0.01905051349414855,6,20,1.8,1250,3.19,0.054865478863147826,32.3,0.013748899999999998,64.66753805747919,64.66753805747919,0.006466753805747919]
[{"$nulls":13},"Сумма",12851.37305050509,"Па"]
[{"$nulls":11},"Местн. Сопротивления",null,null,5140.549220202036,0.4,null,"%","∆Р","dш."]
[{"$nulls":13},"Сумма",17991.922270707124,"Па",null,14.374312805434611,0.15403730581752825,4.723637465093394,0.148,4.771089990831494]
[]
["Расчет системы "]
["№ уч",null,null,"Q вт","G кг/ч","G л/сек","L  м","D мм","l/d ","G / V","A * 10 -4","V м/с","S z","S *10 -4","D P Па","S D P Па","S D P м.в.ст."]
[69,"-","ст.10",2026.7,84.22397898256506,0.023395549717379182,6,20,1.8,1250,3.19,0.06737918318605204,32.3,0.013748899999999998,97.53027819376472,97.53027819376472,0.009753027819376472]
[{"$nulls":13},"Сумма",12884.235790641374,"Па"]
[{"$nulls":11},"Местн. Сопротивления",null,null,5153.69431625655,0.4,null,"%","∆Р","dш."]
[{"$nulls":13},"Сумма",18037.930106897926,"Па",null,14.155356068577968,0.2974365221984481,4.440662297700544]
[]
["Расчет системы "]
["№ уч",null,null,"Q вт","G кг/ч","G л/сек","L  м","D мм","l/d ","G / V","A * 10 -4","V м/с","S z","S *10 -4","D P Па","S D P Па","S D P м.в.ст."]
[70,"-","ст.9",900,37.401480773823735,0.010389300214951037,21.8,15,2.7,690,10.6,0.054205044599744547,12.7,0.0758536,106.10938338981715,106.10938338981715,0.010610938338981715]
[{"$nulls":13},"Сумма",11817.745966930534,"Па"]
[{"$nulls":11},"Местн. Сопротивления",null,null,4727.098386772213,0.4,null,"%","∆Р","dш."]
[{"$nulls":13},"Сумма",16544.84435370275,"Па",null,21.261127855170265,0.44674509751796576,2.673054989510062,0.03,5.251006165524857]
[]
["Расчет системы "]
["№ уч",null,null,"Q вт","G кг/ч","G л/сек","L  м","D мм","l/d ","G / V","A * 10 -4","V м/с","S z","S *10 -4","D P Па","S D P Па","S D P м.в.ст."]
[71,"-","ст.8",1870.8,77.7452113685216,0.021595892046811553,6,20,1.8,1250,3.19,0.062196169094817275,32.3,0.013748899999999998,83.10272224794156,83.10272224794156,0.008310272224794156]
[{"$nulls":13},"Сумма",11165.331657590137,"Па"]
[{"$nulls":11},"Местн. Сопротивления",null,null,4466.132663036055,0.4,null,"%","∆Р","dш."]
[{"$nulls":13},"Сумма",15631.464320626194,"Па",null,25.60801151914138,0.5380831008256213,3.6787724854976074]
[]
["Расчет системы "]
["№ уч",null,null,"Q вт","G кг/ч","G л/сек","L  м","D мм","l/d ","G / V","A * 10 -4","V м/с","S z","S *10 -4","D P Па","S D P Па","S D P м.в.ст."]
[72,"-","ст.7",4053.4,168.44795796513012,0.046791099434758364,6,20,1.8,1250,3.19,0.1347583663721041,32.3,0.013748899999999998,390.12111277505886,390.12111277505886,0.03901211127750589]
[{"$nulls":13},"Сумма",10000.44758253486,"Па"]
[{"$nulls":11},"Местн. Сопротивления",null,null,4000.1790330139443,0.4,null,"%","∆Р","dш."]
[{"$nulls":13},"Сумма",14000.626615548805,"Па",null,33.3693611458798,0.7011668713333602,5.068225990148277]
[]
["Расчет системы "]
["№ уч",null,null,"Q вт","G кг/ч","G л/сек","L  м","D мм","l/d ","G / V","A * 10 -4","V м/с","S z","S *10 -4","D P Па","S D P Па","S D P м.в.ст."]
[73,"-","ст.6",2494.4,103.66028182469547,0.028794522729082075,6,20,1.8,1250,3.19,0.08292822545975638,32.3,0.013748899999999998,147.73817288522946,147.73817288522946,0.014773817288522947]
[{"$nulls":13},"Сумма",7269.6628689639765,"Па"]
[{"$nulls":11},"Местн. Сопротивления",null,null,2907.865147585591,0.4,null,"%","∆Р","dш."]
[{"$nulls":13},"Сумма",10177.528016549568,"Па",null,51.563939792146044,1.0834767312332838,3.5659868628239315]
[]
["Расчет системы "]
["№ уч",null,null,"Q вт","G кг/ч","G л/сек","L  м","D мм","l/d ","G / V","A * 10 -4","V м/с","S z","S *10 -4","D P Па","S D P Па","S D P м.в.ст."]
[74,"-","ст.5",3741.6,155.4904227370432,0.043191784093623106,6,20,1.8,1250,3.19,0.12439233818963455,32.3,0.013748899999999998,332.4108889917662,332.4108889917662,0.033241088899176624]
[{"$nulls":13},"Сумма",4811.876711716753,"Па"]
[{"$nulls":11},"Местн. Сопротивления",null,null,1924.750684686701,0.4,null,"%","∆Р","dш."]
[{"$nulls":13},"Сумма",6736.6273964034535,"Па",null,67.93959302892704,0.8825667932478953,4.597199702000355,0.545,5.185983612234819]
[]
["Расчет системы "]
["№ уч",null,null,"Q вт","G кг/ч","G л/сек","L  м","D мм","l/d ","G / V","A * 10 -4","V м/с","S z","S *10 -4","D P Па","S D P Па","S D P м.в.ст."]
[75,"-","ст.4",4832.9,200.84179603534747,0.05578938778759652,6,20,1.79,1250,3.19,0.16067343682827798,32.3,0.013729759999999999,553.8231922039992,553.8231922039992,0.05538231922039991]
[{"$nulls":13},"Сумма",4033.9786581878307,"Па"]
[{"$nulls":11},"Местн. Сопротивления",null,null,1613.5914632751324,0.4,null,"%","∆Р","dш."]
[{"$nulls":13},"Сумма",5647.570121462963,"Па",null,73.12254547602846,1.5364725207419443,4.5485638172323055]
[]
["Расчет системы "]
["№ уч",null,null,"Q вт","G кг/ч","G л/сек","L  м","D мм","l/d ","G / V","A * 10 -4","V м/с","S z","S *10 -4","D P Па","S D P Па","S D P м.в.ст."]
[76,"-","ст.3",1559,64.78767614043467,0.017996576705676295,6,20,1.8,1250,3.19,0.051830140912347736,32.3,0.013748899999999998,57.710223783292754,57.710223783292754,0.005771022378329276]
[{"$nulls":13},"Сумма",2675.9407847054727,"Па"]
[{"$nulls":11},"Местн. Сопротивления",null,null,1070.3763138821892,0.4,null,"%","∆Р","dш."]
[{"$nulls":13},"Сумма",3746.317098587662,"Па",null,82.17083360027704,1.7265978230294745,2.5091512871634998]
[]
["Расчет системы "]
["№ уч",null,null,"Q вт","G кг/ч","G л/сек","L  м","D мм","l/d ","G / V","A * 10 -4","V м/с","S z","S *10 -4","D P Па","S D P Па","S D P м.в.ст."]
[77,"-","ст.2",900,37.401480773823735,0.010389300214951037,21.8,15,2.7,690,10.6,0.054205044599744547,12.7,0.0758536,106.10938338981715,106.10938338981715,0.010610938338981715]
[{"$nulls":13},"Сумма",2608.0363051852455,"Па"]
[{"$nulls":11},"Местн. Сопротивления",null,null,1043.2145220740983,0.4,null,"%","∆Р","dш."]
[{"$nulls":13},"Сумма",3651.250827259344,"Па",null,82.62326523537614,1.7361044501623062,1.9038331269011264,1.28,2.0545671948831785]
[]
["Расчет системы "]
["№ уч",null,null,"Q вт","G кг/ч","G л/сек","L  м","D мм","l/d ","G / V","A * 10 -4","V м/с","S z","S *10 -4","D P Па","S D P Па","S D P м.в.ст."]
[78,"-","ст.1",1870.8,77.7452113685216,0.021595892046811553,6,20,1.8,1250,3.19,0.062196169094817275,32,0.013653199999999999,82.52428102579812,82.52428102579812,0.008252428102579812]
[{"$nulls":13},"Сумма",1242.7313020908343,"Па"]
[{"$nulls":11},"Местн. Сопротивления",null,null,497.09252083633373,0.4,null,"%","∆Р","dш."]
[{"$nulls":13},"Сумма",1739.823822927168,"Па",null,91.71997254133538,1.927247150595524,2.6741201391078544]
[]
["Расчет системы "]
["№ уч",null,null,"Q вт","G кг/ч","G л/сек","L  м","D мм","l/d ","G / V","A * 10 -4","V м/с","S z","S *10 -4","D P Па","S D P Па","S D P м.в.ст."]
[79,"-","ст.35",900,37.401480773823735,0.010389300214951037,6,20,1.8,1250,3.19,0.029921184619058988,13,0.0075921999999999995,10.620506615007987,10.620506615007987,0.0010620506615007987]
[{"$nulls":13},"Сумма",13307.138081468329,"Па"]
[{"$nulls":11},"Местн. Сопротивления",null,null,5322.855232587332,0.4,null,"%","∆Р","dш."]
[{"$nulls":13},"Сумма",18629.99331405566,"Па",null,4.8971139027643575,0.09593105215901633,3.926748079043661]
[]
["Расчет системы "]
["№ уч",null,null,"Q вт","G кг/ч","G л/сек","L  м","D мм","l/d ","G / V","A * 10 -4","V м/с","S z","S *10 -4","D P Па","S D P Па","S D P м.в.ст."]
[80,"-","ст.34",2806.2,116.61781705278239,0.032393838070217326,6,20,1.8,1250,3.19,0.0932942536422259,32,0.013653199999999999,185.67963230804574,185.67963230804574,0.018567963230804573]
[{"$nulls":13},"Сумма",13451.28153793817,"Па"]
[{"$nulls":11},"Местн. Сопротивления",null,null,5380.512615175268,0.4,null,"%","∆Р","dш."]
[{"$nulls":13},"Сумма",18831.79415311344,"Па",null,3.866955604384353,0.07575096825323853,7.355527952498374]
[]
["Расчет системы "]
["№ уч",null,null,"Q вт","G кг/ч","G л/сек","L  м","D мм","l/d ","G / V","A * 10 -4","V м/с","S z","S *10 -4","D P Па","S D P Па","S D P м.в.ст."]
[81,"-","ст.33",3273.9,136.0541198949128,0.037792811081920216,6,20,1.8,1250,3.19,0.10884329591593023,32,0.013653199999999999,252.73061064150667,252.73061064150667,0.025273061064150667]
[{"$nulls":13},"Сумма",13344.633725534486,"Па"]
[{"$nulls":11},"Местн. Сопротивления",null,null,5337.853490213794,0.4,null,"%","∆Р","dш."]
[{"$nulls":13},"Сумма",18682.487215748282,"Па",null,4.629141635178713,0.09068166198975414,7.595466005748152]
[]
["Расчет системы "]
["№ уч",null,null,"Q вт","G кг/ч","G л/сек","L  м","D мм","l/d ","G / V","A * 10 -4","V м/с","S z","S *10 -4","D P Па","S D P Па","S D P м.в.ст."]
["81а","-","ст.32",1091.3,45.35137329830427,0.012597603693973407,6,20,1.8,1250,3.19,0.036281098638643414,32,0.013653199999999999,28.081178960167414,28.081178960167414,0.0028081178960167414]
[{"$nulls":13},"Сумма",13119.984293853146,"Па"]
[{"$nulls":11},"Местн. Сопротивления",null,null,5247.993717541259,0.4]
[{"$nulls":13},"Сумма",18367.978011394403,"Па"]
[]
["Расчет системы "]
["№ уч",null,null,"Q вт","G кг/ч","G л/сек","L  м","D мм","l/d ","G / V","A * 10 -4","V м/с","S z","S *10 -4","D P Па","S D P Па","S D P м.в.ст."]
[82,"-","ст.31",4521.1,187.88426080726055,0.05219007244646126,6,20,1.8,1250,3.19,0.15030740864580844,32,0.013653199999999999,481.9647246020571,481.9647246020571,0.04819647246020571]
[{"$nulls":13},"Сумма",12916.64364300106,"Па"]
[{"$nulls":11},"Местн. Сопротивления",null,null,5166.657457200425,0.4,null,"%","∆Р","dш."]
[{"$nulls":13},"Сумма",18083.301100201483,"Па",null,7.687882877715806,0.1506002735444341,7.862618493775788]
[]
["Расчет системы "]
["№ уч",null,null,"Q вт","G кг/ч","G л/сек","L  м","D мм","l/d ","G / V","A * 10 -4","V м/с","S z","S *10 -4","D P Па","S D P Па","S D P м.в.ст."]
[83,"-","ст.30",3273.9,136.0541198949128,0.037792811081920216,6,20,1.8,1250,3.19,0.10884329591593023,32,0.013653199999999999,252.73061064150667,252.73061064150667,0.025273061064150667]
[{"$nulls":13},"Сумма",12356.9058633771,"Па"]
[{"$nulls":11},"Местн. Сопротивления",null,null,4942.76234535084,0.4,null,"%","∆Р","dш."]
[{"$nulls":13},"Сумма",17299.66820872794,"Па",null,11.688192934919568,0.22896356269178833,6.025494558831013]
[]
["Расчет системы "]
["№ уч",null,null,"Q вт","G кг/ч","G л/сек","L  м","D мм","l/d ","G / V","A * 10 -4","V м/с","S z","S *10 -4","D P Па","S D P Па","S D P м.в.ст."]
[84,"-","ст.29",2806.2,116.61781705278239,0.032393838070217326,6,20,1.8,1250,3.19,0.0932942536422259,32,0.013653199999999999,185.67963230804574,185.67963230804574,0.018567963230804573]
[{"$nulls":13},"Сумма",11623.362886218383,"Па"]
[{"$nulls":11},"Местн. Сопротивления",null,null,4649.345154487353,0.4,null,"%","∆Р","dш."]
[{"$nulls":13},"Сумма",16272.708040705736,"Па",null,16.930646554703078,0.3316595794940087,5.084962574915422]
[]
["Расчет системы "]
["№ уч",null,null,"Q вт","G кг/ч","G л/сек","L  м","D мм","l/d ","G / V","A * 10 -4","V м/с","S z","S *10 -4","D P Па","S D P Па","S D P м.в.ст."]
["84а","-","ст.28",3585.7,149.01165512299974,0.04139212642305548,6,20,1.8,1250,3.19,0.1192093240983998,32,0.013653199999999999,303.1621157128278,303.1621157128278,0.03031621157128278]
[{"$nulls":13},"Сумма",11740.845369623166,"Па"]
[{"$nulls":11},"Местн. Сопротивления",null,null,4696.3381478492665,0.4,null,"%","∆Р","dш."]
[{"$nulls":13},"Сумма",16437.183517472433,"Па",null,16.091027759943216,0.3152120318173391,5.821539736273186]
[]
["Расчет системы "]
["№ уч",null,null,"Q вт","G кг/ч","G л/сек","L  м","D мм","l/d ","G / V","A * 10 -4","V м/с","S z","S *10 -4","D P Па","S D P Па","S D P м.в.ст."]
[85,"-","ст.27",2806.2,116.61781705278239,0.032393838070217326,6,20,1.8,1250,3.19,0.0932942536422259,32,0.013653199999999999,185.67963230804574,185.67963230804574,0.018567963230804573]
[{"$nulls":13},"Сумма",9343.308061835509,"Па"]
[{"$nulls":11},"Местн. Сопротивления",null,null,3737.323224734204,0.4,null,"%","∆Р","dш."]
[{"$nulls":13},"Сумма",13080.631286569713,"Па",null,33.225644993226126,0.6508672549076111,4.296232653463687]
[]
["Расчет системы "]
["№ уч",null,null,"Q вт","G кг/ч","G л/сек","L  м","D мм","l/d ","G / V","A * 10 -4","V м/с","S z","S *10 -4","D P Па","S D P Па","S D P м.в.ст."]
[86,"-","ст.26",900,37.401480773823735,0.010389300214951037,21.8,15,2.7,690,10.6,0.054205044599744547,13,0.0761716,106.55422429279292,106.55422429279292,0.010655422429279292]
[{"$nulls":13},"Сумма",9264.182653820257,"Па"]
[{"$nulls":11},"Местн. Сопротивления",null,null,3705.673061528103,0.4,null,"%","∆Р","dш."]
[{"$nulls":13},"Сумма",12969.85571534836,"Па",null,33.791135079809905,0.6619448120297464,2.4227990584297707]
[]
["Расчет системы "]
["№ уч",null,null,"Q вт","G кг/ч","G л/сек","L  м","D мм","l/d ","G / V","A * 10 -4","V м/с","S z","S *10 -4","D P Па","S D P Па","S D P м.в.ст."]
[87,"-","ст.25",1870.8,77.7452113685216,0.021595892046811553,8,20,1.8,1250,3.19,0.062196169094817275,32,0.0148016,89.46557569151945,89.46557569151945,0.008946557569151945]
[{"$nulls":13},"Сумма",7942.255441357752,"Па"]
[{"$nulls":11},"Местн. Сопротивления",null,null,3176.9021765431007,0.4,null,"%","∆Р","dш."]
[{"$nulls":13},"Сумма",11119.157617900852,"Па",null,43.23862802276928,0.8470146217744972,3.2842978871743207]
[]
["Расчет системы "]
["№ уч",null,null,"Q вт","G кг/ч","G л/сек","L  м","D мм","l/d ","G / V","A * 10 -4","V м/с","S z","S *10 -4","D P Па","S D P Па","S D P м.в.ст."]
[88,"-","ст.24",900,37.401480773823735,0.010389300214951037,21.8,15,2.7,690,10.6,0.054205044599744547,13,0.0761716,106.55422429279292,106.55422429279292,0.010655422429279292]
[{"$nulls":13},"Сумма",7588.072652215089,"Па"]
[{"$nulls":11},"Местн. Сопротивления",null,null,3035.2290608860358,0.4,null,"%","∆Р","dш."]
[{"$nulls":13},"Сумма",10623.301713101126,"Па",null,45.76988645318597,0.8966002122544698,2.2458106270672538]
[]
["Расчет системы "]
["№ уч",null,null,"Q вт","G кг/ч","G л/сек","L  м","D мм","l/d ","G / V","A * 10 -4","V м/с","S z","S *10 -4","D P Па","S D P Па","S D P м.в.ст."]
[89,"-","ст.23",2026.7,84.22397898256506,0.023395549717379182,6,20,1.8,1250,3.19,0.06737918318605204,32,0.013653199999999999,96.85141314833248,96.85141314833248,0.009685141314833248]
[{"$nulls":13},"Сумма",7296.949906617974,"Па"]
[{"$nulls":11},"Местн. Сопротивления",null,null,2918.7799626471897,0.4,null,"%","∆Р","dш."]
[{"$nulls":13},"Сумма",10215.729869265164,"Па",null,47.850470057664666,0.9373573966380659,3.332882617146765]
[]
["Расчет системы "]
["№ уч",null,null,"Q вт","G кг/ч","G л/сек","L  м","D мм","l/d ","G / V","A * 10 -4","V м/с","S z","S *10 -4","D P Па","S D P Па","S D P м.в.ст."]
[90,"-","ст.22",2962.1,123.09658466682586,0.03419349574078496,6,20,1.8,1250,3.19,0.09847726773346069,32,0.013653199999999999,206.88378784939667,206.88378784939667,0.020688378784939666]
[{"$nulls":13},"Сумма",4529.473698303221,"Па"]
[{"$nulls":11},"Местн. Сопротивления",null,null,1811.7894793212884,0.4,null,"%","∆Р","dш."]
[{"$nulls":13},"Сумма",6341.263177624509,"Па",null,67.62895082526832,1.3248040658021314,3.6954176791749918]
[]
["Расчет системы "]
["№ уч",null,null,"Q вт","G кг/ч","G л/сек","L  м","D мм","l/d ","G / V","A * 10 -4","V м/с","S z","S *10 -4","D P Па","S D P Па","S D P м.в.ст."]
[91,"-","ст.21",2806.2,116.61781705278239,0.032393838070217326,6,20,1.8,1250,3.19,0.0932942536422259,32,0.013653199999999999,185.67963230804574,185.67963230804574,0.018567963230804573]
[{"$nulls":13},"Сумма",3905.6728402381577,"Па"]
[{"$nulls":11},"Местн. Сопротивления",null,null,1562.269136095263,0.4,null,"%","∆Р","dш."]
[{"$nulls":13},"Сумма",5467.941976333421,"Па",null,72.08710415536238,1.4121361859312402,3.539906179965525]
[]
["Расчет системы "]
["№ уч",null,null,"Q вт","G кг/ч","G л/сек","L  м","D мм","l/d ","G / V","A * 10 -4","V м/с","S z","S *10 -4","D P Па","S D P Па","S D P м.в.ст."]
[92,"-","ст.20",2494.4,103.66028182469547,0.028794522729082075,6,20,1.8,1250,3.19,0.08292822545975638,32,0.013653199999999999,146.70983293475223,146.70983293475223,0.014670983293475224]
[{"$nulls":13},"Сумма",3666.4433006875543,"Па"]
[{"$nulls":11},"Местн. Сопротивления",null,null,1466.5773202750217,0.4,null,"%","∆Р","dш."]
[{"$nulls":13},"Сумма",5133.020620962576,"Па",null,73.79681961120927,1.4456283214683248,3.317954866575359]
[]
["Расчет системы "]
["№ уч",null,null,"Q вт","G кг/ч","G л/сек","L  м","D мм","l/d ","G / V","A * 10 -4","V м/с","S z","S *10 -4","D P Па","S D P Па","S D P м.в.ст."]
[93,"-","ст.19",2026.7,84.22397898256506,0.023395549717379182,6,20,1.8,1250,3.19,0.06737918318605204,32,0.013653199999999999,96.85141314833248,96.85141314833248,0.009685141314833248]
[{"$nulls":13},"Сумма",2436.1379523006703,"Па"]
[{"$nulls":11},"Местн. Сопротивления",null,null,974.4551809202682,0.4,null,"%","∆Р","dш."]
[{"$nulls":13},"Сумма",3410.5931332209384,"Па",null,82.58951332913206,1.6178710702424886,2.9077719554760004]
[]
["Расчет системы "]
["№ уч",null,null,"Q вт","G кг/ч","G л/сек","L  м","D мм","l/d ","G / V","A * 10 -4","V м/с","S z","S *10 -4","D P Па","S D P Па","S D P м.в.ст."]
[94,"-","ст.18",1870.8,77.7452113685216,0.021595892046811553,6,20,1.8,1250,3.19,0.062196169094817275,32,0.013653199999999999,82.52428102579812,82.52428102579812,0.008252428102579812]
[{"$nulls":13},"Сумма",1721.874888341117,"Па"]
[{"$nulls":11},"Местн. Сопротивления",null,null,688.7499553364469,0.4,null,"%","∆Р","dш."]
[{"$nulls":13},"Сумма",2410.624843677564,"Па",null,87.6941780887024,1.717867899196826,2.752122916913739]

{"sheet":"Лист2","index":1,"n_rows":28,"n_cols":5,"rows_kept":28,"cut":false,"hidden":false,"merged":[[0,0,0,1],[0,3,0,4]],"flags":["formulas_cached_only"]}
[null,null,null,"Ведомость дроссельных шайб"]
[null,null,null,"№ стояка","d шайбы"]
[null,null,null,13,6.1]
[null,null,null,12,7.4]
[null,null,null,11,4.1]
[null,null,null,10,4.6]
[null,null,null,9,2.8]
[null,null,null,8,3.8]
[null,null,null,7,5.3]
[null,null,null,6,3.7]
[null,null,null,5,4.3]
[null,null,null,4,4.8]
[null,null,null,3,2.7]
[null,null,null,2,2]
[null,null,null,1,2.9]
[null,null,null,30,6.8]
[null,null,null,29,5.6]
[null,null,null,28,6.4]
[null,null,null,27,4.6]
[null,null,null,26,2.6]
[null,null,null,25,3.5]
[null,null,null,24,2.4]
[null,null,null,23,3.6]
[null,null,null,22,3.9]
[null,null,null,21,3.8]
[null,null,null,20,3.6]
[null,null,null,19,3.2]
[null,null,null,18,3]

{"sheet":"Лист3","index":2,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}