{"text_format":"2","workbook":"xlsx","n_sheets":1,"sheets":["Лист1"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":0,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Лист1","index":0,"n_rows":23,"n_cols":21,"rows_kept":23,"cut":false,"hidden":false,"merged":[[13,11,13,12],[13,13,13,17],[13,1,13,6]]}
[]
["Расчетная тепловая нагрузка",{"$nulls":8},100,"кВт"]
["Температура в подающем трубопроводе",{"$nulls":8},80,"°С"]
["Температура вобратном трубопроводе",{"$nulls":8},60,"°С"]
["Плотность теплоносителя",{"$nulls":8},{"$f":"1/0.0010228","v":977.70825185764579},"кг/м3"]
["Теплоемкость теплоносителя",{"$nulls":8},{"$f":"293/70","v":4.1857142857142859},"кДЖ/(кг·°С)"]
["Расход теплоносителя",{"$nulls":8},{"$f":"J2/J6/(J3-J4)/J5*1000","v":1.2217747440273037},"л/с"]
["Расход теплоносителя",{"$nulls":8},{"$f":"J7*3.6","v":4.3983890784982931},"м3/час"]
["Длина трубопроводов отопления",{"$nulls":8},100,"м"]
["Район строительства",{"$nulls":8},"Белгород"]
["Продолжительность отопительного периода",{"$nulls":8},191,"сут."]
["Стоимость электроэнергии",{"$nulls":8},3.33,"руб./кВт·час"]
[]
[null,"Труба Ekoplastik S5 (PN20)",{"$nulls":5},"Скорость","Удельные потери на трение","Потери на трение по длине","Коэффициент потерь в местных сопротивлениях","Общие потери",null,"Насос",{"$nulls":4},"Стоимость системы","Затраты на электроэнергию","Стоимость системы ПЛЮС 5 лет эксплуатации"]
[null,"dн","х","s","dвн","стоимость","цена*1.3","v","R",{"$nulls":4},"марка","расход","подача","Р1","цена"]
[null,"мм",null,"мм","мм","руб./м","руб.","м/с","кПа/м","кПа",null,"кПа","м вод.ст.",null,"м3/час","м","кВт","руб.","руб.","руб./год","руб."]
[null,32,"х",5.4,{"$f":"B17-D17*2","v":21.2},177.12,{"$f":"$J$9*F17*1.3","v":23025.600000000002},{"$f":"($J$7/1000)/((PI()*(E17/1000)^2)/4)","v":3.4612226745599948},5.1210000000000004,{"$f":"$J$9*I17","v":512.1},1,{"$f":"J17*(1+K17)","v":1024.2},{"$f":"L17/9.81","v":104.40366972477064},"CME10-5 A-R-G-V-AQQV",4.4000000000000004,105,3.9,108275,{"$f":"G17+R17","v":131300.6},{"$f":"$J$11*24*Q17*$J$12","v":59532.407999999996},{"$f":"S17+T17*5","v":428962.64}]
[null,40,"х",6.7,{"$f":"B18-D18*2","v":26.6},253.92,{"$f":"$J$9*F18*1.3","v":33009.599999999999},{"$f":"($J$7/1000)/((PI()*(E18/1000)^2)/4)","v":2.1985583114566172},1.645,{"$f":"$J$9*I18","v":164.5},1,{"$f":"J18*(1+K18)","v":329},{"$f":"L18/9.81","v":33.537206931702343},"CME3-5 A-R-A-V-AQQV",4.4000000000000004,33.5,0.92,47320,{"$f":"G18+R18","v":80329.600000000006},{"$f":"$J$11*24*Q18*$J$12","v":14043.5424},{"$f":"S18+T18*5","v":150547.31200000001}]
[null,50,"х",8.3000000000000007,33.4,384.48,49982.400000000001,1.3944672799797806,0.54900000000000004,54.900000000000006,1,109.80000000000001,11.192660550458717,"CME3-2 A-R-A-E-AQQE",4.4000000000000004,11.2,0.35,39100,89082.4,5342.652,115795.66]
[null,63,"х",10.5,42,574.08000000000004,74630.400000000009,0.88186616715093191,0.17299999999999999,17.299999999999997,1,34.599999999999994,3.527013251783893,"MAGNA 25-60",4.4000000000000004,3.5,8.1000000000000003E-2,15880,90510.400000000009,1236.4423200000001,96692.611600000004]
[null,75,"х",12.5,50,1020.96,132724.80000000002,0.62224476754169755,7.3999999999999996E-2,7.3999999999999995,1,14.799999999999999,1.5086646279306828,"MAGNA 25-60",4.4000000000000004,1.5,4.1000000000000002E-2,15880,148604.80000000002,625.85352000000012,151734.06760000001]
[null,90,"х",15,60,1369.92,178089.60000000001,0.43211442190395671,3.1E-2,3.1,1,6.2,0.6320081549439347,"MAGNA 25-40",4.4000000000000004,0.6,3.6999999999999998E-2,12540,190629.6,564.79464000000007,193453.57320000001]
[null,110,"х",18.3,73.400000000000006,2187.36,284356.8,0.28874145603097573,1.2E-2,1.2,1,2.4,0.24464831804281342,"MAGNA 25-40",4.4000000000000004,0.2,3.6999999999999998E-2,12540,296896.8,564.79464000000007,299720.7732]