{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Теплопотери с энергосбер. окнам"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":0,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Теплопотери с энергосбер. окнам","index":0,"n_rows":91,"n_cols":21,"rows_kept":91,"cut":false,"hidden":false,"merged":[[6,1,9,1],[6,0,9,0],[0,0,0,17],[5,0,5,17],[2,14,3,14],[2,15,3,15],[1,11,1,16],[2,16,3,16],[27,1,30,1],[11,0,14,0],[11,1,14,1],[16,0,19,0],[16,1,19,1],[21,0,24,0],[21,1,24,1],[26,0,26,17],[27,0,30,0],[32,0,36,0],[32,1,36,1],[38,0,41,0],[58,0,61,0],[38,1,41,1],[43,0,47,0],[43,1,47,1],[58,1,61,1],[63,0,63,17],[64,0,68,0],[64,1,68,1],[70,0,73,0],[70,1,73,1],[49,0,52,0],[49,1,52,1],[54,0,56,0],[54,1,56,1],[75,0,78,0],[75,1,78,1],[80,0,83,0],[80,1,83,1],[85,0,88,0],[85,1,88,1]],"flags":["formulas_cached_only"]}
["Расчет теплопотерь помещений на объекте: Коттедж Сигнал"]
["№","Наименование","Вид","Размер","Размер","Площадь","Коэффиц.","Тем-ра","Тем-ра","Основн.","ори-","Дополнительные теплопотери",{"$nulls":5},"Общие"]
["пом.","помещения","ограждения",null,null,null,"теплоперед.","внутр.","наружн.","теплопот.","ент-","на ориентац.","на инфильтр.","на двери","на нагрев\nавто Q1, Вт","на нагрев матер.\nQм, Вт","на угловое пом.\nQу, Вт","теплопотр."]
[null,null,null,"а, м","b, м","А, м²","К, Вт/м² ˚С","tв, ˚С","tн, ˚С","Qосн, Вт","ация","Qор, Вт","Qинф, Вт","Qдр, Вт",null,null,null,"Qобщ, Вт"]
[1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,16,17,18]
["отм. или этаж: -3.000",{"$nulls":18},"пол1",0.48]
[1,"Гараж","пол1",42,1,42,0.48,10,-36,927.36,{"$nulls":7},927.36]
[null,null,"пол2",42,1,42,0.23,10,-36,444.36,{"$nulls":7},444.36]
[null,null,"пол3",31,1,31,0.12,10,-36,171.11999999999998,{"$nulls":7},171.11999999999998,null,"стена",0.17]
[null,null,"пол4",9,1,9,0.07,10,-36,28.980000000000004,{"$nulls":7},28.980000000000004,null,"перекрытие",0.18]
[{"$nulls":16},"ƩQ=",1571.82,1600,"окно",1.1]
[2,"ЛК","пол1",33,1,33,0.48,16,-36,823.68,{"$nulls":7},823.68]
[null,null,"пол2",33,1,33,0.23,16,-36,394.68000000000006,{"$nulls":7},394.68000000000006]
[null,null,"пол3",13,1,13,0.12,16,-36,81.12,{"$nulls":7},81.12]
[null,null,"пол4",3,1,3,0.07,16,-36,10.920000000000002,{"$nulls":7},10.920000000000002]
[{"$nulls":16},"ƩQ=",1310.4,1350]
[3,"Тепловой","пол1",13,1,13,0.48,10,-36,287.04,{"$nulls":7},287.04]
[null,null,"пол2",13,1,13,0.23,10,-36,137.54000000000002,{"$nulls":7},137.54000000000002]
[null,null,"пол3",11,1,11,0.12,10,-36,60.71999999999999,{"$nulls":7},60.71999999999999]
[null,null,"пол4",6,1,6,0.07,10,-36,19.32,{"$nulls":7},19.32]
[{"$nulls":16},"ƩQ=",504.62,550]
[4,"техпомещения","пол1",60,1,60,0.48,10,-36,1324.8,{"$nulls":7},1324.8]
[null,null,"пол2",60,1,60,0.23,10,-36,634.8000000000001,{"$nulls":7},634.8000000000001]
[null,null,"пол3",47,1,47,0.12,10,-36,259.44,{"$nulls":7},259.44]
[null,null,"пол4",28,1,28,0.07,10,-36,90.16000000000001,{"$nulls":7},90.16000000000001]
[{"$nulls":16},"ƩQ=",2309.2,2350,5850]
["отм. или этаж: 0.000"]
[4,"гардероб","НС",4.5,3.3,14.85,0.17,19,-36,138.8475,"с",13.88475,{"$nulls":4},6.942375,159.674625]
[null,null,"НС",2.45,3.3,8.085,0.17,19,-36,75.59475,"з",7.559475000000001,{"$nulls":4},3.7797375000000004,86.9339625]
[null,null,"дверь",2.5,0.9,2.25,1.1,19,-36,136.125,"з",13.6125,{"$nulls":4},6.80625,156.54375000000002]
[null,null,"Перекрытие",7,1,7,0.18,19,10,11.34,{"$nulls":7},11.34]
[{"$nulls":16},"ƩQ=",414.4923375,450]
[5,"кухня-столовая","НС",6.6,3.3,21.779999999999998,0.17,19,-36,203.643,"з",20.3643,{"$nulls":4},10.18215,234.18945]
[null,null,"НС",4.1,3.3,13.529999999999998,0.17,19,-36,126.50549999999998,"ю",12.650549999999999,{"$nulls":4},6.3252749999999995,145.481325]
[null,null,"ОК",2.5,2.3,5.75,1.1,19,-36,347.875,"ю",34.7875,{"$nulls":4},17.39375,382.6625]
[null,null,"дверь",2.5,2.3,5.75,1.1,19,-36,347.875,"з",34.7875,{"$nulls":4},17.39375,400.05625000000003]
[null,null,"Перекрытие",24,1,24,0.18,19,10,38.88,{"$nulls":7},38.88]
[{"$nulls":16},"ƩQ=",1201.2695250000002,1250]
[6,"холл","НС",5,3.3,16.5,0.17,19,-36,154.275,"с",15.427500000000002,{"$nulls":4},7.713750000000001,177.41625000000002]
[null,null,"НС",1.5,3.3,4.949999999999999,0.17,19,-36,46.2825,"в",4.62825,{"$nulls":4},2.314125,53.224875]
[null,null,"ОК",1.7,0.9,1.53,1.1,19,-36,92.56500000000001,"в",9.2565,{"$nulls":4},4.62825,101.82150000000001]
[null,null,"Перекрытие",14,1,14,0.18,19,10,22.68,{"$nulls":7},22.68]
[{"$nulls":16},"ƩQ=",355.142625,400]
[8,"Гостинная","НС",3.5,3.3,11.549999999999999,0.17,21,-36,111.9195,"з",11.19195,{"$nulls":4},5.595975,128.707425]
[null,null,"НС",5,3.3,16.5,0.17,21,-36,159.88500000000002,"ю",{"$nulls":5},7.994250000000001,167.87925]
[null,null,"дверь",2.5,2.1,5.25,1.1,21,-36,329.175,"з",32.917500000000004,{"$nulls":4},16.458750000000002,362.09250000000003]
[null,null,"дверь",2.5,1.8,4.5,1.1,21,-36,282.15000000000003,"ю",{"$nulls":5},14.107500000000002,296.25750000000005]
[null,null,"Перекрытие",27,1,27,0.18,21,10,53.459999999999994,{"$nulls":7},53.459999999999994]
[{"$nulls":16},"ƩQ=",1008.3966750000001,1050]
[9,"Спальня","НС",4.5,3.3,14.85,0.17,21,-36,143.8965,"с",14.389650000000001,{"$nulls":4},7.194825000000001,165.480975]
[null,null,"НС",3.7,3.3,12.209999999999999,0.17,21,-36,118.3149,"в",11.83149,{"$nulls":4},5.915745,136.06213499999998]
[null,null,"ОК",1.7,1.3,2.21,1.1,21,-36,138.567,"в",13.856700000000002,{"$nulls":4},6.928350000000001,152.4237]
[null,null,"Перекрытие",13,1,13,0.18,21,10,25.74,{"$nulls":7},25.74]
[{"$nulls":16},"ƩQ=",479.70680999999996,500]
[10,"Кабинет","НС",3.4,3.3,11.219999999999999,0.17,21,-36,108.7218,"в",10.87218,{"$nulls":5},119.59398]
[null,null,"ОК",1.7,2.6,4.42,1.1,21,-36,277.134,"в",27.713400000000004,{"$nulls":5},304.8474]
[null,null,"Перекрытие",15,1,15,0.18,21,10,29.699999999999996,{"$nulls":7},29.699999999999996]
[{"$nulls":16},"ƩQ=",454.14137999999997,500]
["х","ЛК","НС",3.9,3.3,12.87,0.17,19,-36,120.33449999999999,"в",12.03345,{"$nulls":4},6.016725,138.384675]
[null,null,"НС",5,3.3,16.5,0.17,19,-36,154.275,"ю",{"$nulls":5},7.713750000000001,161.98875]
[null,null,"ОК",2.5,1.8,4.5,1.1,19,-36,272.25,"ю",{"$nulls":5},13.6125,272.25]
[null,null,"Перекрытие",20,1,20,0.18,19,10,32.4,{"$nulls":7},32.4]
[{"$nulls":16},"ƩQ=",605.023425,650,4800]
["отм. или этаж: 3.000"]
["х","лестничная клетка","НС",5.3,3.3,17.49,0.17,19,-36,163.5315,"в",16.35315,{"$nulls":4},8.176575,188.06122499999998]
[null,null,"НС",9.8,3.3,32.34,0.17,19,-36,302.379,"ю",{"$nulls":5},15.118950000000002,317.49795]
[null,null,"ОК",1.7,1.3,2.21,1.1,19,-36,133.705,"в",{"$nulls":5},6.685250000000001,133.705]
[null,null,"ОК",3.4,1.8,6.12,1.1,19,-36,370.26000000000005,"ю",{"$nulls":5},18.513,370.26000000000005]
[null,null,"Перекрытие",42,1,42,0.18,19,-36,415.79999999999995,{"$nulls":7},415.79999999999995]
[{"$nulls":16},"ƩQ=",1425.324175,1450]
[11,"гардероб","НС",3.6,3.3,11.879999999999999,0.17,19,-36,111.078,"в",11.107800000000001,{"$nulls":4},5.5539000000000005,127.7397]
[null,null,"НС",5.8,3.3,19.139999999999997,0.17,19,-36,178.95899999999997,"с",17.895899999999997,{"$nulls":4},8.947949999999999,205.80284999999998]
[null,null,"ОК",1.7,1.3,2.21,1.1,19,-36,133.705,"с",13.370500000000002,{"$nulls":4},6.685250000000001,147.0755]
[null,null,"Перекрытие",16,1,16,0.18,19,-36,158.4,{"$nulls":7},158.4]
[{"$nulls":16},"ƩQ=",639.01805,650]
[12,"спальня","НС",5.2,3.3,17.16,0.17,21,-36,166.28040000000001,"з",16.628040000000002,{"$nulls":4},8.314020000000001,191.22246]
[null,null,"НС",4,3.3,13.2,0.17,21,-36,127.90800000000002,"ю",{"$nulls":5},6.395400000000001,134.3034]
[null,null,"дверь",2.7,2.3,6.21,1.1,21,-36,389.367,"ю",{"$nulls":5},19.46835,389.367]
[null,null,"Перекрытие",18,1,18,0.18,21,-36,184.67999999999998,{"$nulls":7},184.67999999999998]
[{"$nulls":16},"ƩQ=",899.57286,900]
[15,"спальня","НС",3.4,3.3,11.219999999999999,0.17,21,-36,108.7218,"с",10.87218,{"$nulls":4},5.43609,125.03007]
[null,null,"НС",1.5,3.3,4.949999999999999,0.17,21,-36,47.96549999999999,"в",4.79655,{"$nulls":4},2.398275,55.160324999999986]
[null,null,"ОК",1.7,1.3,2.21,1.1,21,-36,138.567,"с",13.856700000000002,{"$nulls":4},6.928350000000001,152.4237]
[null,null,"Перекрытие",21,1,21,0.18,21,-36,215.45999999999998,{"$nulls":7},215.45999999999998]
[{"$nulls":16},"ƩQ=",548.0740949999999,550]
[16,"спальня","НС",4.5,3.3,14.85,0.17,21,-36,143.8965,"с",14.389650000000001,{"$nulls":4},7.194825000000001,165.480975]
[null,null,"НС",5.6,3.3,18.479999999999997,0.17,21,-36,179.07119999999998,"в",17.90712,{"$nulls":4},8.95356,205.93187999999998]
[null,null,"ОК",1.7,1.3,2.21,1.1,21,-36,138.567,"в",13.856700000000002,{"$nulls":4},6.928350000000001,152.4237]
[null,null,"Перекрытие",17,1,17,0.18,21,-36,174.42000000000002,{"$nulls":7},174.42000000000002]
[{"$nulls":16},"ƩQ=",698.2565549999999,700,4250]
[{"$nulls":19},14900]