{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Гидравл.расчет"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":0,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Гидравл.расчет","index":0,"n_rows":245,"n_cols":68,"rows_kept":245,"cut":false,"hidden":false,"merged":[[3,66,3,67],[3,58,3,59],[3,60,3,61],[3,62,3,63],[3,64,3,65],[3,8,3,9],[3,10,3,11],[3,12,3,13],[3,28,3,29],[3,38,3,39],[3,2,3,3],[3,4,3,5],[3,6,3,7],[3,22,3,23],[3,24,3,25],[3,26,3,27],[3,14,3,15],[3,16,3,17],[3,18,3,19],[3,20,3,21],[3,40,3,41],[3,42,3,43],[3,44,3,45],[3,30,3,31],[3,32,3,33],[3,34,3,35],[3,36,3,37],[3,54,3,55],[3,56,3,57],[3,46,3,47],[3,48,3,49],[3,50,3,51],[3,52,3,53]],"flags":["formulas_cached_only"]}
[null,null,"Таблица для гидравлического расчета трубопроводов"]
[]
[]
[null,"DнхS в мм","32х2,5",null,"38х2,5",null,"44,5х2,5",null,"45х2,5",null,"57х3,5",null,"76х3,5",null,"89х3,5",null,"108х4",null,"133х4",null,"152х4,5",null,"159х4,5",null,"194х6",null,"194х5",null,"219х7",null,"219х6",null,"273х8",null,"273х7",null,"325х8",null,"377х9",null,"426х10",null,"426х7",null,"426х6",null,"478Х7",null,"478х6",null,"529х7",null,"529х6",null,"630х8",null,"630х7",null,"720х9",null,"720х8",null,"720х7",null,"820х9",null,"820х8"]
[null,"G в т/ч","v в м/сек","∆h в кгс/м2м","v в м/сек","∆h в кгс/м2м","v в м/сек","∆h в кгс/м2м","v в м/сек","∆h в кгс/м2м","v в м/сек","∆h в кгс/м2м","v в м/сек","∆h в кгс/м2м","v в м/сек","∆h в кгс/м2м","v в м/сек","∆h в кгс/м2м","v в м/сек","∆h в кгс/м2м","v в м/сек","∆h в кгс/м2м","v в м/сек","∆h в кгс/м2м","v в м/сек","∆h в кгс/м2м","v в м/сек","∆h в кгс/м2м","v в м/сек","∆h в кгс/м2м","v в м/сек","∆h в кгс/м2м","v в м/сек","∆h в кгс/м2м","v в м/сек","∆h в кгс/м2м","v в м/сек","∆h в кгс/м2м","v в м/сек","∆h в кгс/м2м","v в м/сек","∆h в кгс/м2м","v в м/сек","∆h в кгс/м2м","v в м/сек","∆h в кгс/м2м","v в м/сек","∆h в кгс/м2м","v в м/сек","∆h в кгс/м2м","v в м/сек","∆h в кгс/м2м","v в м/сек","∆h в кгс/м2м","v в м/сек","∆h в кгс/м2м","v в м/сек","∆h в кгс/м2м","v в м/сек","∆h в кгс/м2м","v в м/сек","∆h в кгс/м2м","v в м/сек","∆h в кгс/м2м","v в м/сек","∆h в кгс/м2м","v в м/сек","∆h в кгс/м2м"]
[null,0.2,0.1,0.95]
[null,0.22,0.11,1.14]
[null,0.24,0.17,1.35]
[null,0.26,0.13,1.59]
[null,0.28,0.14,1.82]
[null,0.3,0.15,2.08,0.1,0.72]
[null,0.32,0.16,2.37,0.11,0.81]
[null,0.34,0.17,2.71,0.12,0.92]
[null,0.36,0.18,2.97,0.12,1.03]
[null,0.38,0.19,3.3,0.13,1.15]
[null,0.4,0.2,3.65,0.14,1.26]
[null,0.42,0.21,4,0.14,1.37]
[null,0.44,0.22,4.38,0.15,1.52,0.1,0.59,0.1,0.55]
[null,0.46,0.23,4.75,0.16,1.66,0.11,0.64,0.11,0.6]
[null,0.48,0.24,5.15,0.16,1.82,0.12,0.69,0.11,0.65]
[null,0.5,0.25,5.55,0.17,1.95,0.12,0.76,0.12,0.7]
[null,0.55,0.28,6.66,0.19,2.35,0.13,0.91,0.13,0.85]
[null,0.6,0.3,7.85,0.2,2.8,0.14,1.07,0.14,1.01]
[null,0.65,0.33,8.19,0.22,3.26,0.15,1.27,0.15,1.18]
[null,0.7,0.35,10.7,0.24,3.77,0.17,1.46,0.16,1.37,0.1,0.44]
[null,0.75,0.38,12.3,0.25,4.31,0.18,1.67,0.17,1.57,0.11,0.5]
[null,0.8,0.41,14,0.27,4.86,0.19,1.9,0.18,1.77,0.12,0.57]
[null,0.85,0.43,15.8,0.29,5.45,0.2,2.13,0.2,2,0.13,0.65]
[null,0.9,0.46,17.7,0.31,6.08,0.21,2.38,0.21,2.2,0.13,0.72]
[null,0.95,0.48,19.7,0.32,6.73,0.22,2.64,0.22,2.48,0.14,0.8]
[null,1,0.51,21.9,0.34,7.45,0.24,2.91,0.23,2.72,0.15,0.88]
[null,1.05,0.53,24.1,0.36,8.21,0.25,3.2,0.24,2.99,0.16,1.07]
[null,1.1,0.56,26.5,0.37,9.01,0.26,3.5,0.25,3.29,0.16,1.05]
[null,1.15,0.58,28.9,0.39,9.85,0.27,3.82,0.27,3.58,0.17,1.14]
[null,1.2,0.61,32,0.41,10.7,0.28,4.15,0.28,3.87,0.18,1.24]
[null,1.25,0.63,34.2,0.42,11.6,0.3,4.48,0.29,4.2,0.18,1.34]
[null,1.3,0.66,37,0.44,12.6,0.31,4.83,0.3,4.51,0.19,1.44,0.1,0.27]
[null,1.35,0.68,39.9,0.46,13.6,0.32,4.18,0.31,4.86,0.2,1.55,0.1,0.29]
[null,1.4,0.71,42.9,0.47,14.6,0.33,5.57,0.32,5.21,0.21,1.67,0.11,0.31]
[null,1.45,0.73,46,0.49,15.7,0.34,5.98,0.33,5.59,0.21,1.78,0.11,0.33]
[null,1.5,0.76,49.2,0.51,16.8,0.36,6.4,0.35,5.98,0.22,1.91,0.12,0.36]
[null,1.55,0.79,52.6,0.53,17.9,0.37,6.83,0.36,6.38,0.23,2.02,0.12,0.38]
[null,1.6,0.81,56,0.54,19.1,0.38,7.28,0.37,6.8,0.24,2.14,0.12,0.4]
[null,1.65,0.84,59.6,0.56,20.3,0.39,7.74,0.38,7.23,0.24,2.26,0.13,0.43]
[null,1.7,0.86,63.2,0.58,21.5,0.4,8.2,0.39,7.68,0.25,2.4,0.13,0.46]
[null,1.75,0.89,67,0.59,22.8,0.41,8.7,0.4,8.14,0.26,2.53,0.14,0.48]
[null,1.8,0.91,79,0.61,24.1,0.43,9.21,0.42,8.61,0.27,2.66,0.14,0.51]
[null,1.85,0.94,74.9,0.63,25.5,0.44,9.73,0.43,9.09,0.27,2.81,0.14,0.53]
[null,1.9,0.96,79,0.64,26.9,0.45,10.3,0.44,9.59,0.28,2.96,0.15,0.56]
[null,1.95,0.99,83.2,0.66,28.3,0.46,10.8,0.45,10.1,0.29,3.1,0.15,0.59]
[null,2,1.01,87.5,0.68,29.8,0.47,11.4,0.46,10.6,0.3,3.25,0.16,0.62]
[null,2.1,1.06,96.5,0.71,32.8,0.5,12.5,0.48,11.7,0.31,3.55,0.16,0.68]
[null,2.2,1.11,105.9,75,36,0.52,13.8,0.51,12.9,0.33,3.69,0.17,0.75]
[null,2.3,null,null,0.78,39.4,0.54,15,0.53,14.1,0.34,4.27,0.18,0.81]
[null,2.4,null,null,0.81,42.1,0.57,16.4,0.55,15.3,0.35,4.64,0.19,0.88]
[null,2.5,null,null,0.85,46.5,0.59,17.8,0.58,16.6,0.37,5.04,0.19,0.96]
[null,2.6,null,null,0.88,53,0.62,19.2,0.6,18,0.38,5.45,0.2,1.03]
[null,2.7,null,null,0.92,54.3,0.64,20.7,0.62,19.4,0.4,5.88,0.21,1.1]
[null,2.8,null,null,0.95,58.4,0.66,22.3,0.65,20.8,0.41,6.32,0.22,1.15]
[null,2.9,null,null,0.98,62.6,0.69,23.9,0.67,22.3,0.43,6.78,0.22,1.25]
[null,3,null,null,1.02,67,0.71,25.6,0.69,23.9,0.44,7.26,0.23,1.35]
[null,3.1,null,null,1.05,71.6,0.74,27.3,0.72,25.5,0.46,7.75,0.24,1.45]
[null,3.2,null,null,1.09,76.3,0.76,29.1,0.74,27.2,0.47,8.26,0.25,1.53]
[null,3.3,null,null,1.12,81.1,0.78,31,0.76,28.9,0.49,8.78,0.26,1.62]
[null,3.4,null,null,1.15,86.1,0.8,32.9,0.78,30.7,0.5,9.32,0.26,1.73]
[null,3.5,{"$nulls":4},0.83,34.8,0.81,32.6,0.52,9.88,0.27,1.82,0.19,0.71,0.13,0.27]
[null,3.6,{"$nulls":4},0.85,36.8,0.83,34.4,0.53,10.4,0.28,1.92,0.2,0.75,0.13,0.28]
[null,3.7,{"$nulls":4},0.88,38.9,0.85,36.4,0.55,11,0.29,2.02,0.2,0.79,0.14,0.29]
[null,3.8,{"$nulls":4},0.9,41,0.88,38.4,0.56,11.6,0.29,2.13,0.21,0.83,0.14,0.31]
[null,3.9,{"$nulls":4},0.92,43.2,0.9,40.4,0.58,12.3,0.3,2.22,0.21,0.88,0.14,0.33]
[null,4,{"$nulls":4},0.95,45.5,0.92,42.5,0.59,12.9,0.31,2.33,0.22,0.92,0.15,0.34]
[null,4.2,{"$nulls":4},0.99,50.1,0.97,46.9,0.62,14.2,0.33,2.48,0.23,1.01,0.16,0.38]
[null,4.4,{"$nulls":4},1.04,55,1.02,51.4,0.65,15.6,0.34,2.81,0.24,1.11,0.16,0.41,0.1,0.13]
[null,4.6,{"$nulls":4},1.09,60.1,1.06,56.2,0.68,17.1,0.36,3.07,0.25,1.21,0.17,0.45,0.11,0.14]
[null,4.8,{"$nulls":4},1.14,65.5,1.11,61.2,0.71,18.6,0.37,3.34,0.26,1.31,0.18,0.49,0.11,0.15]
[null,5,{"$nulls":4},1.18,71.1,1.15,66.4,0.74,20.2,0.39,3.62,0.27,1.43,0.18,0.53,0.12,0.17]
[null,5.2,{"$nulls":4},1.23,76.9,1.2,71.9,0.77,21.8,0.4,3.92,0.29,1.54,0.19,0.57,0.12,0.18]
[null,5.4,{"$nulls":4},1.28,82.9,1.25,77.5,0.8,23.5,0.42,4.23,0.3,1.66,0.2,0.61,0.13,0.19]
[null,5.6,{"$nulls":4},1.33,89.1,1.29,83.3,0.83,25.7,0.43,4.54,0.31,1.78,0.21,0.65,0.13,0.2]
[null,5.8,{"$nulls":4},1.37,95.6,1.34,89.4,0.86,27.1,0.45,4.87,0.32,1.91,0.21,0.7,0.14,0.22]
[null,6,{"$nulls":4},1.42,102.3,1.39,95.7,0.89,29,0.47,5.22,0.33,2.04,0.22,0.75,0.14,0.23]
[null,6.2,{"$nulls":6},1.43,102.1,0.92,31,0.48,5.57,0.34,2.22,0.23,0.8,0.15,0.25]
[null,6.4,{"$nulls":8},0.95,33,0.5,5.94,0.35,2.37,0.24,0.85,0.15,0.26]
[null,6.6,{"$nulls":8},0.98,35.1,0.51,6.31,0.36,2.52,0.24,0.9,0.16,0.8]
[null,6.8,{"$nulls":8},1,37.3,0.53,6.7,0.37,2.68,0.25,0.95,0.16,0.31]
[null,7,{"$nulls":8},1.03,39.5,0.54,7.1,0.38,2.84,0.26,1.01,0.17,0.32]
[null,7.5,{"$nulls":8},1.11,45.4,0.58,8.15,41,3.26,0.28,1.15,0.18,0.7]
[null,8,{"$nulls":8},1.18,51.6,0.62,9.27,0.44,3.7,0.3,1.3,0.19,0.42]
[null,8.5,{"$nulls":8},1.26,58.3,0.66,10.5,0.47,4.18,0.31,1.46,0.2,0.47]
[null,9,{"$nulls":8},1.33,65.3,0.7,11.7,0.49,4.69,0.33,1.64,0.21,0.52]
[null,9.5,{"$nulls":8},1.4,72.8,0.74,13.1,0.52,5.22,0.35,1.82,0.22,0.58]
[null,10,{"$nulls":8},1.48,80.6,0.78,14.5,0.55,5.79,0.37,2.02,0.24,0.64]
[null,10.5,{"$nulls":8},1.55,88.9,0.81,16,0.58,6.38,0.39,2.22,0.25,0.7]
[null,11,{"$nulls":8},1.63,97.6,0.85,17.5,0.6,7,0.41,2.44,0.26,0.77]
[null,11.5,{"$nulls":8},1.7,106.6,0.89,19.2,0.63,7.65,0.42,2.67,0.27,0.84]
[null,12,{"$nulls":10},0.93,20.9,0.66,8.33,0.44,2.91,0.28,0.9,0.22,0.46,0.2,0.36]
[null,12.5,{"$nulls":10},0.97,22.6,0.69,9.04,0.46,3.15,0.3,0.98,0.23,0.49,0.21,0.39]
[null,13,{"$nulls":10},1.08,24.5,0.71,9.78,0.48,3.41,0.31,1.06,0.23,0.53,0.21,0.42]
[null,13.5,{"$nulls":10},1.05,26.4,0.74,10.5,0.5,3.68,0.32,1.13,0.24,0.57,0.22,0.45]
[null,14,{"$nulls":10},1.09,28.4,0.77,11.3,0.52,3.96,0.33,1.21,0.25,0.61,0.23,0.48]
[null,14.5,{"$nulls":10},1.12,30.5,0.8,12.2,0.54,4.24,0.34,1.3,0.26,0.66,0.24,0.51]
[null,15,{"$nulls":10},1.16,32.5,0.82,13,0.55,4.54,0.35,1.39,0.27,0.69,0.25,0.55,0.17,0.2,0.16,0.19]
[null,15,{"$nulls":10},1.24,37.1,0.88,14.8,0.59,5.17,0.38,1.58,0.29,0.79,0.26,0.62,0.18,0.23,0.17,0.21]
[null,17,{"$nulls":10},1.32,41.9,0.93,16.7,0.63,5.83,0.4,1.79,0.31,0.88,0.28,0.69,0.19,0.26,0.19,0.24]
[null,18,{"$nulls":10},1.4,46.9,0.99,18.8,0.66,6.54,0.43,2.01,0.33,0.99,0.3,0.77,0.2,0.29,0.2,0.27]
[null,19,{"$nulls":10},1.47,52.3,1.04,20.9,0.7,7.29,0.45,2.23,0.34,1.1,0.31,0.85,0.21,0.32,0.21,0.3]
[null,20,{"$nulls":10},1.55,58,1.1,23.2,0.74,8.08,0.47,2.48,0.36,1.22,0.33,0.95,0.22,0.35,0.22,0.33]
[null,21,{"$nulls":10},1.63,63.9,1.15,25.5,0.78,8.9,0.5,2.73,0.38,1.34,0.34,1.04,0.23,0.39,0.23,0.36]
[null,22,{"$nulls":10},1.71,70.1,1.21,28,0.81,9.77,0.52,3,0.4,1.47,0.36,1.14,0.25,0.42,0.24,0.4]
[null,23,{"$nulls":10},1.78,76.7,1.26,30.6,0.85,10.7,0.54,3.27,0.42,1.61,0.38,1.25,0.26,0.46,0.25,0.43]
[null,24,{"$nulls":10},1.86,83.5,1.32,33.3,0.89,11.6,0.57,3.57,0.43,1.75,0.39,1.36,0.27,0.5,0.26,0.48]
[null,25,{"$nulls":10},1.94,90.6,1.37,36.2,0.92,12.6,0.59,3.87,0.45,1.9,0.41,1.47,0.28,0.54,0.27,0.51]
[null,26,{"$nulls":10},2.02,98,1.43,39.1,0.96,13.6,0.62,4.19,0.47,2.05,0.43,1.6,0.29,0.59,0.28,0.55]
[null,27,{"$nulls":10},2.09,105.6,1.48,42.2,1,14.7,0.64,4.51,0.49,2.22,0.44,1.72,0.3,0.63,0.29,0.59]
[null,28,{"$nulls":12},1.54,45.4,1.03,15.8,0.66,4.85,0.51,2.38,0.46,1.85,0.31,0.68,0.31,0.64]
[null,29,{"$nulls":12},1.59,48.7,1.07,17,0.69,5.21,0.52,2.56,0.48,1.99,0.32,0.72,0.32,0.68]
[null,30,{"$nulls":12},1.65,52.1,1.11,18.2,0.71,5.57,0.54,2.73,0.49,2.12,0.33,0.77,0.33,0.73]
[null,31,{"$nulls":12},1.7,55.6,1.15,19.4,0.73,5.95,0.56,2.92,0.51,2.27,0.35,0.82,0.34,0.77]
[null,32,{"$nulls":12},1.76,59.3,1.18,20.7,0.76,6.34,0.58,3.11,0.53,2.42,0.36,0.87,0.35,0.82]
[null,33,{"$nulls":12},1.81,63,1.22,22,0.78,6.74,0.6,3.31,0.54,2.57,0.37,0.93,0.36,0.87]
[null,34,{"$nulls":12},1.87,66.9,1.26,23.3,0.8,7.16,0.61,3.51,0.56,2.73,0.38,0.98,0.37,0.93]
[null,35,{"$nulls":12},1.92,70.9,1.29,24.7,0.83,7.58,0.63,3.72,0.57,2.89,0.39,1.04,0.38,0.98]
[null,36,{"$nulls":12},1.98,75,1.33,26.2,0.85,8.02,0.65,3.94,0.59,3.06,0.4,1.1,0.39,1.04]
[null,37,{"$nulls":12},2.03,79.2,1.37,27.6,0.87,8.48,0.67,4.16,0.61,3.23,0.41,1.16,0.4,1.1]
[null,38,{"$nulls":12},2.09,83.6,1.4,29.2,0.9,8.94,0.69,4.39,0.62,3.41,0.42,1.23,0.41,1.16]
[null,39,{"$nulls":14},1.44,30.7,0.92,9.42,0.7,4.62,0.64,3.59,0.43,1.29,0.43,1.22,0.34,0.69,0.34,0.66,0.22,0.22,0.21,0.22]
[null,40,{"$nulls":14},1.48,32.3,0.95,9.91,0.72,4.86,0.66,3.78,0.45,1.36,0.44,1.28,0.35,0.73,0.35,0.69,0.22,0.23,0.22,0.23]
[null,41,{"$nulls":14},1.51,33.9,0.97,10.4,0.74,5.11,0.67,3.97,0.46,1.43,0.45,1.35,0.36,0.76,0.35,0.72,0.23,0.24,0.23,0.24]
[null,42,{"$nulls":14},1.55,35.6,0.99,10.9,0.76,5.36,0.69,4.16,0.47,1.5,0.46,1.42,0.37,0.8,0.36,0.76,0.23,0.26,0.23,0.25]
[null,43,{"$nulls":14},1.59,37.3,1.02,11.4,0.78,5.62,0.71,4.36,0.48,1.57,0.47,1.48,0.38,0.84,0.37,0.8,0.24,0.27,0.24,0.26]
[null,44,{"$nulls":14},1.63,39.1,1.04,12,0.79,5.88,0.72,4.57,0.49,1.65,0.48,1.55,0.39,0.88,0.38,0.83,0.25,0.28,0.24,0.27]
[null,45,{"$nulls":14},1.66,40.9,1.06,12.5,0.81,6.15,0.74,4.78,0.5,1.72,0.49,1.62,0.4,0.92,0.39,0.87,0.25,0.29,0.25,0.29]
[null,46,{"$nulls":14},1.7,42.7,1.09,13.1,0.83,6.43,0.76,4.99,0.51,1.8,0.5,1.7,0.4,0.96,0.4,0.91,0.26,0.3,0.25,0.3]
[null,47,{"$nulls":14},1.74,44.6,1.11,13.7,0.85,6.71,0.77,5.21,0.52,1.88,0.51,1.77,0.41,1,0.41,0.95,0.26,0.32,0.26,0.31]
[null,48,{"$nulls":14},1.77,46.5,1.13,14.3,0.87,7,0.79,5.44,0.54,1.96,0.52,1.85,0.42,1.05,0.41,0.99,0.27,0.33,0.26,0.32]
[null,49,{"$nulls":14},1.81,48.5,1.16,14.9,0.89,7.3,0.8,5.67,0.55,2.04,0.53,1.93,0.43,1.09,0.42,1.04,0.27,0.34,0.27,0.34]
[null,50,{"$nulls":14},1.85,50.5,1.18,15.5,0.9,7.6,0.82,5.9,0.56,2.13,0.55,2.01,0.44,1.13,0.43,1.08,0.28,0.36,0.28,0.35]
[null,52,{"$nulls":14},1.92,54.6,1.23,16.7,0.94,8.22,0.85,6.38,0.58,2.3,0.57,2.17,0.46,1.23,0.45,1.17,0.29,0.38,0.29,0.38]
[null,54,{"$nulls":14},1.99,58.9,1.28,18.1,0.98,8.86,0.89,6.88,0.6,2.48,0.59,2.34,0.47,1.32,0.47,1.26,0.3,0.41,0.3,0.41]
[null,56,{"$nulls":14},2.07,63.3,1.32,19.4,1.01,9.53,0.92,7.4,0.62,2.67,0.61,2.52,0.49,1.42,0.48,1.35,0.31,0.44,0.31,0.44]
[null,58,{"$nulls":14},2.14,67.9,1.37,20.8,1.05,10.2,0.95,7.94,0.65,2.86,0.63,2.7,0.51,1.53,0.5,1.45,0.32,0.47,0.32,0.46]
[null,60,{"$nulls":14},2.22,72.7,1.42,22.3,1.08,10.9,0.98,8.5,0.67,3.06,0.65,2.89,0.53,1.63,0.52,1.55,0.34,0.5,0.33,0.49]
[null,62,{"$nulls":14},2.29,77.6,1.47,23.8,1.72,11.7,1.02,9.07,0.69,3.27,0.68,3.08,0.54,1.74,0.53,1.66,0.35,0.53,0.34,0.51]
[null,64,{"$nulls":14},2.36,82.7,1.51,25.4,1.15,12.4,1.05,9.67,0.71,3.48,0.7,3.29,0.56,1.86,0.55,1.77,0.36,0.56,0.35,0.54]
[null,66,{"$nulls":14},2.44,87.9,1.56,27,1.19,13.2,1.08,10.3,0.74,3.7,0.72,3.5,0.58,1.98,0.57,1.88,0.37,0.6,0.36,0.58]
[null,68,{"$nulls":14},2.51,93.4,1.61,28.6,1.23,14.1,1.12,10.9,0.76,3.93,0.74,3.71,0.6,2.1,0.59,1.99,0.38,0.64,0.37,0.61]
[null,70,{"$nulls":14},2.59,98.9,1.65,30.3,1.26,14.9,1.15,11.6,0.78,4.17,0.76,3.93,0.61,2.22,0.6,2.11,0.39,0.68,0.39,0.65]
[null,72,{"$nulls":14},2.66,104.7,1.7,32.1,1.3,15.8,1.18,12.2,0.8,4.41,0.79,4.16,0.63,2.35,0.62,2.23,0.4,0.71,0.4,0.69]
[null,74,{"$nulls":16},1.75,33.9,1.34,16.6,1.21,12.9,0.83,4.66,0.81,4.39,0.65,2.48,0.64,2.36,0.41,0.76,0.41,0.72]
[null,76,{"$nulls":16},1.8,35.8,1.37,17.6,1.25,13.6,0.85,4.91,0.83,4.63,0.67,2.62,0.66,2.49,0.43,0.8,0.42,0.76]
[null,78,{"$nulls":16},1.84,37.7,1.41,18.5,1.28,14.4,0.85,5.17,0.85,4.88,0.69,2.76,0.67,2.62,0.44,0.84,0.43,0.81]
[null,80,{"$nulls":16},1.89,39.6,1.45,19.4,1.31,15.1,0.89,5.44,0.87,5.14,0.7,2.9,0.69,2.76,0.45,0.88,0.44,0.85]
[null,85,{"$nulls":16},2.01,44.7,1.54,22,1.4,17.1,0.95,6.14,0.93,5.8,0.75,3.28,0.73,3.11,0.48,1,0.47,0.96]
[null,90,{"$nulls":16},2.13,50.1,1.63,24.6,1.48,19.1,1,6.89,0.98,6.5,0.79,3.68,0.78,3.49,0.5,1.12,0.5,1.07]
[null,95,{"$nulls":16},2.25,55.9,1.72,27.4,1.56,21.3,1.06,7.67,1.04,7.24,0.83,4.1,0.82,3.89,0.53,1.24,0.52,1.19]
[null,100,{"$nulls":16},2.36,61.9,1.81,30.4,1.64,23.6,1.12,8.5,1.09,8.02,0.88,4.54,0.86,4.31,0.56,1.38,0.55,1.32,0.39,0.52,0.29,0.25,0.22,0.13,0.22,0.12,0.22,0.12]
[null,105,{"$nulls":16},2.48,68.3,1.9,33.5,1.72,26,1.17,9.37,1.15,8.85,0.92,5,0.91,4.75,0.59,1.52,0.58,1.46,0.41,0.58,0.3,0.27,0.24,0.14,0.23,0.13,0.23,0.13]
[null,110,{"$nulls":16},2.6,74.9,1.99,36.8,1.81,28.6,1.23,10.3,1.2,9.71,0.97,5.59,0.95,5.22,0.62,1.67,0.61,1.6,0.43,0.63,0.32,0.3,0.25,0.16,0.24,0.13,0.24,0.14]
[null,115,{"$nulls":16},2.72,81.9,2.08,40.2,1.89,31.2,1.28,11.2,1.25,10.6,1.01,6,0.99,5.7,0.64,1.82,0.63,1.75,0.44,0.69,0.33,0.32,0.26,0.17,0.25,0.16,0.25,0.15]
[null,120,{"$nulls":16},2.84,89.1,2.17,43.8,1.97,34,1.34,12.2,1.31,11.6,1.05,6.53,1.03,6.21,0.67,1.99,0.66,1.91,0.46,0.75,0.34,0.34,0.27,0.19,0.26,0.17,0.26,0.17]
[null,125,{"$nulls":16},2.95,9607,2.26,47.5,2.05,36.9,1.39,13.3,1.36,12.5,1.1,7.09,1.08,6.74,0.7,2.15,0.69,2.07,0.48,0.82,0.36,0.37,0.28,0.2,0.27,0.19,0.27,0.18]
[null,130,{"$nulls":16},3.07,104.6,2.35,51.4,2.13,39.9,1.45,14.4,1.42,13.6,1.14,7.67,1.12,7.29,0.73,2.33,0.72,2.24,0.5,0.88,0.37,0.4,0.29,0.22,0.28,0.2,0.28,0.2]
[null,135,{"$nulls":18},2.44,55.4,2.22,43,1.51,15.5,1.47,14.6,1.19,8.27,1.16,7.86,0.75,2.51,0.74,2.41,0.52,0.95,0.39,0.43,0.3,0.23,0.29,0.22,0.29,0.21]
[null,140,{"$nulls":18},2.53,59.6,2.3,46.3,1.56,16.7,1.53,15.7,1.23,8.89,1.21,8.45,0.78,2.7,0.77,2.59,0.54,1.03,0.4,0.47,0.31,0.25,0.3,0.23,0.3,0.23]
[null,145,{"$nulls":18},2.62,63.9,2.38,49.6,1.62,17.9,1.58,16.9,1.27,9.54,1.25,9.06,0.81,2.9,0.8,2.78,0.56,1.1,0.42,0.5,0.32,0.27,0.32,0.25,0.31,0.24]
[null,150,{"$nulls":18},2.71,68.4,2.46,53.1,1.67,19.1,1.64,18.1,1.32,10.2,1.29,9.7,0.84,3.1,0.83,2.98,0.58,1.18,0.43,0.53,0.34,0.28,0.33,0.27,0.32,0.26]
[null,155,{"$nulls":18},2.8,73,2.54,56.7,1.73,20.4,1.69,19.3,1.36,10.9,1.34,10.4,0.87,3.31,0.85,3.18,0.6,1.26,0.44,0.57,0.35,0.3,0.34,0.28,0.33,0.27]
[null,160,{"$nulls":18},2.89,77.8,2.63,60.4,1.78,21.8,1.75,20.5,1.41,11.6,1.38,11,0.89,3.53,0.88,3.39,0.62,1.34,0.46,0.61,0.36,0.32,0.35,0.3,0.34,0.29]
[null,165,{"$nulls":18},2.98,82.7,2.71,64.3,1.84,23.1,1.8,21.8,1.45,12.3,1.42,11.7,0.92,3.75,0.91,3.6,0.64,1.42,0.47,0.65,0.37,0.34,0.36,0.31,0.36,0.31]
[null,170,{"$nulls":18},3.07,87.8,2.79,68.2,1.9,24.6,1.85,23.2,1.49,13.1,1.47,12.5,0.95,3.99,0.94,3.83,0.66,1.51,0.49,0.69,0.38,0.36,0.37,0.33,0.37,0.33]
[null,175,{"$nulls":18},3.16,93.1,2.87,72.3,1.95,26,1.91,24.6,1.54,13.9,1.51,13.2,0.98,4.22,0.96,4.05,0.68,1.6,0.5,0.73,0.39,0.38,0.38,0.35,0.38,0.34]
[null,180,{"$nulls":22},2.01,27.5,1.96,26,1.58,14.7,1.55,14,1.01,4.47,0.99,4.29,0.7,1.69,0.52,0.77,0.4,0.4,0.39,0.37,0.39,0.36]
[null,190,{"$nulls":22},2.12,30.7,2.07,29,1.67,16.4,1.64,15.6,1.06,4.98,1.05,4.78,0.74,1.89,0.54,0.86,0.43,0.45,0.41,0.42,0.41,0.41]
[null,200,{"$nulls":22},2.23,34,2.18,32.1,1.76,18.2,1.72,17.2,1.12,5.52,1.1,5.3,0.77,2.09,0.57,0.95,0.45,0.5,0.44,0.46,0.43,0.45]
[null,210,{"$nulls":22},2.34,37.5,2.29,35.4,1.85,20,1.81,19,1.17,6.08,1.16,5.84,0.81,2.31,0.6,1.05,0.47,0.55,0.46,0.51,0.45,0.5]
[null,220,{"$nulls":22},2.45,41.1,2.4,38.8,1.93,22,1.9,"20,,9",1.23,6.67,1.21,6.41,0.85,2.53,0.63,1.15,0.49,0.6,0.48,0.56,0.47,0.54]
[null,230,{"$nulls":22},2.56,45,2.51,42.4,2.02,24,1.98,22.8,1.29,7.29,1.27,7,0.89,2.77,0.66,1.26,0.51,0.66,0.5,0.61,0.5,0.59]
[null,240,{"$nulls":22},2.68,49,2.62,46.2,2.11,26.1,2.07,24.8,1.34,7.94,1.32,7.63,0.93,3.01,0.69,1.37,0.54,0.72,0.52,0.66,0.52,0.65]
[null,250,{"$nulls":22},2.79,53.1,2.73,50.2,2.2,28.4,2.16,26.9,1.4,8.62,1.38,8.27,0.97,3.27,0.72,1.49,0.56,0.78,0.54,0.72,0.54,0.7]
[null,260,{"$nulls":22},2.9,57.5,2.84,54.2,2.29,30.7,2.24,29.1,1.45,9.32,1.43,8.95,1.01,3.54,0.75,1.61,0.58,0.84,0.57,0.78,0.56,0.76]
[null,270,{"$nulls":22},3.01,62,2.95,58.5,2.37,33.1,2.33,31.4,1.51,10.1,1.49,9.65,1.04,3.81,0.77,1.73,0.61,0.91,0.59,0.84,0.58,0.82]
[null,280,{"$nulls":22},3.12,66.6,3.05,62.9,2.46,35.6,2.41,33.8,1.57,10.8,1.54,10.4,1.08,4.1,0.8,1.86,0.63,0.98,0.61,0.9,0.6,0.88]
[null,290,{"$nulls":22},3.23,71.5,3.16,67.5,2.55,38.2,2.5,36.3,1.62,11.6,1.6,11.1,1.12,4.4,0.83,2,0.65,1.05,0.63,0.97,0.62,0.95]
[null,300,{"$nulls":22},3.35,76.5,3.27,72.2,2.64,40.8,2.59,38.8,2.68,12.4,1.65,11.9,1.16,4.71,0.86,2.14,0.67,1.12,0.65,1.04,0.65,1.01]
[null,310,{"$nulls":22},3.46,81.7,3.38,77.1,2.72,43.6,2.67,41.4,1.73,13.3,1.71,12.7,1.2,5.03,0.89,2.28,0.69,1.2,0.67,1.11,0.67,1.08]
[null,320,{"$nulls":26},2.81,46.5,2.76,44.1,1.79,14.1,1.76,13.6,1.24,5.36,0.92,2.43,0.72,1.28,0.7,1.18,0.69,1.15,0.55,0.63,0.54,0.62,0.45,0.37,0.44,0.36]
[null,330,{"$nulls":26},2.9,49.4,2.84,46.9,1.85,15,1.82,14.4,1.28,5.7,0.95,2.59,0.74,1.36,0.72,1.26,0.71,1.22,0.57,0.67,0.56,0.66,0.46,0.39,0.46,0.38]
[null,340,{"$nulls":26},2.99,52.5,2.93,49.8,1.9,15.9,1.87,15.3,1.32,6.05,0.97,2.75,0.76,1.44,0.74,1.33,0.73,1.3,0.58,0.71,0.58,0.7,0.47,0.41,0.47,0.41]
[null,350,{"$nulls":26},3.08,55.6,3.02,52.8,1.96,16.9,1.93,16.2,1.35,6.41,1,2.91,0.78,1.53,0.76,1.41,0.75,1.38,0.6,0.76,0.6,0.74,0.79,0.44,0.48,0.43]
[null,360,{"$nulls":26},3.16,58.8,3.1,55.9,2.01,17.9,1.98,17.2,1.39,6.78,1.03,3.08,0.81,1.61,0.78,1.5,0.78,1.46,0.62,0.8,0.61,0.78,0.5,0.46,0.5,0.45]
[null,370,{"$nulls":26},3.25,62.1,3.19,59,2.07,18.9,2.04,18.1,1.43,7.16,1.06,3.25,0.83,1.71,0.81,1.58,0.8,1.54,0.63,0.85,0.63,0.83,0.52,0.49,0.51,0.48]
[null,380,{"$nulls":26},3.34,65.5,3.28,62.3,2.13,19.9,2.09,19.1,1.47,7.55,1.09,3.43,0.85,1.8,0.83,1.67,0.82,1.62,0.65,0.89,0.65,0.87,0.53,0.52,0.53,0.51]
[null,390,{"$nulls":26},3.43,69,3.36,65.6,2.18,21,2.15,20.1,1.51,7.95,1.12,3.62,0.87,1.9,0.85,1.75,0.84,1.71,0.67,0.94,0.66,0.92,0.54,0.54,0.54,0.54]
[null,400,{"$nulls":26},3.52,72.6,3.45,69,2.24,22,2.2,21.2,1.55,8.37,1.15,3.8,0.9,1.99,0.87,1.85,0.86,1.8,0.69,0.99,0.68,0.97,0.56,0.57,0.55,0.56]
[null,410,{"$nulls":26},3.6,76.3,3.53,72.5,2.29,23.2,2.26,22.2,1.59,8.79,1.18,4,0.92,2.09,0.89,1.94,0.88,1.89,0.7,1.04,0.7,1.02,0.57,0.6,0.57,0.59]
[null,420,{"$nulls":26},3.69,80,3.62,76,2.35,24.3,2.31,23.4,1.62,9.23,1.2,4.19,0.94,2.2,0.91,2.04,0.91,1.98,0.72,1.09,0.71,1.07,0.58,0.63,0.58,0.62]
[null,430,{"$nulls":26},3.78,83.9,3.71,79.7,2.4,25.5,2.37,24.5,1.66,9.67,1.23,4.4,0.96,2.3,0.94,2.13,0.93,2.08,0.74,1.14,0.73,1.12,0.6,0.66,0.59,0.65]
[null,440,{"$nulls":26},3.87,87.8,3.79,83.5,2.46,26.7,2.42,25.6,1.7,10.1,1.26,4.6,0.99,2.41,0.96,2.23,0.95,2.18,0.75,1.2,0.75,1.17,0.61,0.69,0.61,0.68]
[null,450,{"$nulls":26},3.96,91.9,3.88,87.3,2.52,27.9,2.48,26.8,1.74,10.6,1.29,4.81,1.01,2.52,0.98,2.34,0.97,2.28,0.77,1.25,0.77,1.22,0.63,0.72,0.62,0.71]
[null,460,{"$nulls":26},4.04,96,3.97,91.2,2.57,29.2,2.53,28,1.78,11.1,1.32,5.03,1.03,2.64,1,2.44,0.99,2.38,0.79,1.31,0.78,1.28,0.64,0.76,0.64,0.74]
[null,470,{"$nulls":26},4.13,100.2,4.05,95.2,2.63,30.5,2.59,29.2,1.82,11.6,1.35,5.25,1.05,2.75,1.02,2.55,1.01,2.48,0.81,1.37,0.8,1.34,0.65,0.79,0.65,0.77]
[null,480,{"$nulls":28},4.14,99.3,2.68,31.8,2.64,30.5,1.86,12,1.38,5.48,1.08,2.87,1.04,2.66,1.03,2.59,0.82,1.42,0.82,1.39,0.67,0.82,0.66,0.81]
[null,490,{"$nulls":28},4.22,103.5,2.74,33.1,2.7,31.8,1.9,12.6,1.4,5.71,1.1,2.99,1.07,2.77,1.06,2.7,0.84,1.48,0.83,1.45,0.68,0.86,0.68,0.84]
[null,500,{"$nulls":30},2.8,35.5,2.75,34,1.93,13.1,1.43,5.94,1.12,3.12,1.09,2.88,1.08,2.81,0.86,1.55,0.85,1.51,0.7,0.89,0.69,0.88,0.49,0.36,0.49,0.35]
[null,520,{"$nulls":30},2.91,38.3,2.86,36.8,2.01,14.1,1.49,6.43,1.16,3.37,1.13,3.12,1.12,3.04,0.89,1.67,0.88,1.63,0.72,0.97,0.72,0.95,0.51,0.39,0.51,0.38]
[null,540,{"$nulls":30},3.02,41.3,2.97,39.6,2.09,15.3,1.55,6.93,1.21,3.63,1.18,3.36,1.16,3.28,0.93,1.8,0.92,1.76,0.75,1.04,0.75,1.02,0.53,0.42,0.53,0.41]
[null,560,{"$nulls":30},3.13,44.3,3.08,42.6,2.17,16.4,1.6,7.46,1.25,3.91,1.22,3.62,1.21,3.53,0.96,1.94,0.95,1.9,0.78,1.12,0.77,1.1,0.55,0.45,0.55,0.44]
[null,580,{"$nulls":30},3.24,47.5,3.19,45.6,2.24,17.6,1.66,8,1.3,4.19,1.26,3.88,1.25,3.78,1,2.08,0.99,2.03,0.81,1.2,0.8,1.18,0.57,0.48,0.56,0.47]
[null,600,{"$nulls":30},3.36,49.6,3.3,48.8,2.32,18.8,1.72,8.56,1.34,4.49,1.31,4.15,1.29,4.05,1.03,2.23,1.02,2.18,0.84,1.29,0.83,1.26,0.59,0.51,0.58,0.5]
[null,620,{"$nulls":30},3.47,53,3.41,50.9,2.4,20.1,1.78,9.14,1.39,4.79,1.35,4.34,1.34,4.32,1.06,2.38,1.05,2.32,0.86,1.38,0.86,1.35,0.61,0.55,0.6,0.54]
[null,640,{"$nulls":30},3.58,56.5,3.52,54.2,2.48,21.4,1.83,9.74,1.43,5.1,1.39,4.73,1.38,4.61,1.1,2.53,1.09,2.48,0.89,1.47,0.88,1.44,0.63,0.58,0.62,0.57]
[null,660,{"$nulls":30},3.69,61,3.63,57.7,2.55,22.8,1.89,10.4,1.48,5.43,1.44,5.03,1.42,4.9,1.13,2.69,1.12,2.63,0.92,1.56,0.91,1.53,0.65,0.62,0.64,0.61]
[null,680,{"$nulls":30},3.8,63.8,3.74,61.2,2.63,24.2,1.95,11,1.52,5.76,1.48,5.33,1.47,5.7,1.17,2.86,1.16,2.8,0.95,1.65,0.94,1.62,0.67,0.66,0.66,0.65]
[null,700,{"$nulls":30},3.91,67.6,3.85,64.9,2.71,25.6,2.01,11.7,1.57,6.11,1.52,5.65,1.51,5.51,1.2,3.03,1.19,2.96,0.97,1.75,0.97,1.72,0.69,0.7,0.68,0.69]
[null,720,{"$nulls":30},4.03,71.5,3.96,68.6,2.79,27.1,2.06,12.3,1.61,6.46,1.57,5.98,1.55,5.83,1.24,3.21,1.22,3.13,1,1.86,0.99,1.82,0.71,0.74,0.7,0.73]
[null,740,{"$nulls":30},4.14,75.5,4.07,72.5,2.86,28.6,2.12,13,1.66,6.82,1.61,6.32,1.59,6.16,1.27,3.39,1.26,3.31,1.03,1.96,1.02,1.92,0.73,0.78,0.72,0.77,0.55,0.39,0.55,0.38,0.55,0.38,0.42,0.19,0.42,0.19]
[null,760,{"$nulls":30},4.25,79.6,4.18,76.5,2.94,30.2,2.18,13.7,1.7,7.2,1.65,6.66,1.64,6.5,1.3,3.57,1.29,3.49,1.06,2.07,1.05,2.03,0.74,0.82,0.74,0.81,0.57,0.41,0.57,0.4,0.56,0.4,0.44,0.2,0.43,0.2]
[null,780,{"$nulls":30},4.36,83.9,4.29,80.5,3.02,31.8,2.24,14.5,1.75,7.58,1.7,7.02,1.68,6.84,1.34,3.76,1.33,3.68,1.09,2.18,1.08,2.13,0.76,0.87,0.76,0.85,0.58,0.43,0.58,0.42,0.58,0.42,0.45,0.21,0.45,0.21]
[null,800,{"$nulls":30},4.47,88.3,4.41,84.7,3.09,33.5,2.29,15.2,1.79,7.97,1.74,7.38,1.72,7.2,1.37,3.96,1.36,3.87,1.11,2.29,1.11,2.24,0.78,0.91,0.78,0.9,0.6,0.45,0.6,0.45,0.59,0.44,0.46,0.23,0.46,0.22]
[null,820,{"$nulls":34},3.17,35.2,2.35,16,1.84,8.38,1.78,7.76,1.77,7.56,1.41,4.16,1.39,4.06,1.14,2.41,1.13,2.36,0.8,0.96,0.8,0.94,0.61,0.47,0.61,0.47,0.61,0.46,0.47,0.24,0.47,0.23]
[null,840,{"$nulls":34},3.25,36.9,2.41,16.8,1.88,8.79,1.83,8.14,1.81,7.94,1.44,4.36,1.43,4.27,1.17,2.53,1.16,2.47,0.82,1,0.82,0.99,0.63,0.5,0.63,0.49,0.62,0.48,0.48,0.25,0.48,0.25]
[null,860,{"$nulls":34},3.33,38.7,2.46,17.6,1.93,9.22,1.87,8.53,1.85,8.32,1.48,4.57,1.46,4.47,1.2,2.65,1.19,2.59,0.84,1.05,0.84,1.04,0.64,0.52,0.64,0.51,0.64,0.51,0.49,0.26,0.49,0.26]
[null,880,{"$nulls":34},3.4,40.5,2.52,18.4,1.97,9.65,1.91,8.93,1.9,8.71,1.51,4.79,1.5,4.68,1.23,2.77,1.22,2.72,0.86,1.1,0.86,1.08,0.65,0.55,0.65,0.54,0.65,0.53,0.51,0.27,0.5,0.27]
[null,900,{"$nulls":34},3.48,42.4,2.58,19.3,2.02,10.1,1.96,9.34,1.94,9.11,1.54,5.01,1.53,4.9,1.25,2.9,1.24,2.84,0.88,1.15,0.88,1.13,0.67,0.57,0.67,0.56,0.67,0.56,0.52,0.29,0.51,0.28]
[null,920,{"$nulls":34},3.56,44.3,2.64,20.1,2.06,10.5,2,9.76,1.98,9.52,1.58,5.23,1.56,5.12,1.28,3.03,1.27,2.97,0.9,1.21,0.9,1.19,0.69,0.6,0.69,0.59,0.68,0.58,0.53,0.3,0.53,0.29]
[null,940,{"$nulls":34},3.64,46.2,2.69,21,2.11,11,2.05,10.2,2.03,9.94,1.61,5.46,1.6,5.34,1.31,3.16,1.3,3.1,0.92,1.26,0.92,1.24,0.7,0.62,0.7,0.61,0.7,0.61,0.54,0.31,0.54,0.31]
[null,960,{"$nulls":34},3.71,48.2,2.75,21.9,2.15,11.5,2.09,10.6,2.07,10.4,1.65,5.7,1.63,5.57,1.34,3.3,1.33,3.23,0.94,1.31,0.93,1.29,0.72,0.65,0.72,0.64,0.71,0.63,0.55,0.32,0.55,0.32]
[null,980,{"$nulls":34},3.79,50.2,2.81,22.8,2.2,12,2.13,11.1,2.11,10.8,1.68,5.94,1.67,5.81,1.36,3.44,1.35,3.37,0.96,1.37,0.95,1.34,0.73,0.68,0.73,0.67,0.73,0.66,0.56,0.34,0.56,0.33]
[null,1000,{"$nulls":34},3.87,52.3,2.87,23.3,2.24,12.5,2.18,11.5,2.16,11.2,1.72,6.18,1.7,6.05,1.39,3.58,1.38,3.51,0.98,1.42,0.97,1.4,0.75,0.71,0.75,0.7,0.74,0.69,0.57,0.35,0.57,0.35]
[null,1020,{"$nulls":34},3.95,54.4,2.92,24.7,2.29,13,2.22,12,2.2,11.7,1.75,6.43,1.73,6.29,1.42,3.72,1.41,3.65,1,1.48,0.99,1.46,0.76,0.73,0.76,0.72,0.76,0.71,0.59,0.37,0.58,0.36]
[null,1040,{"$nulls":34},4.02,56.6,2.98,25.7,2.33,13.5,2.26,12.5,2.24,12.2,1.78,6.69,1.77,6.54,1.45,3.87,1.44,3.79,1.02,1.54,1.01,1.51,0.78,0.76,0.78,0.75,0.77,0.74,0.6,0.38,0.59,0.38]
[null,1060,{"$nulls":34},4.1,58.8,3.04,26.7,2.38,14,2.31,13,2.28,12.6,1.82,6.95,1.8,6.79,1.48,4.02,1.47,3.94,1.04,1.6,1.03,1.57,0.79,0.79,0.79,0.78,0.79,0.77,0.61,0.4,0.61,0.39]
[null,1080,{"$nulls":34},4.18,61,3.1,27.7,2.42,14.5,2.35,13.5,2.33,13.1,1.85,7.21,1.84,7.05,1.5,4.17,1.49,4.09,1.06,1.66,1.05,1.63,0.81,0.82,0.8,0.81,0.8,0.8,0.62,0.41,0.62,41]
[null,1100,{"$nulls":34},4.26,63.3,3.15,28.8,2.46,15.1,2.39,14,2.37,13.6,1.89,7.48,1.87,7.31,1.53,4.33,1.52,4.24,1.08,1.72,1.07,1.69,0.82,0.85,0.82,0.84,0.82,0.83,0.63,0.43,0.63,0.42]
[null,1150,{"$nulls":34},4.45,69.2,3.3,31.4,2.58,16.5,2.5,15.3,2.48,14.9,1.97,8.18,1.96,7.99,1.6,4.73,1.59,4.64,1.13,1.88,1.12,1.85,0.86,0.93,0.86,0.92,0.85,0.91,0.66,0.47,0.66,0.46]
[null,1200,{"$nulls":34},4.64,75.3,3.44,34.2,2.69,17.9,2.61,16.6,2.59,16.2,2.06,8.9,2.04,8.71,1.67,5.15,1.66,5.05,1.18,2.05,1.17,2.02,0.9,1.02,0.89,1,0.89,0.99,0.69,0.51,0.69,0.5]
[null,1250,{"$nulls":34},4.84,81.7,3.58,37.1,2.8,19.5,2.72,18,2.69,17.6,2.14,9.66,2.13,9.45,1.74,5.59,1.73,5.48,1.22,2.25,1.22,2.19,0.94,1.1,0.93,1.09,0.93,1.07,0.72,0.55,0.71,0.54]
[null,1300,{"$nulls":34},5.03,88.4,3.73,40.2,2.91,21.1,2.83,19.5,2.8,19,2.23,10.4,2.21,10.2,1.81,6.05,1.8,5.93,1.27,2.41,1.27,2.37,0.97,1.19,0.97,1.18,0.96,1.16,0.75,0.59,0.74,0.59]
[null,1350,{"$nulls":34},5.22,95.3,3.87,43.3,3.03,22.7,2.94,21,2.91,20.5,2.32,11.3,2.3,11,1.88,6.52,1.87,6.39,1.32,2.6,1.31,2.55,1.01,1.29,1.01,1.27,1,1.25,0.78,0.64,0.77,0.63]
[null,1400,{"$nulls":34},5.42,102.5,4.01,46.6,3.14,24.4,3.05,22.6,3.02,22,2.4,12.1,2.38,11.8,1.95,7.01,1.93,6.87,1.37,2.79,1.36,2.74,1.05,1.38,1.04,1.36,1.04,1.34,0.8,0.69,0.8,0.68]
[null,1450,{"$nulls":36},4.16,50,3.25,26.2,3.16,24.3,3.12,23.6,2.49,13,2.47,12.7,2.02,7.52,2,7.37,1.42,2.99,1.41,2.94,1.09,1.49,1.08,1.46,1.07,1.44,0.83,0.74,0.83,0.73]
[null,1500,{"$nulls":36},4.3,53.5,3.36,28,3.26,26,3.23,25.3,2.57,13.9,2.55,13.6,2.09,8.05,2.07,7.89,1.47,3.2,1.46,3.15,1.12,1.59,1.12,1.57,1.11,1.54,0.86,0.79,0.86,0.78]
[null,1550,{"$nulls":36},4.44,57.1,3.47,29.9,3.37,27.7,3.34,27,2.66,14.9,2.64,14.5,2.16,8.6,2.14,8.42,1.52,3.42,1.51,3.36,1.16,1.7,1.16,1.67,1.15,1.65,0.89,0.85,0.89,0.83]
[null,1600,{"$nulls":36},4.59,60.9,3.59,31.9,3.48,29.5,3.45,28.8,2.74,15.8,2.72,15.5,2.23,9.16,2.21,8.98,1.57,3.65,1.56,3.58,1.21,1.81,1.19,1.73,1.19,1.76,0.92,0.9,0.91,0.89]
[null,1650,{"$nulls":36},4.73,64.7,3.7,35.9,3.59,31.4,3.56,30.6,2.83,16.8,2.81,16.5,2.3,9.74,2.28,9.55,1.62,3.88,1.61,3.81,1.24,1.92,1.23,1.89,1.22,1.87,0.95,0.96,0.94,0.95]