{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["REGISTR v.3.1"],"not_rendered":{"charts":0,"images":0,"macros":1,"external_links":1,"defined_names":1,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"REGISTR v.3.1","index":0,"n_rows":37,"n_cols":5,"rows_kept":37,"cut":false,"hidden":false,"merged":[[2,7,2,8]],"flags":["formulas_cached_only"]}
[]
[]
[]
[null,null,"общая мощность","Вт",3500]
[null,null,null,"ккал/ч",3009.4582975064486]
[]
[null,null,"температура подачи t1","°С",95]
[null,null,"температура обратки t2","°С",70]
[null,null,"температура внутреннего воздуха tвн","°С",16]
[]
[null,null,"диаметр регистра","Ду",3]
[null,null,"число рядов",null,4]
[null,null,"ф",null,1.4]
[]
[null,null,"q","ккал/(ч*экм)",345.74040554292986]
[null,null,"требуемая площадь нагр поверхности","экм",8.704387017712254]
[]
[null,null,"площадь нагр поверхности 1 м"]
[null,null,"открытой горизонтальной трубы","экм/м",0.405]
[]
[]
[null,null,"длина греющей трубы","м",21.49231362398087]
[]
[null,null,"длина регистра","м",5.3730784059952175]
[]
[null,null,null,"Вт/м",162.84891711680316]
[]
[]
[]
[]
[]
[null,null,null,"Ду","f э (экм/м)"]
[null,null,1,40,0.27]
[null,null,2,50,0.334]
[null,null,3,65,0.405]
[null,null,4,80,0.465]
[null,null,null,100,0.55]