{"text_format":"2","workbook":"xls","n_sheets":3,"sheets":["Таблица регистров","Лист2","Лист3"],"not_rendered":{"charts":0,"images":0,"macros":1,"external_links":1,"defined_names":0,"comments":16,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Таблица регистров","index":0,"n_rows":73,"n_cols":20,"rows_kept":73,"cut":false,"hidden":false,"merged":[[0,7,0,9],[0,6,1,6],[0,11,0,16]],"flags":["formulas_cached_only"]}
["Число секций","Длина l(м)","Вес секции (кг)","Вес регистра (кг)",null,null,"Температура воздуха в помещении","Теплоноситель водда с параметрами:",null,null,null,"Поверхность нагрева регистра (м2)",{"$nulls":5},"Наружный диаметр (мм)","Число рядов","Высота регистра (мм)"]
[3,1,18.8,35,null,null,null,"150-70","130-70","110-70","Длина (м)",1,2,3,4,5,10]
[3,2,37.6,53.8,null,"150-70",5,945,855,765,null,0.716,1.432,2.148,2.864,3.58,7.16,"76*3,5",3,550]
[3,3,56.3,72.5,null,"130-70",12,882,792,702,null,0.84,1.68,2.52,3.36,4.2,8.4,"89*3,5",3,610]
[3,4,75.2,91.4,null,"110-70",16,846,756,666,"столбец",0.955,1.91,2.865,3.82,4.775,9.55,"76*3,5",4,700]
[3,5,93.9,113.4,null,null,18,828,738,648,1,1.02,2.04,3.06,4.08,5.1,10.2,"108*4,0",3,690]
[3,10,187.8,210.6,null,null,20,810,720,630,2,1.12,2.24,3.36,4.48,5.6,11.2,"89*3,5",4,790]
[4,1,25,45.9,{"$nulls":6},3,1.19,2.38,3.57,4.76,5.95,11.9,"76*3,5",5,850]
[4,2,50.1,71,{"$nulls":6},4,1.26,2.52,3.78,5.04,6.3,12.6,"133*4,0",3,790]
[4,3,75.1,96,{"$nulls":6},5,1.36,2.72,4.08,5.44,6.8,13.6,"108*4,0",4,910]
[4,4,100.2,121.1,{"$nulls":6},10,1.4,2.8,4.2,5.6,7,14,"89*3,5",5,970]
[4,5,125.2,150.1,{"$nulls":7},1.67,3.34,5.01,6.68,8.35,16.7,"133*4,0",4,1060]
[4,10,250.4,279.3,{"$nulls":7},1.7,3.4,5.1,6.8,8.5,17,"108*4,0",5,1130]
[5,1,31.3,57.2,{"$nulls":7},2.09,4.18,6.27,8.36,10.45,20.9,"133*4,0",5,1330]
[5,2,62.6,88.5]
[5,3,93.9,119.8]
[5,4,125.2,151.1,2,16180,3,3,5,"133*4,0",3,550]
[5,5,156.5,187.1]
[5,10,313,348.9]
[3,1,22.1,40.9]
[3,2,44.3,63.1]
[3,3,66.4,85.2,null,null,666,null,null,12.147147147147146,10.45,{"$nulls":4},5]
[3,4,88.6,107.4]
[3,5,110.7,133]
[3,10,221.4,247.4]
[4,1,29.5,54.2]
[4,2,59,83.7]
[4,3,88.6,113.3]
[4,4,118,142.1]
[4,5,147.6,276.7]
[4,10,295.2,328.8]
[5,1,36.9,67.6]
[5,2,73.8,104.5]
[5,3,110.7,141.4]
[5,4,147.6,170.3]
[5,5,184.5,224.5]
[5,10,369.5,410.8]
[3,1,30.8,54.5]
[3,2,61.6,85.3]
[3,3,92.3,116]
[3,4,123.2,146.9]
[3,5,153.9,181.6]
[3,10,307.8,339.4]
[4,1,41,72.9]
[4,2,82.1,114]
[4,3,123.1,155]
[4,4,164.2,196.1]
[4,5,205.2,242]
[4,10,410.4,452.4]
[5,1,51.3,91.3]
[5,2,102.6,142.6]
[5,3,153.9,195.3]
[5,4,205.2,245.2]
[5,5,256.5,302.5]
[5,10,513,565.2]
[3,1,38.2,70.1]
[3,2,76.4,108.3]
[3,3,114.6,146.5]
[3,4,152.8,184.7]
[3,5,191,227.3]
[3,10,382,422.8]
[4,1,50.9,94.1]
[4,2,101.8,145]
[4,3,152.7,195.9]
[4,4,203.6,246.8]
[4,5,254.5,303.4]
[4,10,509,563.7]
[5,1,63.6,118.2]
[5,2,127.2,181.8]
[5,3,190.8,245.4]
[5,4,254.4,309]
[5,5,318,379.6]
[5,10,636,704.7]

{"sheet":"Лист2","index":1,"n_rows":57,"n_cols":13,"rows_kept":57,"cut":false,"hidden":false,"merged":[[20,8,21,8],[20,9,20,12],[29,3,29,8]],"flags":["formulas_cached_only"]}
[13000,null,null,855,15.2046783625731,2,7.60233918128655,5]
{"$rows_empty":7}
[{"$nulls":4},5,null,null,null,1,null,5]
[{"$nulls":8},2]
[{"$nulls":6},2,null,3]
[{"$nulls":8},4]
[{"$nulls":8},5]
[]
[{"$nulls":9},10.45]
[{"$nulls":11},7.6]
[{"$nulls":6},1,{"$nulls":4},10.45]
[{"$nulls":6},2,{"$nulls":4},7]
[]
[]
[{"$nulls":8},"Температура воздуха в помещении","Теплоноситель вода с параметрами:"]
[{"$nulls":6},"150-70",null,null,"150-70","130-70","110-70","95-70"]
[{"$nulls":6},"130-70",null,5,945,855,765,698]
[{"$nulls":6},"110-70",null,12,882,792,702,653]
[{"$nulls":6},"95-70",null,16,846,756,666,598]
[{"$nulls":8},18,828,738,648,580]
[{"$nulls":8},20,810,720,630,570]
[]
[]
[null,null,null,"Поверхность нагрева регистра (м2)",{"$nulls":5},"Наружный диаметр (мм)","Число рядов","Высота регистра (мм)"]
[null,null,"Длина (м)",1,2,3,4,5,10]
[null,null,null,0.716,1.432,2.148,2.864,3.58,7.16,"76*3,5",3,550]
[null,null,null,0.84,1.68,2.52,3.36,4.2,8.4,"89*3,5",3,610]
[null,null,"столбец",0.955,1.91,2.865,3.82,4.775,9.55,"76*3,5",4,700]
[null,null,1,1.02,2.04,3.06,4.08,5.1,10.2,"108*4,0",3,690]
[null,null,2,1.12,2.24,3.36,4.48,5.6,11.2,"89*3,5",4,790]
[null,null,3,1.19,2.38,3.57,4.76,5.95,11.9,"76*3,5",5,850]
[null,null,4,1.26,2.52,3.78,5.04,6.3,12.6,"133*4,0",3,790]
[null,null,5,1.36,2.72,4.08,5.44,6.8,13.6,"108*4,0",4,910]
[null,null,10,1.4,2.8,4.2,5.6,7,14,"89*3,5",5,970]
[null,null,null,1.67,3.34,5.01,6.68,8.35,16.7,"133*4,0",4,1060]
[null,null,null,1.7,3.4,5.1,6.8,8.5,17,"108*4,0",5,1130]
[null,null,null,2.09,4.18,6.27,8.36,10.45,20.9,"133*4,0",5,1330]
[]
[]
[null,null,null,2.09,4.18,6.27,8.36,10.45,20.9]
[null,null,null,1.7,3.4,5.1,6.8,8.5,17]
[null,null,null,1.67,3.34,5.01,6.68,8.35,16.7]
[null,null,null,1.4,2.8,4.2,5.6,7,14]
[null,null,null,1.36,2.72,4.08,5.44,6.8,13.6]
[null,null,null,1.26,2.52,3.78,5.04,6.3,12.6]
[null,null,null,1.19,2.38,3.57,4.76,5.95,11.9]
[null,null,null,1.12,2.24,3.36,4.48,5.6,11.2]
[null,null,null,1.02,2.04,3.06,4.08,5.1,10.2]
[null,null,null,0.955,1.91,2.865,3.82,4.775,9.55]
[null,null,null,0.84,1.68,2.52,3.36,4.2,8.4]
[null,null,null,0.716,1.432,2.148,2.864,3.58,7.16]

{"sheet":"Лист3","index":2,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}